## Complete MasterDataset
complaint_date | dealer_name | dealer_location | exp_domestic | customer_name | customer_location | model | compressor_sr_no | FRR_no | FRR_date | FSR_no | FSR_date | nature_of_complaint | displacement_date | commision_date | run_hrs | rpm | application_market_segment | period_dd_to_dc_in_months | FSR_site_observations | cylinder_number_details | open_close | spares_parts_replaced
2015-04-07 | Trade Links | Secunderabad | D | Sira Chilling Center | null | KCX2 | 3364K627 | 32 | 2015-03-27 | 68 | 2015-09-03 | crank shaft pin wear. | 2013-05-24 | 2014-11-08 | 1600 | null | null | 15 | bigend bearings worn out and brokened at cyl.no.01, c.pin no01 and conrod worn out | null | closed | crankshaft conrod assly,bigend bearing
2015-04-07 | S M Refrigeration | null | D | Star Milk Udyog | Uttar Pradesh | KC2 | 336K3135 | 1415/14 | 2015-03-31 | 5218 | 2015-03-27 | kc oil pump low oil pressure problem. | 2014-01-03 | 2014-11-04 | 2500 | null | null | 1 | oil pump pressure not develops | null | closed | scoring marks on oil pump cover gears and bushes damaged
2015-04-07 | S M Refrigeration | null | D | Sabhya Sanchi Cold Storage | null | KC3 | 337K4181 | 12 | 2015-03-31 | 5212 | 2015-09-03 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-03 | 2015-02-26 | 13 | null | null | 1 | Driving gear tang broken | null | closed | gear kit
2015-04-07 | S M Refrigeration | null | D | Ram Rathi Cold Storage | null | KC6 | 339K3139 | 13 | 2015-03-31 | 5219 | 2015-03-24 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-01 | 2015-02-26 | 195 | null | null | 1 | Driving gear tang broken | null | closed | gear kit
2015-04-07 | S M Refrigeration | null | D | Ramrathi Cold Storage | null | KC6 | 339K3139 | 11 | 2015-03-31 | 5211 | 2015-04-03 | knocking / abnormal sound | 2015-01-01 | 2015-02-26 | 18 | null | null | 1 | piston 2nos & piston ring sets 3 nos worn out | null | closed | piston and piston ring sets replaced
2015-04-07 | S M Refrigeration | null | D | Bajpai Referigerator | null | KC72 | 347K794 | 1039 | 2015-02-04 | 1458 | 2015-03-16 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-09 | 2015-03-16 | ZH | null | null | 6 | HP LP pressure gauges out and leak from adaptor | null | closed | HP LP presure gauges
2015-04-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shriya Chemicals PvtLtd | null | KC102 | 349K28 | 74 | 2015-03-31 | 133156 | 2015-02-26 | null | 2014-08-31 | 2015-02-26 | null | null | null | 6 | Required 02 nos solenoide valve coils for business pramotion. | null | closed | null
2015-04-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Linde Indial Ltd | Dahej | KCX3 | 3374K703/704 | 75 | 2015-03-31 | null | 2015-10-02 | gauge board leakage | 2013-01-12 | 2015-11-02 | 200 | null | null | 14 | Gauge board board leakage from all the ferrule joints even after tightning of all the joints. Also TAH8 Valve & pressure gauge pre mature failure takes place. | null | closed | Replaced control panel box, pressure gauge , TAH8 Valve assly & union /ferrules.
2015-04-10 | Multivista Global Pvt Ltd | null | D | Jrj Sea Foods No155 | Padukkottai | KC31 | 343K1398 | 24 | 2015-03-26 | null | 2015-03-25 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-02-18 | 2014-07-10 | PC | null | null | 8 | Oil pressure not develop due to drive shaft tang broken , bush damaged. | null | closed | Oil pump assembly
2015-04-10 | Kalp Marketing | Gujrat | D | Dilip Buidcon Limited | Madhya Pradesh | KC6 | 339K3097 | 74 | 2015-03-31 | 413 | 2015-03-16 | knocking / abnormal sound | 2014-01-11 | 2015-03-03 | 100 | null | null | 4 | Discharge valve leakage after 100 hrs. resulting susequent damages of parts. | null | closed | Piston, Piston ring set & Delivery valve
2015-04-10 | null | null | D | Gokul Cold Storage | Boriavi | KC2 | null | 76 | 2015-03-31 | null | 2015-02-14 | spares supply cylinder liner problem | null | null | null | null | null | null | During fitment piston was not ncerted in liner. Diamensional problem. | null | closed | cylinder liner replaced
2015-04-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | K A Malle Pharma Ltd | Ankleshwar Gujarat | KC3 | 337K4288 | 77 | 2015-03-31 | null | 2015-11-03 | tah8 valve tight / stem broken / leakage | 2014-01-10 | 2015-12-03 | ZH | null | null | 5 | During commossioning tried to open TAH8 valve fully but coudent open properly. Steam jammed in valve. | null | closed | TAH8 Valve assembly replaced.
2015-04-12 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Koppal Dist | KCX4 | 3384K814 | 34 | 2015-03-28 | 71 | 2015-03-28 | cylinder overheating | 2013-07-29 | 2014-08-14 | 1336 | null | null | 11 | Delivery valve leakage . | null | closed | Piston , piston ring set , delivery valve & buffer spring replaced.
2015-04-12 | Gargi Engineering Enterprices Pvt Ltd | null | D | Deepak Fertilisers & Petrochemicals | Taloja, Mh | KC72 | 347K654 | 1 | 2015-01-04 | null | 2015-03-27 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2013-01-06 | 2014-04-21 | 150 | null | null | 13 | Both bushes found wornout along with both gears, The distance between bushes measured from top & bottom side , backside 16.4mm & top side 15.8mm. | null | closed | Pump assly
2015-04-12 | Gargi Engineering Enterprices Pvt Ltd | null | D | Cj Jain Cold Storage | Dighe | KC3 | 337K4202 | 2 | 2015-01-04 | null | 2015-03-20 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-05 | 2015-01-23 | 150 | null | null | 8 | Both bushes jammed to breaking of driving gear leg notch. | null | closed | Gear kit replaced
2015-04-12 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Koppal Dist | KCX4 | 3384K814 | 33 | 2015-03-28 | 69 | 2015-03-15 | knocking / abnormal sound | 2013-07-29 | 2014-08-14 | 212 | null | null | 11 | Delivery valve leakage . | null | closed | delivery valve assly replaced
2015-04-12 | S M Refrigeration | null | D | Mahindra Cold Storage | Jalandhar | KC4 | 338K5136 | 1040 | 2015-06-04 | 1560 | 2015-01-04 | pressure gauges (suc./disch./oil) not working/malfunctioning | null | 2015-01-04 | ZH | null | null | 6 | Pressure gauge 16 kg found faullty | null | closed | Pressure gauge replaced.
2015-04-13 | Kalp Marketing | Gujrat | D | Agrwal Cold Storage | null | KC4 | 338K5021 | 3 | 2015-01-04 | null | 2015-03-13 | kc oil pump low oil pressure problem. | 2014-12-02 | 2014-05-11 | PC | null | null | 8 | Checked found scoring on cover plate , housing and gear set. | null | closed | Oil pump assembly replaced.
2015-04-18 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shree Salasar Agro Cold Storage | Tapi | KCX3 | 3374K804 | 001/20152016 | 2015-03-04 | null | 2015-03-28 | solenoide valve threading spoil | 2014-01-09 | 2015-03-28 | ZH | null | null | 6 | During commissionning thread of solenoid valve top side observed not proper resulting top side adaptor not fitted properly. | null | closed | Adaptor & solenoid valve replaced.
2015-04-18 | S M Refrigeration | null | D | Inana Chilling Centre | Nagpur | KC2 | 336K3260 | 1041 | 2015-10-04 | 132 | 2015-09-02 | sound in disch. stop valve | 2014-01-11 | 2015-04-02 | 44 | null | null | 3 | Visited site found compressor in stop condition , After start the compressor , found sound in discharge stop valve . | null | closed | Stop valve replaced.
2015-04-18 | Kalp Marketing | Gujrat | D | Himalaya Ice Factory | Madhya Pradesh | PC2 | 331K2587 | 002/20152016 | 2015-08-04 | 455 | 2015-03-07 | stop valve leakage | 2014-01-01 | 2015-04-04 | 1700 | null | null | 14 | Stop valve leakage in suction line. | null | closed | Stop valve replaced.
2015-04-20 | Parag Marketing Services | null | D | Sumukh Farms | Shimoga | KCX2 | 3364K796 | 1 | 2015-04-15 | 1 | 2015-10-04 | knocking / abnormal sound | 2014-11-21 | 2015-10-04 | PC | null | null | 5 | Observed knocking sound at cyl. No. 2 while in unloading time. Checked and found gudgeon pin has loosed and connecting rod bolt also slightly tapered. | null | closed | Gudgeon pin , Con rod bolt & Hex nut replaced.
2015-04-20 | Multivista Global Pvt Ltd | null | D | Asoka Foods | Trichy | PC2 | 331K2672 | MVGL15/1601 | 2015-09-04 | null | 2015-08-04 | shaft seal leakage | 2014-08-29 | 2015-01-02 | 500 | null | null | 6 | Stationary sealing ring damaged. | null | closed | Shaft seal assly replaced.
2015-04-22 | Kalp Marketing | Gujrat | D | Trirupati Balaji Agri Foods | Ranasan | KCX4 | 3384K847 | 1415/62 | 2015-01-13 | 220 | 2014-10-18 | cylinder overheating | 2014-01-01 | 2014-02-26 | 2378 | null | null | 1 | Opened all head and found one discharge valve assembly in leakage condition and piston was broken . Discharge valve assembly leakage resulted in overheating of cylinder and due to that piston damaged . Hence following spares are replaced and recommended for free replacement. | null | closed | Piston , Piston ring set , Discharge valve assembly.
2015-04-22 | Kalp Marketing | Gujrat | D | Mothershree Cold Storage | Ahmedabad | KCX3 | 3374K684 | 1415/65 | 2015-01-13 | 228 | 2014-11-17 | high oil consumption / oil carry over | 2013-01-11 | 2014-08-02 | 2150 | null | null | 4 | Piston ring close gap observed more than 1.00 mm. | null | closed | Replaced piston ring sets
2015-04-22 | Kalp Marketing | Gujrat | D | Anik Industries | Bhopal | KC4 | 338K5062 | 1415/64 | 2015-01-13 | 131 | 2014-07-11 | high oil consumption / oil carry over | 2014-01-04 | 2014-12-08 | 100 | null | null | 4 | Opened all head and removed all connecting rod assembly. Checked piston ring close gap and found ok. Replaced all VLD Orings and non return valve only. | null | closed | NRV, VLD Oring set replaced
2015-04-22 | Kalp Marketing | Gujrat | D | Pavan Ice Factory | Dwarka | KC3 | 337K4006 | 1415/63 | 2015-01-13 | 150 | 2014-04-11 | knocking / abnormal sound | 2013-01-07 | 2014-07-30 | 1530 | null | null | 11 | Opened the head and found discharge valve assembly in leakage condition and also damaged the liner housing hence replaced following spares. | null | closed | Piston , Piston ring set , Discharge valve assembly.
2015-04-22 | Kalp Marketing | Gujrat | D | NRH Com Bara Road | Junagadh Veraval, Gujarat | KCX3 | 3374K640 | 1415/61 | 2015-01-13 | 230 | 2014-12-10 | knocking / abnormal sound | 2013-01-07 | 2014-08-18 | 4570 | null | null | 12 | Opened all head and found all discharge valve assembly in leakage condition. For cylinder no. 1 it found heavy leakage and resulted in the failure of piston and liner cylinder. Both the piston and liner worn out hence replaced. The discharge valve leakage problem is replaced hence replaced with KC discharge | null | closed | Replaced Piston ring set , Cylinder liner , Piston , Suction strike lim,itor , CR Lock, VLD Oring & NRV.
2015-04-25 | Trade Links | Secunderabad | D | Rinac India Ltd | null | PC2 | 331K2628 | 28 | 2015-02-03 | 61 | 2015-12-02 | pc2 oil pump low oil pressure | 2014-04-30 | 2014-11-22 | 650 | null | null | 7 | Compressor loading / unloading problem due to low oil pressure. | null | closed | Oil pump assly replaced
2015-04-27 | Trade Links | Secunderabad | D | Modern Frozen Foods | null | KC42 | 344K901 | Mail | null | null | null | c.case leak due to welding crack near side door and foot | 2014-01-04 | 2014-01-06 | 2000 | null | null | 2 | null | null | open | null
2015-04-27 | null | null | E | Vietnam | null | KCX4 | 3384K912 | Mail | null | null | null | cylinder overheating | null | null | PC | null | null | null | Cyinder no. 2 temp 143⁰C while others are 123 - 125 ⁰C | null | closed | null
2015-04-27 | null | null | E | Vietnam | null | KCX6 | 3394K486 | Mail | null | null | null | knocking / abnormal sound | null | null | PC | null | null | null | Piston touch to delivery valve after 30 min running at cyl no. 6 and M6 tubing leakage from nut fitment. | null | closed | null
2015-04-27 | Cool Comfort Private Limited | West Bengal | D | Kamla Cold Starage | null | KC6 | 339K3149 | Mail | null | null | null | knocking / abnormal sound | null | null | 8 | null | null | 2 | Intermiddiate bearings damaged, c.pin no.6 & bigend bearings damaged | null | closed | null
2015-04-27 | null | null | E | Vietnam | null | KCX6 | 3394K455 | Mail | null | null | null | pump manifold damage | null | null | PC | null | null | null | Pump manifold damage | null | closed | null
2015-04-27 | null | null | E | Vietnam | null | KCX3 | 3374K725 | Mail | null | null | null | stop valve leakage & oil pressure not develop | null | null | PC | null | null | null | Stop valve leakage & oil pressure not develop | null | closed | null
2015-05-09 | Multivista Global Pvt Ltd | null | D | Aks Cold Storage | Mettupalayam | KC4 | 338K4930 | MVGL 15 /1603 | 2015-04-25 | null | 2015-04-24 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2013-08-09 | 2014-10-16 | 529 | null | null | 12 | Oil pressure not develop , remove the pump cover checke the gear found driving gear broken and housing wornout. | null | closed | Oil pump assembly replaced
2015-05-09 | Geekay Pneumatic Pvt Ltd | null | D | Veronica Marine Exports | Kollam | KC51 | 345K887 | 001/201516 | 2015-04-29 | 1838 | 2015-04-18 | knocking / abnormal sound | 2014-02-26 | 2014-08-14 | 2600 | null | null | 6 | Delivery valve stroke limitor wornout and cylinder damage | null | closed | Delivery valve
2015-05-09 | Geekay Pneumatic Pvt Ltd | null | D | Makka Ice Palnt | Chandiroor | KC3 | 337K4261 | 002/201516 | 2015-04-29 | 1838 | 2015-04-22 | shaft seal leakage | 2014-08-29 | 2014-12-10 | 2820 | null | null | 2 | Axial play observed 2.00 mm , found thrust ring bronz was wornout and because of same shaft seal fail. | null | closed | Shaft seal assly , thrust ring and bearing bush replaced
2015-05-09 | Multivista Global Pvt Ltd | null | D | Rasi Ice Company 4/7 H Sethu Road | Uchi Pull Ramnad | KC2 | 336K3222 | MVGL 15 /1602 | 2015-04-25 | null | 2015-04-17 | transport damage | 2014-09-19 | 2015-04-17 | ZH | null | null | 7 | Stop valve hand wheel briken - Transport damage | null | closed | Hand wheel replaced
2015-05-17 | Parag Marketing Services | null | D | Indapur Dairy And Milk Product | Baramati | KC9 | 340K327 | 5 | 2015-04-05 | null | 2015-04-28 | high oil consumption / oil carry over | 2013-12-30 | 2014-05-28 | 4900 | null | null | 5 | High oil cary over problem | null | closed | Set piston ring , cylinder liner,surtain spring , NRV replaced
2015-05-17 | S M Refrigeration | null | D | NKanodia & Sons Ramaipur | Kanpur Up | KC3 | 337K4161 | 1516/03 | 2015-04-27 | 5205 | 2015-02-24 | kc oil pump low oil pressure problem. | 2014-01-03 | 2014-08-19 | 607 | null | null | 5 | Dismentle the compressor found both bearing bushes wornout , Also dismentle pump found scoring on bushes, shaft and cover plate | null | closed | KIT Oil pump replaced
2015-05-17 | S M Refrigeration | null | D | Brij Raj Foods Products | Uttar Pradesh | KC31 | 343K1454 | 1516/04 | 2015-04-27 | null | 2015-12-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-01 | 2015-12-04 | ZH | null | null | 3 | Dismentle oil pump assembly found drive gear broken and scoring to bushes | null | closed | KIT Oil pump replaced
2015-05-17 | S M Refrigeration | null | D | Shyam Enterprises | Sitapur, Uttar Pradesh | KC3 | null | 1516/02 | 2015-04-27 | null | null | pressure gauges (suc./disch./oil) not working/malfunctioning | null | null | null | null | null | null | Spares supply defective pressure gauge 25kg/cm2 | null | closed | null
2015-05-17 | S M Refrigeration | null | D | Sanjeevani Ice Plant | Amethi, Uttar Pradesh | KC4 | 338K5141 | 1516/01 | 2015-04-27 | 5223 | 2015-02-04 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-11 | 2015-02-04 | PC | null | null | 5 | Suction pressure gauge found defective . | null | closed | 016 kg/cm2 gauge replaced
2015-05-20 | S M Refrigeration | null | D | Komal Ice Factory | Jagdishpur | KC4 | 338K5079 | 5 | 2015-05-05 | 436 | 2015-04-24 | kc oil pump low oil pressure problem. | 2014-01-05 | 2014-11-22 | 500 | null | null | 6 | observed deep scoring in oil pump housing bushes damaged | null | closed | Oil pump assembly replaced
2015-05-21 | null | null | E | An Refrigeration Industry Co Ltd | Vietnam | KCX6 | 3394K486 | Mail | null | null | 2015-05-18 | high oil consumption / oil carry over | null | null | PC | null | null | null | 5/liter oil consumption observed / day due to one cylinder ORV fall down. | null | closed | null
2015-05-23 | Kalp Marketing | Gujrat | D | Ekta Cold Storage | Mehsana | KCX3 | 3374K829 | 012/20152016 | 2015-11-05 | 459 | 2015-03-19 | cutouts not working / malfunctioning | 2014-01-11 | 2015-02-13 | 100 | null | null | 3 | During start the compressor , Evry time motor found tripped on oil pressure switch. | null | closed | OP Cut out replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Pethapur Cold Storage | Gandhinagar | KCX2 | 3364K694 | 011/20152016 | 2015-11-05 | 291 | 2015-03-31 | cylinder overheating | 2014-01-01 | 2015-03-03 | 3000 | null | null | 2 | Overheating of cylinder takes place due to delivery valve leakage. | null | closed | Delivery Kit replaced.
2015-05-23 | Parag Marketing Services | null | D | Om Gagan Milk Dairy | null | KCX2 | 3364K670 | 6 | 2015-06-05 | null | 2015-04-28 | cylinder overheating | 2013-09-10 | 2014-03-23 | PC | null | null | 5 | Cylinder no.1 seized due to delivery valve leakage. | null | closed | Set of piston ring , Cylinder liner , Suction valve ring, Spring , Piston , valve discharge assly , bearings and buffer spring replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Vardhan Cold Storage | null | KC3 | 337K4275 | 010/20152016 | 2015-11-05 | 501 | 2015-03-04 | high oil consumption / oil carry over | 2014-01-09 | 2015-03-03 | 600 | null | null | 5 | All piston ring gaps observed 0.8 mm hence replaced and 01 no. K5 Vlave observed leakage from spindle . | null | closed | Piston ring sets and K5 Vlave replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Shiv Shakti Cold Storage | Palanpur | KCX4 | 3384K942 | 007/20152016 | 2015-11-05 | 432 | 2015-02-27 | k5 valve tight / stem broken / leakage | 2014-01-11 | 2015-02-18 | 50 | null | null | 3 | Found leakage at spindle which is observed loose in valve housing although o ring fitted with teflon tape. | null | closed | K5 valve replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Ganraj Cold Storage | Madhya Pradesh | KC3 | 337K4363 | 013/20152016 | 2015-11-05 | 461 | 2015-07-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-01 | 2015-03-03 | 403 | null | null | 2 | Opened the pump found driving gear broken | null | closed | Gearkit replaced
2015-05-23 | Parag Marketing Services | null | D | Carlsberg India Pvt Ltd | Haryana | KC6 | 339K3151 | 7 | 2015-06-05 | null | 2015-11-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-01 | 2015-11-04 | ZH | null | null | 3 | Scoring on oil pump cover plate , Broken driving tang and jammed in bush. | null | closed | Gear kit replaced.
2015-05-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Nilkanth Cold Storage | Nadiad | KCX4 | 3384K855 | 015/20152016 | 2015-11-05 | null | 2015-04-18 | kcx oil pump oil pressure not develop. | 2014-01-01 | 2014-02-24 | 4800 | null | null | 1 | Found driving gear was broken and driven gear wornout. | null | closed | Oil pump element assembly replaced.
2015-05-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Anugrah Cold Storage | Nadiad | KCX4 | 3384K840 | 016/20152016 | 2015-11-05 | null | 2015-03-04 | kcx oil pump oil pressure not develop. | 2013-01-11 | 2014-02-22 | 6000 | null | null | 3 | Opened oil pump and found that driving gear wornout hence replaced . | null | closed | Oil pump element assembly replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Maruti Frozen Food | Mangalore, Karnataka | KC51 | 345K898 | 005/20152016 | 2015-11-05 | 233 | 2014-02-11 | knocking / abnormal sound | 2014-01-05 | 2014-08-21 | 100 | null | null | 3 | Crankpin worn out and bearing wornout at HP Cylinder. Delivery valve observed leakage and piston ring gap measured up to 2.00mm. | null | closed | Piston ring set , Berings and delivery kit replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Umiya Ice Factory | Ahmedabad | KC4 | 338K5036 | 006/20152016 | 2015-11-05 | 279 | 2014-12-15 | knocking / abnormal sound | 2014-01-02 | 2014-03-27 | 1300 | null | null | 1 | Found 2 delevery valve assembly in leakage condition which is resulted in to the entire damage hence , below | null | closed | Piston ring set , Piston , Cylinder liner , NRV , Delivery valve kit.
2015-05-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Nandan Agro Cold Storage | Anand (Gj) | KCX3 | 3374K860 | 004/20152016 | 2015-04-13 | null | 2015-03-15 | knocking / abnormal sound | 2015-01-01 | 2015-02-25 | 250 | null | null | 2 | Knocking sound observed from cyl. No. 1 , discharge valve assly in leakage condition resulting into overheating and cylinder seized. | null | closed | Kit delivery valve , Piston , Piston ring set , gudgeon pin , bushes replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Ronak Agro Food | Dhansura | KCX4 | 3384K936 | 014/20152016 | 2015-11-05 | 364 | 2015-02-21 | oil level glass leakage | 2014-01-11 | 2015-07-02 | 25 | null | null | 3 | Oil level glass found in broken condition | null | closed | Oil level glass broken
2015-05-23 | Kalp Marketing | Gujrat | D | Indus Mega Food | Madhya Pradesh | KC6 | 339k2975 & 76 | 008/20152016 | 2015-11-05 | null | null | shaft seal leakage | 2013-01-10 | 2015-05-21 | 2300 | null | null | 19 | Checked the axial play found 1.8 mm due to thrust ring bronz worn out . | null | closed | Thrust ring bronz & thrust ring steel replaced.
2015-05-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Linde Indial Ltd | Dahej | KCX3 | 3374K703/704 | 003/20152016 | 2015-04-13 | null | 2015-04-04 | shaft seal leakage | 2013-01-12 | 2015-06-02 | 600 | null | null | 2 | Shaft seal assly heavy scoring on face. | null | closed | Shaft Seal assly replaced
2015-05-23 | Kalp Marketing | Gujrat | D | Brahmani Cold Storage | Gandhinagar | KCX3 | 3374k813 | 09/20152016 | 2015-11-05 | 3310 | 2015-02-22 | solenoid valve coil not working / malfunctioning | 2014-01-11 | 2015-02-22 | ZH | null | null | 2 | Solenoide valve coil malfunctioning. | null | closed | Coil for solenoide valve replaced.
2015-05-23 | S M Refrigeration | null | D | Decorating Stone Industries | Jaipur | KC4 | 338K5223 | 1042 | 2015-05-18 | 221 | 2015-04-24 | solenoid valve coil not working / malfunctioning | 2015-01-02 | 2015-04-24 | ZH | null | null | 2 | Solenoid valve coil not woring during commissioning. | null | closed | Coil for solenoide valve replaced.
2015-05-23 | Kalp Marketing | Gujrat | D | Himalaya Ice Factory | Madhya Pradesh | PC2 | 331K2587 | 002/20152016 | 2015-08-04 | 455 | 2015-07-03 | stop valve leakage | 2014-01-01 | 2015-04-04 | 1700 | null | null | 15 | Stop valve lekage | null | closed | Tal valve assly 0850400150 replaced.
2015-05-29 | Multivista Global Pvt Ltd | null | D | Madeena Ice Factory | Chennai | KCX2 | 3364K685 | 003/201516 | 2015-05-15 | 1893 | 2015-04-22 | high oil consumption / oil carry over | 2014-07-01 | 2014-04-03 | 7000 | null | null | 2 | Checked and found oil splasing through one piston . Changed thr piston ring set and VLD O ring for the same . Checked all VLD & NRVs and found ok. Changed the safety valve spring and teflon seat to arrest the safety valve leak. Also informed to customer that the dischagre pressure is high advised to run the compressor with 2 Kg/cm2 working pressure . Also advised customer to open the liquid line stop valve fu;; and ensure 2 kg/cm2 | null | closed | Piston ring set, Oring for VLD Piston, Spring safety valve , Ring teflon for safety valve .
2015-05-29 | Sidharth | null | D | Shri Bholenath Cold Storage | Baharaich | KC3 | 337K4177 | 1516/07 | 2015-05-25 | 439 | 2015-05-15 | kc oil pump low oil pressure problem. | 2014-01-01 | 2014-12-30 | 600 | null | null | 11 | Dismentle oil pump assly and found cut marks on drive and driven gear bush . Also scoring on cover plate. | null | closed | Gear kit replaced.
2015-05-29 | S M Refrigeration | null | D | Shri Balaji Industries | Sandila | KC4 | 338K5229 | 1516/06 | 2015-05-25 | 5251 | 2015-03-05 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-02 | 2015-05-04 | 172 | null | null | 2 | Driving gear shaft tang broken , oil pressure not develop and shaft seal leakage. | null | closed | Gear kit and shaft seal assly replaced.
2015-05-29 | Trade Links | Secunderabad | D | Bharat Ice Plant | Hydrabad | KCX2 | 3364K767 | 7 | 2015-07-05 | null | null | kcx low oil pressure | 2014-01-08 | 2015-11-02 | 250 | null | null | 6 | Oil pressure gratually reduced . | null | closed | Oil pump assembly replaced.
2015-05-29 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K003 | 6 | 2015-07-05 | null | 2015-03-25 | knocking / abnormal sound | 2014-01-07 | 2015-02-15 | 24 | null | null | 7 | Tap bolt of liner broken . | null | closed | Tap bolt replaced 02 nos.
2015-05-29 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K002 | 8 | 2015-07-05 | null | 2015-04-22 | knocking / abnormal sound | 2014-01-07 | 2015-02-14 | ZH | null | null | 7 | Liner tap bolt broken | null | closed | Liner tap bolt replaced
2015-05-29 | Trade Links | Secunderabad | D | Al Yameen Frozen Foods | Mahaboobnagar Dist | KC42 | 344K929 | 1 | 2015-07-05 | 167 | 2015-08-02 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-07 | 2015-08-02 | PC | null | null | 7 | During commisssioning observed SUCTION pressure gauge FAULTY. | null | closed | Suction pressure gauge 16.00 kg/cm2 replaced.
2015-05-29 | Trade Links | Secunderabad | D | The Nalgonda- Ranga Reddy Milk Products | Hydrabad | KCX21 | 3424K003 | 2 | 2015-07-05 | 170 | 2015-02-21 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-10 | 2015-02-21 | PC | null | null | 4 | During commisssioning observed SUCTION pressure gauge 3 kg/cm2 error. | null | closed | Suction pressure gauge 16.00 kg/cm2 replaced.
2015-05-29 | Trade Links | Secunderabad | D | Utkai Ice & Cold Storage | Godavari Dist | KCX4 | 3384K949 | 3 | 2015-07-05 | null | 2015-07-03 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-12 | 2015-07-03 | PC | null | null | 3 | During commisssioning observed discharge pressure gauge 1 kg/cm2 error. | null | closed | Discharge pressure gauge 25.00 kg/cm2 replaced.
2015-05-29 | Trade Links | Secunderabad | D | Archimedis Laboratories Ltd | Nalanda Dist | KCX3 | 3374K801 | 4 | 2015-07-05 | 219 | 2015-03-28 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-09 | 2015-03-28 | PC | null | null | 6 | Suction pressure gauge observed having 2 kg/cm2 error | null | closed | Suction pressure gauge 16.00 kg/cm2 replaced.
2015-05-29 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444k001 | 9 | 2015-07-05 | 230 | 2015-04-17 | shaft seal leakage | 2014-01-05 | 2015-08-13 | 3200 | null | null | 15 | Shaft seal wornout. | null | closed | Shaft seal replaced
2015-05-29 | Parag Marketing Services | null | D | Ice Port | Banglore | KC2 | 336K3189 | FH002/1516 | 2015-05-12 | 5 | 2015-06-05 | shaft seal leakage | 2014-06-22 | 2014-12-26 | 500 | null | null | 6 | Shaft seal bronze ring is wornout . | null | closed | Shaft seal assly replaced.
2015-05-29 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K003 | 5 | 2015-07-05 | null | 2015-03-25 | solenoid valve coil not working / malfunctioning | 2014-01-07 | 2015-02-15 | 24 | null | null | 7 | Cylinder no. 4 loading / unloading problem due to solenoide valve not operate electrically. | null | closed | Solenoide valve coil replaced.
2015-05-31 | Kbtl | Thailand | E | Thai Union | Thailand | KC9 | 340K304 | MAIL | null | null | null | knocking / abnormal sound | 2013-05-15 | null | PC | null | null | null | knocking sound observed from cyl. No.9 due to buffer spring shrinkage(Old type) & resulted in to delivery valve leakage. | null | closed | null
2015-05-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Gsp Crop Science Ltd | Vadodara , Gujarat | KC63 | 346K199 | 1415/66 | 2015-01-16 | null | 2015-04-01 | knocking / abnormal sound | 2014-01-03 | 2014-05-13 | 5000 | null | null | 2 | Heavy damage of all 3 nos HP cylinder resulted due to liquid refregerant entry in to the cylinder , free replacement recommended only for con rods side face wornout. | null | closed | HP Con rod assly replaced 02 NOS.
2015-05-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Surat Agro Cold Storage | Surat, Gujarat | KC3 | 337K4042 | 1415/58 | 2014-04-11 | null | 2014-11-09 | knocking / abnormal sound | 2013-01-09 | 2014-02-05 | 450 | null | null | 8 | Cylinder no. 3 observed knocking sound due to discharge valve leak and cylinder seize. | null | closed | Delivery valve assly , & cylinder assly replaced.
2015-05-31 | null | null | E | Cascade Marine | Uae | KC63 | 346K201 | Mail | 2015-05-20 | null | 2015-05-18 | shaft seal leakage | 2014-01-05 | 2014-11-16 | 2900 | null | null | 6 | Shaft seal leakage | null | closed | Shaft seal required to replaced.
2015-06-03 | Kalp Marketing | Gujrat | D | Anik Industries | Bhopal | KC4 | 338K5062 | 22 | 2015-05-27 | 488 | 2015-04-14 | high oil consumption / oil carry over | 2015-01-04 | 2014-12-08 | 100 | null | null | 4 | close gap of piston rings increased observed up to 0.90 mm | null | closed | replace piston ring sets , cylinder liner,piston
2015-06-03 | Kalp Marketing | Gujrat | D | Annapurna Cold Storage | null | KC4 | 338K5138 | 21 | 2015-05-27 | 475 | 2015-11-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-11 | 2015-01-02 | 50 | null | null | 3 | Tang broken | null | closed | replace gear kit
2015-06-03 | Kalp Marketing | Gujrat | D | Indus Mega Food | null | KC12 | 341K52 | 23 | 2015-05-27 | 491 | 2015-04-20 | knocking / abnormal sound | 2013-11-01 | 2014-05-23 | 1948 | null | null | 17 | discharge valve leakage | null | closed | replace del. Valve, cylinder liner
2015-06-03 | Kalp Marketing | Gujrat | D | Mahadev Cold Storage | Deesa | KCX6 | 3394K472 | 20 | 2015-05-27 | 527 | 2015-05-18 | knocking / abnormal sound | 2015-01-01 | 2015-03-14 | 610 | null | null | 3 | Buffer spring shrinkage | null | closed | replace buffer spring
2015-06-03 | Kalp Marketing | Gujrat | D | Kutch Chemical Industries | null | KC9 | 340K322 | 18 | 2015-05-27 | 374 | 2015-09-05 | knocking / abnormal sound | 2013-01-12 | 2014-08-10 | 750 | null | null | 2 | Delivery valve leak & buffer spring shrink | null | closed | replace buffer spring, del.valve assly,piston,cyl.liner,piston ring set
2015-06-03 | Kalp Marketing | Gujrat | D | Phatemeda Chilling Center | null | PC2 | 331K2719 | 17 | 2015-05-27 | 373 | 2015-05-05 | pc2 oil pump low oil pressure | 2015-01-02 | 2015-04-29 | 40 | null | null | 2 | driving gear found in broken condition, Bush tight with driving gear. | null | closed | Replace gearkit and bushes
2015-06-03 | Kalp Marketing | Gujrat | D | Indus Mega Food | Madhya Pradesh | KC6 | 339K2975 | 19 | 2015-05-27 | 412 | 2015-03-23 | shaft seal leakage | 2013-01-10 | 2014-02-09 | 2250 | null | null | 11 | Frequent wearout of thrust ring | null | closed | replace thrust ring bronze,steel,main bearings,shaft seal assly
2015-06-06 | Gargi Engineering Enterprices Pvt Ltd | null | D | Velankani Ice | null | KCX3 | 3374K798 | 9 | 2015-05-18 | null | 2015-03-31 | high oil consumption / oil carry over | 2014-01-09 | 2015-03-02 | 270 | null | null | 5 | oil carryover 1.5 ltr per 24 hrs | null | closed | Piston ring sets
2015-06-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chandivali Ice Factory | Andheri West | KCX3 | 3374K874 | 8 | 2015-05-18 | 9 | 2015-05-13 | cutouts not working / malfunctioning | 2015-01-03 | 2015-05-13 | ZH | null | null | 2 | HP cutout not tripping | null | closed | HP cutout
2015-06-09 | Multivista Global Pvt Ltd | null | D | Winner Dairy | Pondicherry | KCX2 | 3364K853 | 15/1605 | 2015-01-06 | null | 2015-05-30 | cutouts not working / malfunctioning | 2015-06-04 | 2015-05-30 | ZH | null | null | 1 | Oil diffential pressure cutout not working | null | closed | OP Cut out replaced.
2015-06-09 | Trade Links | Secunderabad | D | Karnataks Milk Dairy Products Pvt Ltd | Banglore | KCX2 | 3364K741 | 004/1516 | 2015-06-06 | 4 | 2015-05-29 | gauge panel board rusty | 2014-06-13 | 2015-05-29 | ZH | null | null | 12 | Gauge board board found rusty and required ss fittings for SS tubing . | null | closed | Panel board single stage & fittings replaced.
2015-06-09 | Parag Marketing Services | null | D | Krishna Kanya Milk Processing | null | KCX3 | 3374K794 | 12 | 2015-05-29 | null | 2015-04-29 | high oil consumption / oil carry over | 2014-09-29 | 2015-02-28 | 204 | null | null | 5 | piston ring close gap increased | null | closed | Piston ring sets
2015-06-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Akash Ice Post | null | KCX3 | 3374K861 | 10 | 2015-05-18 | null | 2015-09-05 | high oil consumption / oil carry over | 2015-01-02 | 2015-09-04 | 200 | null | null | 2 | oil carryover | null | closed | null
2015-06-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Salasar Agro Cold Storage | null | KCX3 | 3374K804 | 24 | 2015-09-06 | null | 2015-05-13 | kc oil pump low oil pressure problem. | 2015-01-09 | 2015-08-05 | 20 | null | null | 4 | liquid entery,lubrication fails and wearing of components | null | closed | replace 3 conrods, 6 bigend bearing sets,gasket set,oring set.
2015-06-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Salasar Agro Cold Storage | null | KCX3 | 3374K799 | 24 | 2015-09-06 | null | 2015-05-13 | kc oil pump low oil pressure problem. | 2015-01-09 | 2015-01-22 | 700 | null | null | 4 | liquid entery,lubrication fails and wearing of components | null | closed | replace 3 conrods, 6 bigend bearing sets,gasket set,oring set.
2015-06-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Al Faiz Enterprises | null | KC3 | 337K3998 | 13 | 2015-05-29 | null | 2015-04-13 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2013-06-29 | 2015-07-01 | 100 | null | null | 18 | driving gear shaft broken | null | closed | Gearkit
2015-06-09 | Trade Links | Secunderabad | D | Mukunda Dairy Products | null | KC3 | 337K4242 | 3 | 2015-04-06 | null | null | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-07-21 | 2015-01-16 | 280 | null | null | 5 | KC Pump low oil presure problem , gearkit replaced run the cpmpressor and drive gear broke.. | null | closed | Gearkit and Oil pump assly replaced.
2015-06-09 | Multivista Global Pvt Ltd | null | D | Mib Ice Plant | Ramanathupuram | PC2 | 331K2653 | 15/1604 | 2015-05-25 | null | 2015-05-15 | shaft seal leakage | 2014-06-30 | 2014-11-30 | 3600 | null | null | 5 | Shaft seal leakage due to face damage . | null | closed | Shaft seal replaced
2015-06-12 | Parag Marketing Services | null | D | Shyam Cold Storage | null | KC3 | 337K4090 | 14 | 2015-06-06 | null | 2015-06-06 | kc oil pump low oil pressure problem. | 2013-11-11 | 2015-02-28 | 250 | null | null | 4 | scoring on cover plate, wearing of bush, gears. | null | closed | oil pump assembly
2015-06-13 | S M Refrigeration | null | D | Carlsberg India Pvt Ltd | Haryana | KC6 | 339K3145 | 1043 | 2015-12-06 | null | 2015-12-06 | crank shaft broken. | 2015-01-01 | 2015-04-21 | 915 | null | null | 4 | crank shaft damaged due to M12 tap holes of direct drive flywheel missing | null | closed | crank shaft damaged due to M12 tap holes of direct drive flywheel missing
2015-06-16 | Trade Links | Secunderabad | D | Profand Vayalat Marine Export PvtLtd Arror Industrial Estate | null | KC63 | 346K212 | 004/201516 | 2015-02-06 | 2129 | 2015-01-06 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-09-26 | 2015-01-05 | ZH | null | null | 8 | Drive gear was tight and the driven gear was broken and gear seating portion of housing is also wornout. | null | closed | Oil pump assembly replaced
2015-06-16 | Trade Links | Secunderabad | D | Kattappna Dairy | Idukki | KCX3 | 3374K737 | 005/201516 | 2015-05-06 | 1822 | 2015-03-06 | kcx oil pump purging problem. | 2014-03-23 | 2015-02-27 | 180 | null | null | 11 | Purging problem. LC 03 14 361 | null | closed | Oil pump assly replaced
2015-06-20 | S M Refrigeration | null | D | SMC Foods Ltd Saharanpur | Uttar Pradesh | KC6 | 339K3105 | 1045 | 2015-06-16 | 3312 | 2015-05-13 | abnormal noise | 2014-01-11 | 2015-02-17 | 600 | null | null | 3 | Found noise in shaft seal due to shaft seal damage. It seems Oring jammed with due to which shaft seal got damaged. | null | closed | Shaft seal assly replaced.
2015-06-20 | S M Refrigeration | null | D | Anand Ice Factory | null | KC4 | 338K5204 | 9 | 2015-03-06 | 5263 | 2015-05-21 | kc oil pump low oil pressure problem. | 2015-01-01 | 2015-04-04 | 630 | null | null | 4 | oil pressure not built up properly | null | closed | Oil pump assly
2015-06-20 | S M Refrigeration | null | D | New Kannouj Cold Storage | null | KC4 | 338K5112 | 8 | 2015-03-06 | 5262 | 2015-05-20 | kc oil pump low oil pressure problem. | 2014-01-09 | 2015-08-02 | 750 | null | null | 5 | driving gear broken | null | closed | Oil pump assly
2015-06-20 | S M Refrigeration | null | D | Vhv Beverage PvtLtd | null | KC4 | 338K5155 | 1049 | 2015-06-16 | 3334 | 2015-05-06 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-11 | 2015-03-15 | 1342 | null | null | 4 | Found oil pump body & cover cutted and driven gear shaft wear out. | null | closed | Oil pump assly
2015-06-20 | S M Refrigeration | null | D | Raja Royal Milk | Uttar Pradesh | KC6 | 339K3117 | 1047 | 2015-06-16 | 2130 | 2015-05-05 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-11 | 2015-04-24 | 39 | null | null | 5 | Driven gear jammed in bush and gear shaft damage | null | closed | Gear kit replaced
2015-06-20 | S M Refrigeration | null | D | Aveen Milk Products | Uttarakhand | KC4 | 338K5125 | 1046 | 2015-06-16 | 3304 | 2015-05-05 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-10 | 2015-12-03 | 49 | null | null | 5 | Drive gear broken , oil pressure not builtup. | null | closed | Oil pump gear kit replaced
2015-06-20 | S M Refrigeration | null | D | Sanjeevani Ice Plant | Amethi, Uttar Pradesh | KC2 | 336K3270 | 10 | 2015-03-06 | 5258 | 2015-08-05 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-12 | 2015-08-05 | ZH | null | null | 5 | Suction pressure gauge out | null | closed | Suction pressure gauge
2015-06-20 | S M Refrigeration | null | D | Raja Royal Milk | Uttar Pradesh | KC6 | 339K3159 | 1048 | 2015-06-16 | 3315 | 2015-05-16 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-12 | 2015-05-16 | ZH | null | null | 5 | Found pressure gauge & K5 Valve defective | null | closed | Pressure gauge 16kg/cm2 & k5 valve replaced
2015-06-20 | S M Refrigeration | null | D | Goyal Dairy | Uttar Pradesh | KC2 | 336K3268 | 1044 | 2015-06-16 | 3282 | 2015-02-04 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-12 | 2015-02-04 | ZH | null | null | 4 | Found pressure gauge 25 Kg/cm2 & 16 Kg/cm2 defective at the time of commissining . | null | closed | Pressure gauges 16.00 & 25.00kg/cm2 replaced
2015-06-24 | S M Refrigeration | null | D | Amroon Foods PvtLtd | Uttar Pradesh | KC72 | 347K364 | 1516/11 | 2015-06-19 | null | 2015-06-18 | hp con rod scoring | 2010-01-04 | 2010-10-11 | 1800 | null | null | 7 | Dismentled the compressor and found deep cut marks on both HP Connecting rod assly. | null | closed | Both HP con rod replaced.
2015-06-26 | Ziya Cold | null | E | Migros | Turkey | KCX4 | 3384K735 | Mail | 2015-06-24 | null | null | compressor seize / jam. | null | null | PC | null | null | null | All pistons , delivery valves crankshaft damaged | null | open | null
2015-06-26 | Trade Links | Secunderabad | D | Goan Bounty | Goa | KC72 | 347K755 | 19 | 2015-06-26 | null | 2015-06-22 | connecting rod scoring | 2014-05-25 | 2014-05-08 | 1800 | null | null | 3 | cyl.04,05,06 conrod wear | null | closed | replace HP 1,LP1 conrod
2015-06-26 | Trade Links | Secunderabad | D | Goan Bounty | Goa | KC72 | 347K753 | 19 | 2015-06-26 | null | 2015-06-22 | connecting rod scoring | 2014-05-25 | 2014-03-08 | 1800 | null | null | 3 | cyl.01,02,03 conrod wear upto 1.3mm&cyl.4,5,6,wear out up to 2.4 | null | closed | replace HP 2,LP1 conrod
2015-06-26 | Kbtl | Thailand | E | Vietnam | null | KCX6 | 3394K456 | Mail | null | null | null | delivery valve touches to piston | null | null | PC | null | null | null | Delivery valve touches to piston | null | closed | null
2015-06-26 | Cool Comfort Private Limited | West Bengal | D | Lokneth Cold Storage | Paragana | KC51 | 345K921 | 1 | 2015-06-26 | 184 | 2015-06-17 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-11-18 | 2015-06-16 | ZH | null | null | 7 | During commissioning of compressor oil pump failed after 45min,oil pump cover plate and housing badly damaged | null | closed | Replace KC oil pump assly
2015-06-26 | Geekay Pneumatic Pvt Ltd | null | D | Kay Kay Exports | Kerala | KCX72 | 3474K001 | 8 | 2015-06-19 | 2132 | 2015-06-06 | kcx low oil pressure | 2015-10-01 | 2015-05-02 | 1000 | null | null | 1 | oil presure drop down | null | closed | replace KCX oil pump
2015-06-26 | Geekay Pneumatic Pvt Ltd | null | D | Kings Seafoods | Kollam | KC51 | 345K897 | 7 | 2015-06-19 | 3052 | 2015-06-16 | knocking / abnormal sound | 2014-04-05 | 2015-07-05 | 180 | null | null | 12 | big end bearings, crankpin dia's wearout | null | closed | replace crankshaft, bearings
2015-06-26 | Geekay Pneumatic Pvt Ltd | null | D | Hic Abf Special Foods Pvt Ltd | Aroor | KC51 | 345K913 | 6 | 2015-06-18 | 1889 | 2015-11-06 | knocking / abnormal sound | 2014-08-24 | 2015-02-20 | 180 | null | null | 6 | piston molten due to delivery valve leakage | null | closed | Del. Valve assly,piston,liner
2015-07-01 | S M Refrigeration | null | D | Goyal Dairy | Uttar Pradesh | KC2 | 336K3268 | 1050 | 2015-01-07 | 3287 | 2015-10-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-12 | 2015-02-04 | ZH | null | null | 4 | Driving gear tight with bushes,tang broken | null | closed | gear kit
2015-07-01 | S M Refrigeration | null | D | Manohar Cold Storage | Uttar Pradesh | KCX2 | 3364K807 | 1051 | 2015-01-07 | 3319 | 2015-05-20 | knocking / abnormal sound | 2014-01-12 | 2015-03-17 | 548 | null | null | 3 | big end bearings wearout & play in piston and gudgeon pin | null | closed | main and conrod bearings,gudgeon pin.
2015-07-11 | Trade Links | Secunderabad | D | Goan Bounty | Goa | KC72 | 347K755 | 20 | 2015-06-26 | null | 2015-06-22 | connecting rod scoring | 2014-05-25 | 2014-03-08 | 2000 | null | null | 3 | Burr was noticed in the crankcase and after inspection it was verified that there is side wear on connecting rods big end side for cy. No. 4/5/6 | null | closed | HP & LP Coonecting rod 02 nos.
2015-07-11 | Trade Links | Secunderabad | D | Goan Bounty | Goa | KC72 | 347K753 | 19 | 2015-06-26 | null | 2015-06-22 | connecting rod scoring | 2014-05-25 | 2014-03-08 | 2000 | null | null | 3 | During annual maintenance inspection , metal burr was observed in the oil sump while cleaning the crankcase. Upon checking it is noticed that there is side wear on connecting ros. Big end side Cyl.no. 1/2/3 : Wear is 1.3mm and cyl no. 4/5/6 is 2.4mm. | null | closed | HP & LP Coonecting rod 03 nos.
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kasturi Ice | Alibaug | KCX2 | 3364K847 | 17 | 2015-06-20 | null | 2015-06-15 | cylinder overheating | 2015-01-03 | 2015-06-05 | 100 | null | null | 2 | Found delivery valve leak , buffer spring shorten causing overheating and damage liner , piston , buffer spring . | null | closed | Delivery valve , liner , piston & buffer spring .
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sumitomo Chemicals | Tarapur | KC4 | 338K4935 | 15 | 2015-06-20 | null | 2015-01-06 | discharge oil str m22 pipe crack | 2013-01-09 | 2014-03-05 | 6000 | null | null | 8 | Replaced top housing of discharge oil strainer. | null | closed | Discharge oil str. Top
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Khira Dist Co Op Milk Prod Ltd | Surat, Gujarat | KC4 | 338K5144 | 028/20152016 | 2015-06-20 | null | 2015-12-06 | high oil consumption / oil carry over | 2014-01-11 | 2015-01-27 | 2200 | null | null | 12 | Replaced all VLD Oring. Checked all NRV due to leakage. | null | closed | Oring & ORV Replaced
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Walinkani Enterprises Ice Factory | Bhayander | KCX3 | 3374K798 | 16 | 2015-06-20 | null | 2015-04-06 | high oil consumption / oil carry over | 2014-01-09 | 2015-03-02 | 1500 | null | null | 5 | Replaced orv & Orings twice and found formation of step in liner no.3 , Hence | null | closed | Liner , piston , piston rings & ORV Replaced
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chintal Cold Storage | Nadiad | KC4 | 338K586 | 25/20152016 | 2015-10-06 | null | 2015-07-04 | k5 valve tight | 2015-01-01 | 2015-07-04 | ZH | null | null | 3 | K5 Valve tighten and could not open during commissioning hence need to replace. | null | closed | Replaced K5 Valve
2015-07-11 | Parag Marketing Services | null | D | Chaman Cold Storage And Ice Factory | Jabalpur | KC3 | 337K4149 | 21 | 2015-04-07 | null | 2015-01-07 | kc oil pump pressure not develop | 2014-02-15 | 2014-10-08 | PC | null | null | 6 | Low oil pressure problem , housing wearout | null | closed | KC oil pump
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kasturi Ice | Alibaug | PC2 | 331K2748 | 18 | 2015-06-25 | 16 | 2015-05-06 | key loose in flywheel | 2015-01-05 | 2015-05-06 | ZH | null | null | 1 | Key was loose in key way hence replaced. | null | closed | Key 9970003306
2015-07-11 | Kalp Marketing | Gujrat | D | Jay Parvati Cold Storage | Deesa | KCX4 | 3384K983 | 30/20152016 | 2015-06-29 | 381 | 2015-02-06 | knocking / abnormal sound | 2015-01-01 | 2015-02-20 | 656 | null | null | 1 | Knocking sound found in two cylinder . Opened all head and discharge valve assly , Buffer spring found ok. Observed that liner housing & piston in both the cylinders are worned out at upper side. | null | closed | Replaced cylinder liner & Piston ring set.
2015-07-11 | Kalp Marketing | Gujrat | D | Mahadev Cold Storage | Deesa | KCX6 | 3394K472 | 27/20152016 | 2015-06-20 | 527 | 2015-05-18 | knocking / abnormal sound | 2015-01-01 | 2015-05-18 | 610 | null | null | 4 | Knocking sound found in direct cylinder , Opened the head and buffer spring length observed 110mm which was reduced. | null | closed | Replaced buffer spring
2015-07-11 | Trade Links | Secunderabad | D | Promog Engineering Services | Solapur | KCX3 | 3374K729 | FH006/1516 | 2015-09-07 | 8 | 2015-05-21 | knocking / abnormal sound | 2014-02-25 | 2014-09-15 | 1600 | null | null | 7 | Crankshaft wornout at cylinder no. 1 approx 2mm. Initially we rejected free spares . Good customer and contineuosly purchasing KCX compressor and spares . Hence as Goodwill & Customer request replaced Crankshaft assly KCX3. | null | closed | Replaced crankshaft
2015-07-11 | Kalp Marketing | Gujrat | D | Uttam Dairy | Khokhra | KC6 | 339K3133 | 29/20152016 | 2015-06-20 | 518 | 2015-08-06 | shaft seal leakage | 2014-01-12 | 2015-12-05 | 600 | null | null | 5 | Opened the shaft seal and found that the stationary ring was wornout. Checked thrust ring bronze and found ok. | null | closed | Replaced Shaft seal assly
2015-07-11 | Gargi Engineering Enterprices Pvt Ltd | null | D | Rajiv Cloride Ltd | Ankleshwar Gujarat | KC2 | 336K3295 | 026/20152016 | 2015-10-06 | null | 2015-11-05 | tah8 valve tight | 2015-01-02 | 2015-11-05 | ZH | null | null | 3 | TAH8 Valve assembly tighten and could not opened during commissioning hence replaced | null | closed | Replaced TAH8 Valve
2015-07-17 | Geekay Pneumatic Pvt Ltd | null | D | Integrated Rubian Exports Ltd | Aroor | KC72 | 347K821 | 10 | 2015-07-15 | null | null | wrong supply of pressure gauges | 2015-01-18 | null | ZH | null | null | 6 | For NH3 control panel box freon gauges used. | null | closed | Freon pressure gauges
2015-07-18 | Geekay Pneumatic Pvt Ltd | null | D | Ksv Ice Plant | null | KCX3 | 3374K783 | 9 | 2015-07-07 | 2138 | 2015-06-27 | high oil consumption / oil carry over | 2014-10-24 | 2015-12-01 | 1750 | null | null | 2 | oil splashung from cylinder no.01 hence piston ring set replaced | null | closed | piston ring set1no.
2015-07-18 | Fridge House | null | D | Dharwad Dist CoOpMilk Prod Soc Ltd | Dharwad | KC9 | 340K344 | 5 | 2015-03-07 | 18 | 2015-06-26 | kc oil pump low oil pressure problem. | 2014-12-23 | 2015-05-02 | 1550 | null | null | 2 | scoring marks on oil pump housing | null | closed | Oil pump assembly,thrust ring, main bearing flywheel end
2015-07-21 | Trade Links | Secunderabad | D | Frigerio Conserva Allana Ltd | Medak Dist | KC72 | 347K698 | 11 | 2015-08-06 | 354 | 2015-06-06 | kc oil pump low oil pressure problem. | 2013-01-11 | 2014-06-29 | 120 | null | null | 6 | Oil pressure not developing | null | closed | Replace oil pump
2015-07-21 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC42 | 344K997 | 14 | 2015-07-13 | 361 | 2015-06-24 | kc oil pump low oil pressure problem. | 2015-01-03 | 2015-06-24 | ZH | null | null | 3 | low oil pressure problem | null | closed | Replace oil pump
2015-07-21 | Trade Links | Secunderabad | D | Mohd Saleem & Co | Ghatkesar | KC42 | 344K973 | 13 | 2015-07-13 | 122 | 2015-04-24 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-12 | 2015-04-24 | ZH | null | null | 4 | driving gear stem sheared and housing worn out. | null | closed | Replace oil pump
2015-07-21 | Trade Links | Secunderabad | D | Frigerio Conserva Allana Ltd | Medak Dist | KC42 | 344K1001 | 16 | 2015-07-13 | 367 | 2015-02-07 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-03 | 2015-01-07 | ZH | null | null | 4 | oil pump gear housing damaged.gears are not rotating in housing | null | closed | Oil pump assly
2015-07-21 | Trade Links | Secunderabad | D | Aurobindo Pharma Pvt Ltd | Shrikakulam | KC63 | 346K220 | 17 | 2015-07-14 | 372 | 2015-10-07 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-01-12 | 2015-10-07 | ZH | null | null | 6 | driving gear stem sheared and housing worn out. | null | closed | oil pump assly.gear kit, pump cover
2015-07-21 | Trade Links | Secunderabad | D | Archimedis Laboratories Ltd | Nalanda Dist | KCX3 | 3374K801 | 10 | 2015-08-06 | 246 | 2015-05-22 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2014-01-09 | 2015-03-28 | 120 | null | null | 6 | Replace pump element assly,OPR. | null | closed | KCX oil pump
2015-07-21 | Trade Links | Secunderabad | D | Dodla Dairy Ltd Devrapalem | null | KCX4 | 3384K996 | 15 | 2015-07-13 | 271 | 2015-06-29 | knocking / abnormal sound | 2015-01-01 | 2015-04-03 | 1600 | null | null | 2 | cylinder no.01 piston siezed due to delivery valve back leakage | null | closed | Replace piston, piston ring set,del.valve.
2015-07-21 | Multivista Global Pvt Ltd | null | D | Sr Ice Plant No 176 | Theresapuram Tuticorin Dist | KC3 | 337K4422 | 15/1606 | 2015-06-15 | null | 2015-06-14 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-04-18 | 2015-06-14 | ZH | null | null | 2 | Oil pressure gauge needle damaged. Suction pressure 2.00 kg/cm2 error. | null | closed | LP/OP Pressure gauge
2015-07-21 | Trade Links | Secunderabad | D | Mohd Saleem & Co | Ghatkesar | KC3 | 337K4287 | 12 | 2015-08-06 | 307 | 2015-05-23 | solenoid valve coil not working / malfunctioning | 2014-01-10 | 2015-05-23 | ZH | null | null | 5 | Solenoide valve not operating electrically | null | closed | Replace SV coil
2015-07-21 | Multivista Global Pvt Ltd | null | D | VVMarine Products | Tuticorin Dist | KC72 | 347K830 | 15/1607 | 2015-06-07 | null | 2015-03-07 | tah8 valve broken | 2015-10-03 | 2015-03-07 | ZH | null | null | 4 | TAH8 Valve broken and feruule not fitting so change tah8 valve and ferrule from customer stock. | null | closed | TAH8 Valve & Ferrule.
2015-07-22 | Trade Links | Secunderabad | D | Nagahanuman Fish & Ice Plant | Godavari Dist | KC3 | 337K4407 | 18 | 2015-07-14 | null | 2015-06-17 | shaft seal leakage | 2015-01-03 | 2015-04-24 | 1092 | null | null | 1 | Observed heavy leakage from shaft seal due to shaft seal assly wornout , Axial clearance observed 3.00mm - Thrust ring abnormally wornout also also pump housing wornout. | null | closed | Shaft seal assly , oil pump assly , thrust ring , main bearing bush replaced.
2015-07-25 | Parag Marketing Services | null | D | Parag Marketing | null | KCX4 | 3384K106 | Mail | null | null | 2015-07-25 | leakges in fitting & flange | null | null | PC | null | null | null | leakages in fitting and flange | null | closed | null
2015-07-25 | S M Refrigeration | null | D | PCDF Ltd | Kanuaj Dugdh, Uttar Pradesh | KC2 | 336K3266 | 1516/12 | 2015-07-13 | 5253 | 2015-04-05 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-12 | 2015-04-05 | ZH | null | null | 5 | Discharge pressure gauge found defective during commissioning of compressor. | null | closed | Discharge pressure gauge 25.00Kg/cm2 replaced.
2015-07-25 | Morgan | null | E | Sehwan Ice Plant | null | KC6 | null | Mail | null | null | 2015-07-25 | solenoid valve coil not working / malfunctioning | null | null | PC | null | null | null | solenoid coil not working | null | closed | Replaced coil
2015-07-25 | Morgan | null | E | Au Fisheries | null | KC6 | 339K3128 | Mail | 2015-03-25 | null | null | solenoid valve coil not working / malfunctioning | null | null | PC | null | null | null | solenoid coil not working | null | closed | Sol. Valve coil
2015-07-25 | Morgan | null | E | Kotli International | null | KC6 | 339K2093 | Mail | 2015-03-25 | null | 2015-07-25 | solenoid valve not working / malfunctioning | null | null | PC | null | null | null | Solenoid valve not working | null | closed | Replaced valve
2015-07-25 | S M Refrigeration | null | D | Glaciars Sandila Industrial Area | Uttar Pradesh | KC4 | 338K5225 | 1516/13 | 2015-07-13 | 5270 | 2015-01-06 | tah8 valve assembly problem | 2015-01-02 | 2015-01-06 | ZH | null | null | 4 | TAH8 Valve assembly found defective during commissioning of compressor | null | closed | TAH8 Valve assembly replaced.
2015-07-25 | Cool Point | null | E | Saudi | null | KCX4 | 3384K845 | Mail | null | null | 2015-07-25 | welding leakage from compressor discharge | 2013-12-12 | null | PC | null | null | null | leak from weld joint of compressor discharge | null | closed | null
2015-07-31 | Geekay Pneumatic Pvt Ltd | null | D | Cap Seafoods | Kochi | KC72 | 347K775 | 011/201516 | 2015-07-22 | 3006 | 2015-07-13 | kc oil pump low oil pressure problem. | 2014-07-28 | 2014-12-08 | 1980 | null | null | null | During inspection found that the pressure regulator spring and ball was damaged and also found overflow valve spring tension is reduced . Checked the cover plate and gear and found ok.Also found 1 no. ORV was damaged. | null | closed | Replaced OPR ball , spring , Overflow spring & ORV.
2015-08-04 | Parag Marketing Services | null | D | Bora Agro Foods | Pune | KC3 | 337K4014 | 22 | 2015-08-07 | 178810 | 2015-04-13 | delivery valve leakage | 2013-07-30 | 2014-06-16 | 750 | null | null | 12 | overheating of cylinder no.3 due to delivery valve leakage. | null | closed | Delivery valve assly replaced.(old type)
2015-08-04 | Trade Links | Secunderabad | D | Sai Balaji Cold Storage | Khammam Dist | KC2 | 336K3294 | 19 | 2015-07-21 | null | 2015-07-15 | knocking / abnormal sound | 2015-01-01 | 2015-03-23 | 1232 | null | null | 2 | Abnormal sound from cylinder no.1 piston had seized due to overheating due to delivery valve backleaking. Hence liner , piston rings , piston had also damaged. | null | closed | Delivery valve ,Piston , Piston rings , Liner & Bearings replaced.
2015-08-04 | Parag Marketing Services | null | D | Bafna Cold Storage | Sangli | KC2 | 336K3155 | 23 | 2015-08-07 | 178808 | 2015-06-07 | shaft seal leakage | 2014-03-25 | 2015-02-21 | PC | null | null | 12 | Leakage from seat , nominal scarches lapping done but leakage not stopped. | null | closed | Shaft seal assly replaced
2015-08-04 | Trade Links | Secunderabad | D | Mohd Saleem & Co | Ghatkesar | KC3 | 337K4287 | 20 | 2015-07-28 | 377 | 2015-07-25 | solenoid valve not working / malfunctioning | 2014-01-10 | 2015-05-23 | PC | null | null | 5 | Solenoid valve assly not woring hence replaced | null | closed | Replaced solenoid valve assly
2015-08-12 | Fridge House | null | D | Bangalore Urban Society | null | KCX3 | 3374K97 | FH007/1516 | 2015-10-08 | null | 2015-06-08 | cutouts not working / malfunctioning | 2014-09-30 | 2015-06-08 | ZH | null | null | 11 | LP & OP cutout not working. | null | closed | Replace LP< LP/OP cutouts.
2015-08-12 | Trade Links | Secunderabad | D | Aurobindo Pharma Pvt Ltd | Hatnoor, Madhya Pradesh | KC42 | 344K937 | 22 | 2015-10-08 | null | 2015-08-08 | flywheel wobbling | 2014-01-08 | 2015-04-21 | 500 | null | null | 8 | flywheel keyway, crankshaft keyway and key damaged. | null | closed | Replace crankshaft,flywheel,key, retaining plate
2015-08-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Naik Oceanics PvtLtd | Midc Taloja | KC72 | 347K758 | 29 | 2015-03-08 | null | 2015-07-29 | compressor loading problem | 2014-01-05 | 2015-07-20 | ZH | null | null | 10 | Zero hour trouble found during compressor commissioning that found solenoid valve not working / not ok. All 3 valves rubber cut and 4th no. coil problem. | null | closed | Solenoid valve coil replaced 01 no.
2015-08-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hmg Industries Ltd | Pawane | KC93 | 348K123 | 25 | 2015-07-18 | 26 | 2015-07-16 | cutouts not working / malfunctioning | 2015-01-04 | 2015-07-16 | ZH | null | null | 15 | Oil pressure cut out was tripping the oil pressure of compressor was 2.00kg/cm2. Coil was heating continusly through T2 Connection was phase after delay. | null | closed | OP Cut out replaced.
2015-08-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chandivali Ice Factory | Andheri West | KCX3 | 3374K761 | 27 | 2015-03-08 | null | 2015-07-31 | high oil consumption / oil carry over | 2014-01-06 | 2014-11-08 | 6000 | null | null | 14 | For oil carry over problem all ORV & Orings replaced. | null | closed | All ORV & Orings replaced.
2015-08-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chandivali Ice Factory | Andheri West | KCX3 | 3374K762 | 28 | 2015-03-08 | null | 2015-01-08 | high oil consumption / oil carry over | 2014-01-06 | 2014-04-07 | 6000 | null | null | 13 | Direct piston found damage , hence all 3 no. piston ring sets replaced with ORV - 03 NOS , VLD Orings and piston - 01 no. | null | closed | Replaced Piston 01 no. , Ring set 03 nos, VLD Orings 03 nos & ORV 03 Nos.
2015-08-17 | Kalp Marketing | Gujrat | D | Jay Parvati Cold Storage | Deesa | KCX4 | 3384K983 | 31 | 2015-10-08 | 315 | 2015-10-07 | knocking / abnormal sound | 2015-01-01 | 2015-02-20 | 656 | null | null | 1 | overheating of cyl.no.01 | null | closed | cylinder liner2, piston ring set2,housing manifold1
2015-08-21 | Trade Links | Secunderabad | D | S M Sea Marine | null | KC3 | 337K4228 | 21 | 2015-07-28 | 455 | 2015-07-24 | flywheel wobbling | 2014-01-06 | 2015-01-29 | 540 | null | null | 7 | Flywheel wobbling keyway of c.shaft and flywheel damaged | null | closed | c.shaft ,flywheel 1012,key.
2015-08-25 | Kalp Marketing | Gujrat | D | Hapa Cold Storage | Ahmedabad | KCX3 | 3374K739 | 037/20152016 | 2015-10-08 | 376 | 2015-05-23 | cylinder overheating | 2014-01-03 | 2014-11-27 | 3300 | null | null | 8 | Discharge valve assembly found leakage - 01 no. and Pressure gauge has error. | null | closed | Replaced discharge valve01 no. and pressure gauge 16.00kg/cm2.
2015-08-25 | Kalp Marketing | Gujrat | D | New Sagar Cold Storage -2 | Veraval, Gujarat | KC51 | 345K947 | 041/20152016 | 2015-08-18 | 179680 | 2015-07-08 | cylinder overheating | 2015-01-04 | 2015-07-27 | ZH | null | null | 3 | Low oil pressure and overheating of compressor . Liner seat gasket slip off resulting into overheating of liner & piston. Also oil pressure suddenly drop after 1 hour. Replaced oil pump . Also due to overheating o1 no. delivery valve valve seat damage. | null | closed | Oil pump assly , Pressure gauge , Delivery valve seat replaced.
2015-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amit Ice Factory | Vadodara , Gujarat | KC4 | 338K5135 | 032/20152016 | 2015-10-08 | null | 2015-12-05 | high oil consumption / oil carry over | 2014-01-10 | 2014-12-22 | 2000 | null | null | 2 | Replaced VLD Orings and checked NRV found ok but during trail cyl.no. 3 observed overheating and found delivery valve leakage. | null | closed | Replaced discharge valve kit.
2015-08-25 | Kalp Marketing | Gujrat | D | Janta Ice Cream Co | Kalol Road | KC42 | 344K1012 | 040/20152016 | 2015-08-14 | 383 | 2015-05-08 | intermediate pressure high | 2015-01-04 | 2015-10-06 | 800 | null | null | 2 | Opened the head and found discharge valve leak . Lapping done but not ok hence replaced. | null | closed | Replaced Delivery valve seat & Kit delivery valve.
2015-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | H N Indigos P Ltd | Navsari | KC31 | 343K1461 | 033/20152016 | 2015-10-08 | null | 2015-06-22 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-03 | 2015-06-20 | ZH | null | null | 3 | Drive gear jammed in bushing and found in broken condition. | null | closed | Oil pump gear kit replaced.
2015-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | K A Malle Pharma Ltd | Ankleshwar Gujarat | KC3 | 337K4288 | 035/20152016 | 2015-10-08 | null | 2015-11-03 | knocking / abnormal sound | 2014-01-10 | 2015-12-03 | 1450 | null | null | 5 | Discharge valve assly leakage . Piston seized in liner and damaged entire cylinder. | null | closed | Replaced valve kit , Piston , Piston ring set , Gudgeon pin , Buffer spring and thrust ring bronze.
2015-08-25 | Kalp Marketing | Gujrat | D | Giriraj Milk Pproduct | Rajkot, Gujrat | KC4 | 338K5110 | 036/20152016 | 2015-10-08 | 473 | 2015-05-22 | oil pressure not buildup | 2014-01-09 | 2015-01-31 | 1000 | null | null | 4 | Observed that both gear shaft wornou. | null | closed | Replaced drive and driven gear
2015-08-25 | Kalp Marketing | Gujrat | D | Azad Ice Factory | Jamnagar | KC3 | 337K4368 | 039/20152016 | 2015-10-08 | 601 | 2015-10-06 | solenoid valve not working / malfunctioning | 2015-01-02 | 2015-03-31 | 980 | null | null | 2 | Solenoid valve not working loading unloading problem hence replaced . | null | closed | Solenoid valve with coil replaced.
2015-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | H N Indigos P Ltd | Navsari | KC4 | 338K5235 | 034/2015/2016 | 2015-10-08 | null | 2015-12-06 | t connector of gauge damaged & leakage | 2014-01-12 | 2015-12-06 | ZH | null | null | 6 | Thread of T connector of pressure gauge found damage and leakage. | null | closed | Replaced T Connector of gauge.
2015-08-25 | Kalp Marketing | Gujrat | D | Sagar Samrat Sea Food | Porbandar | KC72 | 347K781 | 038/20152016 | 2015-10-08 | 551 | 2015-05-26 | thrust ring bronze wornout | 2014-01-08 | 2015-01-31 | 430 | null | null | 5 | During crancase cleaning bronze particle found in oil due to bronze thrust ring wornout. | null | closed | Replaced bronze thrust ring.
2015-08-28 | Trade Links | Secunderabad | D | Modern Frozen Foods | null | KC72 | 347K743 | 23 | 2015-08-25 | null | 2015-08-24 | crankshaft key way damaged | 2014-01-04 | 2014-07-28 | 2600 | null | null | 3 | Customer had observed wobbling of flywheel and they had removed the flywheel . Inspection of the flywheel , Crankshaft and Key way was done . Keyway of crankshaft had chip off on one side and key had damaged. This resulted to wobbling of flywheel. | null | closed | Replaced crankshaft , Flywheel and Key.
2015-09-01 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC2 | 336K3284 | 27 | 2015-08-27 | 364 | 2015-06-26 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-01-01 | 2015-06-26 | ZH | null | null | 5 | Observed error in suction pressure gauge up to 2.00 Kg/cm2. | null | closed | Suction pressure gauge replaced
2015-09-04 | S M Refrigeration | null | D | Cralsberg Indial | Dharuhera Haryana | KC6 | 339K3145 | 1053 | 2015-08-26 | 952 | 2015-08-13 | high oil consumption / oil carry over | 2015-01-01 | 2015-04-21 | 1297 | null | null | 4 | Observed noise from cylinder no. 1,2,4&5due to high wearing of liner bore , Piston , Piston ring set. The abnormal noise | null | closed | Cylinder liner and piston ring sets replaced
2015-09-04 | S M Refrigeration | null | D | Frigerio Conserva Allana Ltd | New Delhi | KC9 | 340K350 | 1052 | 2015-08-27 | 1495 | 2015-08-20 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-06 | 2015-08-20 | ZH | null | null | 2 | During commissioning driven gear and shaft jammed in bush resulting into drove shaft broken withing 6 houres . | null | closed | Replaced oil pump assly.
2015-09-04 | S M Refrigeration | null | D | Manohar Cold Storage | Uttar Pradesh | KCX2 | 3364K807 | 1054 | 2015-08-26 | 6563 | 2015-05-08 | knocking / abnormal sound | 2014-01-12 | 2015-03-17 | 827 | null | null | 3 | Found abnormal sound from crankcase , Dismentle the compressor both big end bearings and main bearings cut marks and material diposited at crankshaft. | null | closed | Piston , Piston ring set, Bearings replaced.
2015-09-04 | S M Refrigeration | null | D | Shri Balaji Industries | Sandila | KC3 | 337K4409 | 1516/15 | 2015-08-19 | null | 2015-07-28 | shaft seal leakage | 2015-01-03 | 2015-09-05 | 1606 | null | null | 2 | Shaft seal assly checked found all set screw open in rotary seal due to this shaft seal assly has badly damaged. | null | closed | Shaft seal assly replaced.
2015-09-04 | S M Refrigeration | null | D | Komal Ice Factory | Jagdishpur | KC4 | 338K5079 | 1516/14 | 2015-08-19 | null | 2015-07-26 | shaft seal leakage | 2014-01-05 | 2014-11-22 | 1850 | null | null | 6 | Shaft seal assly found heavy cut marks on stationary sealing ring and axial clearance found 3.00mm. | null | closed | Shaft seal assly replaced.
2015-09-04 | Trade Links | Secunderabad | D | Keerti Technocarts & Geospatial P Ltd | Spsp Nellore | KC4 | 338K5259 | 24 | 2015-08-27 | null | 2015-12-06 | solenoid valve coil not working / malfunctioning | 2015-01-04 | 2015-12-06 | ZH | null | null | 2 | Solenoid valve not operating electrically. | null | closed | Solenoid valve coil replaced 02 nos.
2015-09-04 | Trade Links | Secunderabad | D | Sree Valli Ice | Guntur | KC4 | 338K5247 | 25 | 2015-08-27 | null | 2015-12-06 | solenoid valve coil not working / malfunctioning | 2015-01-03 | 2015-12-06 | ZH | null | null | 3 | Solenoid valve not operating electrically. | null | closed | Solenoid valve coil replaced 02 nos.
2015-09-05 | Trade Links | Secunderabad | D | Samba Siva Ice Factory | Godavari Dist | KC3 | 337K4237 | 26 | 2015-08-27 | null | 2015-06-08 | kc oil pump low oil pressure problem. | 2014-01-07 | 2014-09-27 | 4500 | null | null | 2 | Driving and driven gear had worn out abnormally.Oil pump housing , oil and filters are in good condition. | null | closed | Replaced gear kit
2015-09-11 | Trade Links | Secunderabad | D | Shri Maheshwari Cold Storage | Kadap Dist | KC3 | 337K4237 | 28 | 2015-08-31 | null | 2015-08-13 | kc oil pump low oil pressure problem. | 2014-01-07 | 2014-09-27 | 4500 | null | null | 2 | Driving and driven gear had worn out abnormally.Oil pump housing , oil and filters are in good condition. | null | closed | Replaced gear kit
2015-09-11 | S M Refrigeration | null | D | Flex Foods Ltd | Dehradun | KC93 | 348K120 | 1055 | 2015-09-04 | 1498 | 2015-09-01 | knocking / abnormal sound | 2015-01-02 | 2015-06-22 | 940 | null | null | 4 | Abnormal sound / Noise from cylinder no. 4 due to delivery valve leakag resulting piston seized with liner. | null | closed | Replaced cylinder liner , Piston , Delivery valve and piston ring set.
2015-09-18 | Kalp Marketing | Gujrat | D | Ronak Agro Food | Dholpur | KCX3 | 3374K815 | 047/20152016 | 2015-10-09 | 515 | 2015-06-22 | cutouts not working / malfunctioning | 2014-01-11 | 2015-02-07 | 400 | null | null | 8 | OP Cutout switch not working properly. | null | closed | OP Cut out replaced.
2015-09-18 | Kalp Marketing | Gujrat | D | Ganraj Cold Storage | Ujjain | KC3 | 337K4360 | 043/20152016 | 2015-09-09 | 611 | 2015-09-08 | kc oil pump low oil pressure problem. | 2015-01-01 | 2015-08-08 | 2000 | null | null | 7 | Drive shaft broken . | null | closed | Kit oil pump gear replaced
2015-09-18 | Kalp Marketing | Gujrat | D | Jinny Marine Traders | Veraval, Gujarat | KC4 | 338K946 | 046/20152016 | 2015-10-09 | null | 2015-03-09 | kc oil pump pressure not develop | 2015-01-04 | 2015-08-22 | 62 | null | null | 4 | Driving gear shaft tang broken twice . Also K5 valve tangs observed twised. Due to riving gear and cover plate problem, Oil pump housing bore worn out & needs to be replace oil pump assly. | null | closed | Oil pump assly1 , gear kit 2& K5 Valve3 replaced.
2015-09-18 | Kalp Marketing | Gujrat | D | Star Marine Products | Veraval, Gujarat | KC51 | 345K946 | 045/20152016 | 2015-10-09 | null | 2015-08-24 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-04 | 2015-08-17 | ZH | null | null | 4 | Drive shaft broken and slonoid valve coil not working. | null | closed | Gear kit and coil replaced.
2015-09-18 | null | null | E | Sindbad Fisheries | Pakistan | KC63 | 346K202 | null | 2015-09-16 | null | 2015-09-18 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | null | null | PC | null | null | null | oil pump gears broken | null | closed | Replace gear kit and bush
2015-09-18 | Kalp Marketing | Gujrat | D | Sanchi Dairy | Ujjain | KCX3 | 3374K756 | 044/20152016 | 2015-09-09 | 610 | 2015-03-08 | knocking / abnormal sound | 2015-01-05 | 2015-07-25 | 1500 | null | null | 2 | Observed 01 no. BE bearing and main bearing bush wornout.Also crankshaft wornout. | null | closed | Big end bearing , Main bearing replaced
2015-09-20 | Kalp Marketing | Gujrat | D | Hapa Cold Storage | Ahmedabad | KCX3 | 3374K739 | 049/20152016 | 2015-09-16 | 565 | 2015-07-09 | discharge filter manifold leakage. | 2014-01-03 | 2014-11-27 | 2000 | null | null | 8 | Manifold threading observed loose , bling plug not fitted properly. Due to this compressor running at higher risk. | null | closed | Housing manifold relaced
2015-09-20 | Trade Links | Secunderabad | D | Aurobindo Pharma Pvt Ltd | Medak Dist | KC42 | 344K937 | 30 | 2015-05-09 | null | 2015-04-09 | flywheel wobbling | 2014-01-08 | 2015-04-21 | 500 | null | null | 8 | Continuation of first complaint observed thrist ring and main bearing bushes wornout. | null | closed | Replaced bearing bushes & Thrust ring.
2015-09-20 | Geekay Pneumatic Pvt Ltd | null | D | Zam Zam Ice Plant | Cherthala | KCX2 | 3364K828 | 013/201516 | 2015-07-09 | 3021 | 2015-08-24 | high oil consumption / oil carry over | 2015-03-03 | 2015-06-16 | 1545 | null | null | 3 | Observed oil is splashing through cylinder no. 2 also found 01 no. NRV is malfunctioning. | null | closed | Replaced Piston ring set and NRV
2015-09-20 | Kalp Marketing | Gujrat | D | New Sagar Cold Storage | Veraval, Gujarat | KC51 | 345K947 | 048/20152016 | 2015-09-14 | 954 | 2015-01-09 | kc oil pump low oil pressure problem. | 2015-01-04 | 2015-07-27 | 40 | null | null | 3 | Oil pump assly with both filters , gaskets , Orings , 01 no. pressure gauge replaced | null | closed | Oil pump assly with both filters , gaskets , Orings , 01 no. pressure gauge replaced
2015-09-20 | Geekay Pneumatic Pvt Ltd | null | D | ASMarine Industries Pvt Ltd | Kochi | KC51 | 345K927 | 012/201516 | 2015-08-21 | 3027 | 2015-07-27 | knocking / abnormal sound | 2014-12-28 | 2015-05-23 | 80 | null | null | 5 | Sound observed from discharge stop valve due to spindle of the valve is slightly loosen. | null | closed | Stop valve assembly replaced.
2015-09-21 | Trade Links | Secunderabad | D | Hatsun Agro Products Ltd | Hydrabad | KC3 | 337K4193 | 29 | 2015-05-09 | null | 2015-08-25 | kc pump low oil pressure loading delay problem | 2014-01-04 | 2014-07-15 | 2600 | null | null | 3 | Observed late loading nerly 5 minuts. Oil condition filters ok, Oil pump gear bushes found ok. But cover wornout abnormally. Axial clearance ok. Recommended new type of oil pump gears & cover. | null | closed | Pump gearkit replaced.
2015-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Castelrock Fisheries Pvt Ltd | Taloja, Mh | KC3 | 337K4320 | 30 | 2015-03-08 | 31 | 2015-08-24 | cutouts not working / malfunctioning | 2014-01-11 | 2015-07-30 | ZH | null | null | 8 | In pannel box observed 2 nos LP Cutouts instead of 1HP & 1HP. | null | closed | HP CUTOUT.
2015-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Foods Pvt Ltd | Taloja, Mh | KC3 | 337K4233 | 31 | 2015-12-08 | 34 | 2015-08-24 | kc oil pump low oil pressure problem. | 2014-01-06 | 2015-08-08 | ZH | null | null | 2 | Oil pressure observed very low due to scoring. | null | closed | Replaced gearkit.
2015-09-22 | Sidharth | null | D | Uppal Agro Resh India PvtLtd | Mohali | KC3 | 337K4325 | 1056 | 2015-09-19 | 1169 | 2015-09-13 | kc oil pump no oil pressure | 2014-01-12 | 2015-02-09 | 32 | null | null | 9 | Oil pump seized. | null | closed | Replaced gearkit.
2015-09-22 | S M Refrigeration | null | D | Amsons Laboratories Pvt Ltd | Haryana | PC2 | 331K2663 | 1057 | 2015-09-19 | 3400 | 2015-09-08 | pc2 oil pump low oil pressure | 2014-01-07 | 2015-04-25 | 180 | null | null | 9 | Oil pressure problem due to drive gear damage and cover wornout. Also leakage in stop valves from taflon packing. | null | closed | Replaced gearkit ,Tal 32,50 Taflon & Gland packing.
2015-09-22 | S M Refrigeration | null | D | Creamy Foods Limited | Uttar Pradesh | KC6 | 339K3196 | 1059 | 2015-09-19 | 6561 | 2015-08-08 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-01-06 | 2015-02-08 | ZH | null | null | 2 | Pressure gauge 16.00Kg/cm2 defective. | null | closed | Replaced Pressure gauge 16.00Kg/cm2
2015-09-22 | Parag Marketing Services | null | D | Excell Industries Ltd | Ratnagiri | KCX6 | 3394K429 | 24 | 2015-08-07 | 180562 | 2015-05-23 | shaft seal leakage | 2014-01-05 | 2014-08-22 | PC | null | null | 3 | Shaft seal found scoring on both seal, Bronze thrust ring found scoring . Also TAH8 Valve steam jammed. | null | closed | Replaced shaft seal assly , TAH8 Valve , bronze thrust ring .
2015-09-22 | S M Refrigeration | null | D | Namaste India Foods PvtLtdHapur | Uttar Pradesh | KC2 | 336K3293 | 1058 | 2015-09-19 | 6564 | 2015-07-08 | stop valve leakage | 2015-01-01 | 2015-06-08 | ZH | null | null | 7 | Leakage from taflon packing of discharge stop valve. | null | closed | Replaced Taflon
2015-09-25 | Kalp Marketing | Gujrat | D | Navarang Sea Foods | null | KC72 | 347K844 | 52 | 2015-09-21 | 641 | 2015-10-09 | kc oil pump low oil pressure problem. | 2015-01-05 | 2015-08-06 | ZH | null | null | 1 | driven gear jammed in bush | null | closed | gear kit
2015-09-25 | Kalp Marketing | Gujrat | D | Kailash Cold Storage | null | KCX4 | 3384K965 | 53 | 2015-09-21 | 396 | 2015-09-15 | knocking / abnormal sound | 2014-01-12 | 2015-02-21 | 1074 | null | null | 2 | knocking sound in cylinder no.01 | null | closed | cylinderliner,piston,pistonringset
2015-09-25 | Kalp Marketing | Gujrat | D | Maruti Cold Storage | null | KCX3 | 3374K836 | 51 | 2015-09-21 | 630 | 2015-04-09 | knocking / abnormal sound | 2014-01-12 | 2015-09-02 | 1541 | null | null | 2 | delivery valve leak | null | closed | d.valve kit
2015-09-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shree Sulphurics PvtLtd | Ankleshwar Gujarat | KCX6 | 3394K466 | 50 | 2015-03-09 | null | 2015-07-21 | shaft seal leakage | 2014-01-12 | 2015-06-24 | 350 | null | null | 6 | shaftseal face deep scoring marks | null | closed | Shaft seal assly.
2015-09-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bismilla Cold Storage | Taloja, Mh | KC2 | 336K3247 | 36 | 2015-09-15 | null | 2015-12-09 | control panel box leakage | 2014-01-10 | 2015-09-15 | ZH | null | null | 11 | During commissioning , at 4 points of T-Connection assly . Leakage was observed . | null | closed | Replaced panel box
2015-09-28 | Parag Marketing Services | null | D | Ajanta Brewaries | Aurangabad | PC2 | 331K2274 | 49 | 2014-01-11 | null | 2014-02-22 | knocking / abnormal sound | 2013-04-12 | 2014-02-22 | PC | null | null | 2 | Knocking sound from cylinder no. 1 found breakdown in cylinder. | null | closed | Replaced all cylinder assly
2015-09-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vidhi Dyechem(P) Ltd | Dhatav | KC6 | 339K3077 | 34 | 2015-09-15 | 38 | 2015-03-09 | knocking / abnormal sound | 2014-01-07 | 2015-02-09 | PC | null | null | 14 | During commissioning delivery valve found leakage resulting piston damage and buffer spring length found 109mm. | null | closed | Replaced delivery valve , Buffer spring , Piston & Piston ring set.
2015-10-02 | Kalp Marketing | Gujrat | D | Jinny Marine Traders | Veraval, Gujarat | KC4 | 338K5262 | 055/20152016 | 2015-09-29 | 540 | 2015-09-19 | kc oil pump low oil pressure problem. | 2015-01-04 | 2015-08-22 | 280 | null | null | 4 | Low oil pressure. After replacement of new VLD pressure observed 14Kg/cm2 and oil pressure drop sudenly . Hence installed old pump from other compressor , which is working satisfactory. | null | closed | Gear kit replaced.
2015-10-02 | Cool Comfort Private Limited | West Bengal | D | Essex Marine PvtLtd | West Bengal | KC72 | 347K735 | 3 | 2015-09-17 | 467 | 2015-07-17 | kc oil pump low oil pressure problem. | 2015-03-26 | 2015-06-26 | 900 | null | null | 3 | Oil pressure not developing. | null | closed | replace oil pump assly
2015-10-02 | Kalp Marketing | Gujrat | D | Bhopal Glue Chem PvtLtd | Bhopal | KC3 | 337K4449 | 054/20152016 | 2015-09-20 | 640 | 2015-09-24 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-06 | 2015-08-31 | 200 | null | null | 2 | Driving gear shaft broken. | null | closed | Gearkit Replaced
2015-10-02 | Cool Comfort Private Limited | West Bengal | D | Utkal Udyog Cold Storage | Odisha | KCX4 | 3384K971 | 2 | 2015-09-17 | 421 | 2015-10-09 | knocking / abnormal sound | 2014-01-12 | 2015-07-22 | 450 | null | null | 6 | Abnormal sound from cylinder no.03 | null | closed | cylinder liner,piston,piston ring set.
2015-10-02 | Kalp Marketing | Gujrat | D | Kriti Cold Storage | Veraval, Gujarat | KC4 | 338K5111 | null | 2015-09-20 | null | null | leak from c.case foot and shell weld run due to crack | 2014-01-10 | 2014-01-09 | 2000 | null | null | 1 | leak from foot and c.case weld run | null | closed | Shaft seal assly, del valve 03Nos.
2015-10-05 | Geekay Pneumatic Pvt Ltd | null | D | Boon Ice Plant | Muvattupuzha | KCX3 | 3374K743 | 015/201516 | 2015-09-28 | 5870 | 2015-09-09 | cylinder loading problem | 2014-03-30 | 2014-10-20 | 3190 | null | null | 7 | Found cylinders both tap bolts were broken. | null | closed | Replaced tap bolts , Spring & Piston ring set
2015-10-05 | Fridge House | null | D | Taj Cold Storage | Gulbarga Dist | KC42 | 344K991 | FH008/1516 | 2015-09-28 | 15 | 2015-09-23 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-02-27 | 2015-09-23 | ZH | null | null | 7 | Within one hour running of compressor oil pressure not builtup. Checked found drive gear spindle broken and bushes damaged. | null | closed | Gearkit Replaced
2015-10-05 | Geekay Pneumatic Pvt Ltd | null | D | Kay Kay Exports | Kerala | KCX31 | 3434K010 | 016/201516 | 2015-09-28 | 180542 | 2015-08-09 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-03-27 | 2015-08-09 | ZH | null | null | 6 | One no. solenoid valve is leaking because of cross threading and coil not working. Also found suction pressure gauge was out. | null | closed | Replaced pressure gauge & solenoid valve assly
2015-10-07 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Foods Pvt Ltd | Taloja, Mh | KC72 | 347K767 | 35 | 2015-09-15 | null | 2015-11-09 | cutouts not working / malfunctioning | 2014-01-06 | 2015-10-08 | ZH | null | null | 2 | Microswitch plate not moving up and down. | null | closed | OP cutout 9995206908
2015-10-07 | Kalp Marketing | Gujrat | D | Nilkanth Cold Storage | null | KCX3 | 3374K840,841 | 59 | 2015-05-10 | 642 | 2015-09-16 | stop valve leakage | 2014-01-12 | 2015-02-17 | 1850 | null | null | 2 | Stop valve Tal80 leakage from welding. Also LP OP Cutout malfunctioning. | null | closed | Replaced TAL Valve 80 & OP Cutout.
2015-10-09 | Delhi Branch | null | D | Hma Frozen Foods | Agra | KC72 | 347K674 | 1060 | 2015-01-10 | 1171 | 2015-09-28 | connecting rod worn out | 2013-01-08 | 2015-06-19 | 5500 | null | null | 18 | connecting rod of cylinder no.03 & 04 wornout | null | closed | con rod assly LP1 & HP1
2015-10-09 | Kalp Marketing | Gujrat | D | Somnath Ice Factory | Kodinar | KC4 | 338K5289 | 56 | 2015-03-10 | 573 | 2015-09-23 | cylinder overheating | 2015-01-08 | 2015-08-21 | 250 | null | null | 1 | Cylinder no.04 overheating due to suction valve ring broken | null | closed | Suction valve ring
2015-10-09 | Kalp Marketing | Gujrat | D | Jinny Marine Traders | Veraval, Gujarat | KC4 | 338K5262 | 57 | 2015-03-10 | 574 | 2015-09-24 | kc oil pump low oil pressure problem. | 2015-01-06 | 2015-08-22 | 285 | null | null | 2 | Replace oil pump assly | null | closed | Replace oil pump assly
2015-10-09 | Kalp Marketing | Gujrat | D | J Bhagwan | null | KC51 | 345K906 | 58 | 2015-06-10 | 397 | 2015-09-28 | knocking / abnormal sound | 2014-01-06 | 2015-08-21 | 300 | null | null | 2 | Replace CR bearings as worn out | null | closed | replace bearing bush drive end,BE bearing half
2015-10-10 | Parag Marketing Services | null | D | Exotic Fruits Ltd | null | KC31 | 343K1451 | 43 | 2015-09-10 | null | null | short supply | 2015-01-16 | 2015-10-10 | ZH | null | null | 10 | Suction stariner , spring , Oring , TAH8 Valve , Suction cloth bag. | null | closed | null
2015-10-14 | Fridge House | null | D | Sirsi Chilling Center | Kannada Dist | KCX2 | 3364K779 | FH009/1516 | 2015-10-13 | null | 2015-10-14 | breather assly fall down | 2014-11-28 | 2015-02-25 | PC | null | null | 3 | Breather assly fall down and wiremesh damage | null | closed | Replaced brather assly
2015-10-21 | Kalp Marketing | Gujrat | D | Star Marine | Veraval, Gujarat | KC51 | 345K945 | 61 | 2015-10-16 | 644 | 2015-08-10 | cylinder overheating | 2014-01-04 | 2015-08-13 | 452 | null | null | 16 | Replace del.valve assly | null | closed | Replace del.valve assly
2015-10-21 | Kalp Marketing | Gujrat | D | Amber Export | Veraval, Gujarat | KC51 | 345K903 | 60 | 2015-10-16 | 643 | 2015-09-10 | shaft seal leakage | 2014-01-04 | 2014-08-22 | 1150 | null | null | 4 | Shaft seal leakage | null | closed | Replaced shaft seal assly, main bearing FW,thrust ring
2015-10-28 | Cool Point | null | E | Al Amar Ice Plant (Al Hassa Ice Plant ) | null | KCX4 | 3384K845 | Mail | 2015-06-10 | null | 2015-06-10 | cylinder overheating | 2014-04-19 | 2015-10-05 | null | null | null | 13 | piston ,liners damaged | null | closed | piston liner del.valves
2015-10-28 | Geekay Pneumatic Pvt Ltd | null | D | Abad Fisheries | Secunderabad | KC21 | 342K871 | 018/201516 | 2015-10-14 | 3998 | 2015-08-23 | k5 valve tight / stem broken / leakage | 2015-07-13 | 2015-09-20 | ZH | null | null | 2 | 01 NO. K5 Valve found too much tight and canot open. | null | closed | Replaced K5 Valve.
2015-10-28 | Geekay Pneumatic Pvt Ltd | null | D | Ernakulam Dairy | Secunderabad | KC6 | 339K3041 | 019/201516 | 2015-10-15 | 3091 | 2015-06-10 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-02-18 | 2015-04-02 | 1000 | null | null | 12 | Found gear was broken . | null | closed | Gearkit replaced
2015-10-28 | Geekay Pneumatic Pvt Ltd | null | D | Kattappana Dairy | Secunderabad | KCX3 | 3374K735 | 017/201516 | 2015-10-13 | 3092 | 2015-07-10 | knocking / abnormal sound | 2014-03-23 | 2015-02-27 | 180 | null | null | 11 | Piston no. 2 was broken , The ischarge stroke limitor were wornout and due to the same delivery valve leaked resulting in damage of components. | null | closed | Replaced Valve assly , piston , piston ringsets, liner etc.
2015-10-28 | Fridge House | null | D | Al-Aziz International Industries | Bihar | KC42 | 344K1018 | FH010/1616 | 2015-10-20 | 28 | 2015-10-14 | shaft seal leakage | 2015-06-27 | 2015-10-09 | 143 | null | null | 3 | Observed much more dirty oil due to filters not replaced and more scraches on bronze ring. | null | closed | Shaft seal assly replaced
2015-11-01 | Parag Marketing Services | null | D | Indapur Dairy And Milk Product | Baramati | KC9 | 340K327 | 38 | 2015-09-22 | 3510 | 2015-12-09 | cylinder overheating | 2013-12-30 | 2014-05-28 | 5500 | null | null | 5 | overheat and oil carryover problem | null | closed | Del.valve,liner,piston
2015-11-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kwality Chemical Industries | null | KCX3 | 3374K893 | 46 | 2015-12-10 | null | 2015-10-10 | kcx manifold threads damaged | 2015-01-05 | 2015-06-22 | 1200 | null | null | 1 | Housing manifold thread dmamged | null | closed | KCX Manifold
2015-11-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Sea Foods Pvt Ltd | null | KCX2 | 3364K879 | 45 | 2015-12-10 | 46 | 2015-10-10 | kcx manifold threads damaged | 2015-01-06 | 2015-10-10 | PC | null | null | 4 | Housing manifold thread dmamged | null | closed | KCX Manifold
2015-11-01 | Parag Marketing Services | null | D | Diamond Cold Storage | null | KCX2 | 3364K723 | 39 | 2015-09-22 | null | 2015-12-08 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2014-04-30 | 2015-04-04 | 1151 | null | null | 12 | Pump elelment tang broken, scoring on cover and bush | null | closed | KCX pump elemrnt assly
2015-11-01 | Geekay Pneumatic Pvt Ltd | null | D | Cherukattu Industries | Kerala | KCX3 | 3374K768 | 21 | 2015-10-27 | 3097 | 2015-10-22 | knocking / abnormal sound | 2014-06-28 | 2014-07-30 | 6000 | null | null | 1 | piston hits to del.valve | null | closed | piston ring set & piston
2015-11-01 | Geekay Pneumatic Pvt Ltd | null | D | A S Marine Ice Plant | Kerala | KC4 | 338K5084 | 20 | 2015-10-26 | 785 | 2015-10-17 | shaft seal leakage | 2014-06-18 | 2014-12-12 | 4000 | null | null | 6 | Shaft seal leakage | null | closed | Replace shaft seal
2015-11-01 | Kalp Marketing | Gujrat | D | Indus Mega Food | Madhya Pradesh | KC6 | 339K2975 | 19 | 2015-05-27 | 412 | 2015-03-23 | shaft seal leakage | 2013-01-10 | 2014-05-22 | 2250 | null | null | 7 | Replace shaft seal assly thrust ring bronze | null | closed | Replace shaft seal assly thrust ring bronze
2015-11-02 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aarti Drugs Limited | null | KC4 | 338K5189 | 42 | 2015-03-10 | 41 | 2015-09-24 | cutouts not working / malfunctioning | 2015-01-01 | 2015-10-09 | ZH | null | null | 8 | Microswitch plate not moving up and down. | null | closed | OP cutout
2015-11-02 | Gargi Engineering Enterprices Pvt Ltd | null | D | Manik Foods Pvt Ltd | Wada | KCX2 | 3364K778 | 41 | 2015-03-10 | null | 2015-01-10 | cutouts not working / malfunctioning | 2014-01-09 | 2015-08-07 | ZH | null | null | 10 | Microswitch plate not moving up and down. | null | closed | OP cutout
2015-11-02 | Trade Links | Secunderabad | D | Hygro Chemicals & Pharmatek P Ltd | Medak Dist | KCX3 | 3374K820 | 33 | 2015-10-20 | null | 2015-10-10 | cylinder overheating | 2014-01-11 | 2015-09-02 | 1200 | null | null | 3 | Delivery valve back leakage problem due to this liner pressing ring had broken and resulted to overheating of cylinder. | null | closed | Replaced delivery valve , suction valve ring , spring , Piston ring set and liner kit.
2015-11-02 | Gargi Engineering Enterprices Pvt Ltd | null | D | Fine Organic Industries | Ambernath | KC2 | 336K3072 | 40 | 2015-03-10 | null | 2015-08-21 | high oil consumption / oil carry over | 2013-01-09 | 2015-11-04 | 400 | null | null | 18 | In open trial oil throw observed | null | closed | Replaced ORV , Orings and Piston rings.
2015-11-02 | Trade Links | Secunderabad | D | Pavitra Agrofresh Cold Storage | Hydrabad | KC21 | 342K866 | 32 | 2015-10-20 | null | 2015-10-13 | k5 valve tight / stem broken / leakage | 2015-01-05 | 2015-09-10 | ZH | null | null | 5 | 02 Nos K5 Valves steam had stuck and were not open | null | closed | Replaced K5 Valve
2015-11-02 | Parag Marketing Services | null | D | Finolex Cabale Limited | Urse, Pune | KC6 | 339K3208 | 44 | 2015-09-10 | 3603 | 2015-02-10 | leakage from top housing discharge | 2015-12-08 | 2015-09-09 | PC | null | null | 1 | Observed top housing discharge pipe crack due to high vibration. | null | closed | Replaced top housing discharge.
2015-11-02 | Delhi Branch | null | D | Sr Chilling | New Delhi | KC4 | 338K5231 | 1061 | 2015-10-23 | 1599 | 2015-10-15 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-01-02 | 2015-10-14 | ZH | null | null | 8 | Pressure gauges out | null | closed | Pr. Gauge 16 kg/cm2
2015-11-02 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K003 | 31 | 2015-10-20 | null | 2015-10-14 | shaft seal leakage | null | 2015-02-14 | 1624 | null | null | 6 | Shaft seal had wornout. | null | closed | Replaced Shaft seal assembly
2015-11-06 | Parag Marketing Services | null | D | Eternis Fine Chemicals Ltd | Pune | KC2 | 336K3297 | 37 | 2015-09-22 | 3739 | 2015-11-09 | cylinder overheating | 2015-07-02 | 2015-07-06 | PC | null | null | 4 | Overheating and Knocking sound. | null | closed | Replaced Cylinder liner , Piston , piston ring set , Delivery valve kit , Suction ring & spring.
2015-11-06 | Trade Links | Secunderabad | D | Ana Clara Ice Plant | Goa | KCX2 | 3364K822 | 26 | 2015-07-27 | 24 | 2015-08-16 | high oil consumption / oil carry over | 2015-02-25 | 2015-04-18 | 24 | null | null | 2 | Found open oil throw in both cylinders . | null | closed | Replaced piston ring sets
2015-11-06 | Trade Links | Secunderabad | D | Ferrao Ice Plant | Goa | KCX2 | 3364K713 | 31 | 2015-08-21 | 22 | 2015-08-13 | shaft seal leakage | 2014-03-26 | 2014-07-26 | 3500 | null | null | 4 | Shaftseal wornout. | null | closed | Replaced shaft seal assembly
2015-11-08 | Multivista Global Pvt Ltd | null | D | Nurey Chemicals | null | KC42 | 3344K902 | 11 | 2015-07-11 | null | 2015-07-11 | knocking / abnormal sound | 2014-04-19 | null | 40 | null | null | null | replace int.bearing not suitable replace int.bearing assly | null | closed | intermidiate bearing assly
2015-11-09 | Hss Solution Pvt Ltd | null | D | Satnam Sakshi Cold Storage | Jaipur | KC4 | 338K5059 | 1062 | 2015-10-31 | 164 | 2015-09-30 | high oil consumption / oil carry over | 2014-01-03 | 2014-11-11 | 300 | null | null | 8 | Oil throw thru piston rings | null | closed | Piston ring sets
2015-11-20 | Morgan | null | E | Sea Green Fisheries | Karachi | KC63 | 346K230 | null | 2015-11-20 | null | 2015-11-16 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-08 | 2015-11-16 | ZH | null | null | 3 | Oil pump gear broken. | null | closed | Suggested to replace with modified oil pump
2015-11-22 | Fridge House | null | D | Sirsi Chilling Center | Kannada Dist | KCX2 | 3364K779 | FH012/1516 | 2015-11-11 | 30 | 2015-10-28 | cylinder overheating | 2014-11-28 | 2015-02-25 | 3295 | null | null | 3 | In continuation of erlier FRR No. 009 dt.13/10/15 remaining following spares also damaged and hence we replaced these items while assly. Now compressor is running satisfactory. | null | closed | Replaced Piston , Piston ring , Big end bearing , delivery valve kit , Buffer spring etc.
2015-11-22 | Trade Links | Secunderabad | D | Hygro Chemicals & Pharmatek P Ltd | Medak Dist | KCX3 | 3374K820 | 36 | 2015-02-11 | null | 2015-10-29 | high oil consumption / oil carry over | 2014-01-11 | 2015-09-02 | 1250 | null | null | 3 | Delivery valve & ORV back leaking. | null | closed | Replaced Delivery valve kit , Buffer spring , Piston & Kit liner.
2015-11-22 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC42 | 342K997 | 35 | 2015-10-31 | null | 2015-10-27 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-03 | 2015-06-24 | PC | null | null | 3 | Oil pump assembly - Drive gear stuck in the bush and resulted to shearing of driving gear tang - Old pump | null | closed | Replaced Oil pump assembly
2015-11-22 | Trade Links | Secunderabad | D | Shri Lakshmi Ice Industries | null | KC3 | 337K4454 | 34 | 2015-10-31 | 433 | 2015-10-26 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-06 | 2015-10-26 | ZH | null | null | 4 | driving shaft tang broken | null | closed | Gear kit
2015-11-22 | Fridge House | null | D | Dharwad Dist CoOpMilk Prod Soc Ltd | Dharwad | KC9 | 340K351 | FH012/1516 | 2015-11-11 | null | 2015-07-10 | pipe damaged in top housing assly | 2015-06-07 | 2015-07-10 | ZH | null | null | 3 | Checked and found pipe was damaged while transportation time. Which is connected near by Tah8 valve assly. | null | closed | null
2015-11-24 | Cool Comfort Private Limited | West Bengal | D | Jagadish Cold Storage (P) Ltd | null | KC6 | 339K3150 | 4 | 2015-11-18 | 508 | 2015-06-11 | knocking / abnormal sound | 2015-01-28 | 2015-09-30 | 28 | null | null | 8 | Cylinder no.3 nocking sound , During visit found that piston top broken. Probable cause : Failure was occurred due to leakage in delivery valve assly & which caused over heating . Thrust ring bronze and main bearing damaged due to material dust of broken parts. | null | closed | Replaced delivery valve assly & 1 set of cylinder assly.
2015-11-24 | Parag Marketing Services | null | D | Dinshaw Food P Ltd | Nagpur | KC12 | 341K054 | 53 | 2015-11-19 | 3609 | 2015-10-21 | knocking / abnormal sound | 2014-01-12 | 2015-04-22 | 2290 | null | null | 4 | Intermediate bearings seized and oil pump wearing of housing. | null | closed | Replaced Intermediate bearing & Oil pump assembly.
2015-11-25 | S M Refrigeration | null | D | Jain Traders Pvt Ltd | null | KC4 | 338K5183 | 1064 | 2015-11-21 | 6567 | 2015-10-08 | high oil consumption / oil carry over | 2015-01-01 | 2015-05-04 | 960 | null | null | 3 | oil lifting problem needs to replace ORV 4Nos. | null | closed | ORV 4Nos.
2015-11-25 | S M Refrigeration | null | D | Himalaya Cold Storage | null | KC4 | 338K5156 | 16 | 2015-02-11 | 5322 | 2015-10-23 | kc oil pump low oil pressure problem. | 2014-01-12 | 2015-01-03 | 2188 | null | null | 3 | scoring on oil pump coverplate,and housing | null | closed | Replace KC oil pump assly
2015-11-25 | Hss Solution Pvt Ltd | null | D | Bhansali Engineering Polymers Ltd | Sirohi | KC42 | 344K998 | 1063 | 2015-11-21 | 242 | 2015-05-11 | leakage from oil pump body | 2015-01-03 | 2015-05-11 | ZH | null | null | 8 | leak from oil pump body mounting hole. | null | closed | KC oil pump
2015-11-25 | S M Refrigeration | null | D | Namaste India Foods PvtLtdHapur | Uttar Pradesh | KC2 | 336K3298 | 1065 | 2015-11-21 | 6565 | 2015-07-08 | oil level glass broken | 2015-01-02 | 2015-06-08 | PC | null | null | 6 | oil level glass broken while commissioning | null | closed | oil level glass
2015-11-28 | Geekay Pneumatic Pvt Ltd | null | D | San Marine Export | null | KC51 | 345K949 | 22 | 2015-11-21 | 3047 | 2015-12-11 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-04-27 | 2015-09-11 | ZH | null | null | 7 | driving gear broken and driven gear tight | null | closed | Replace kit oil pump gear
2015-11-28 | Geekay Pneumatic Pvt Ltd | null | D | Popular Ice Factory | null | KCX4 | 3384K1005 | 23 | 2015-11-21 | 3090 | 2015-07-11 | knocking / abnormal sound | 2015-02-20 | 2015-07-11 | 110 | null | null | 9 | liner gasket damaged,lever damaged | null | closed | Replace kit liner part
2015-12-02 | Trade Links | Secunderabad | D | Al Sl Sami Agro Products | null | KC42 | 344K960 | 37 | 2015-11-23 | 318 | 2015-06-10 | cutouts not working / malfunctioning | 2014-01-11 | 2015-06-10 | ZH | null | null | 11 | LP & OP cutout not working. | null | closed | Replace LP/OP cutout
2015-12-02 | Trade Links | Secunderabad | D | Vizag Foods Pvt Ltd | null | KC72 | 347K834 | 38 | 2015-11-26 | 264 | 2015-11-21 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-03 | 2015-11-20 | ZH | null | null | 8 | driving gear tang broken | null | closed | Replace kit oil pump gear
2015-12-02 | Parag Marketing Services | null | D | Nuray Chemicals | null | KC42 | 344K902 | 12 | 2015-11-27 | null | null | knocking / abnormal sound | 2015-04-19 | null | 40 | null | null | null | HP connecting rod big end bore ovality,wearout | null | closed | Replace HP connecting rod
2015-12-05 | Trade Links | Secunderabad | D | Shiri Maheshwari Cold Storage P Ltd Jammalamadugu | Kadap Dist | KC3 | 337K4465 | 40 | 2015-11-27 | null | 2015-11-17 | shaft seal leakage | 2015-01-07 | 2015-08-13 | 705 | null | null | 1 | Shaft seal had worn out abnormally. Axial clearance and thrust ring were checked and found ok. | null | closed | Shaft seal assembly replaced
2015-12-05 | Hss Solution Pvt Ltd | null | D | Nature Organics Products PvtLtd Virat Nagar | Jaipur | KC3 | 337K4318 | 1066 | 2015-11-30 | 169 | 2015-03-11 | solenoid valve coil not working / malfunctioning | 2014-01-11 | 2015-10-16 | ZH | null | null | 12 | Coil wire short and burnt. | null | closed | Solenoid valve coil replaced
2015-12-05 | Trade Links | Secunderabad | D | Al-Hijaz Frozen Foods Llp Ltd Saroornagar | R R Dist | KC31 | 343K1480 | 39 | 2015-11-27 | null | 2015-11-18 | solenoid valve not working / malfunctioning | 2015-01-08 | 2015-11-18 | ZH | null | null | 3 | During loading / unloading of cylinders 1 no solenoid valve had failed. Inspection of the coil was done & it is found ok. | null | closed | Solenoid valve replaced.
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Libran Cold Storage | null | KC2 | 336K3288 | 47 | 2015-10-31 | 50 | 2015-10-28 | cutouts not working / malfunctioning | 2015-01-01 | 2015-10-28 | ZH | null | null | 9 | OP Cutout switch not working properly & LP,OP pressure gauges out. | null | closed | cutout MP 55 A & 016 kg pr. Gauge2nos.
2015-12-08 | Parag Marketing Services | null | D | Shramik Milk Products | null | KCX3 | 3374K774 | 52 | 2015-07-11 | 3655 | 2015-09-26 | high oil consumption / oil carry over | 2014-07-25 | 2015-07-06 | 5500 | null | null | 11 | Oil throw thru piston rings | null | closed | Replace piston ring sets
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Fine Organic Industries | Ambernath | KC2 | 336K3072 | 50 | 2015-07-11 | null | 2015-05-08 | high oil consumption / oil carry over | 2013-01-09 | 2015-11-04 | 500 | null | null | 18 | oil carryover observed 1.5 ltrs/24 hours | null | closed | Replace piston rings,ORV,Orings
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Sea Foods Pvt Ltd | null | KC102 | 349K029 | 48 | 2015-10-31 | 18 | 2015-10-24 | kc oil pump low oil pressure problem. | 2015-01-06 | 2015-09-10 | 48 | null | null | 4 | Cover plate found damaged and gears backside scoring | null | closed | KC oil pump
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Supreet Chemicals Pvt Ltd | null | KCX6 | 3394K503 | 49 | 2015-07-11 | 21 | 2015-08-10 | knocking / abnormal sound | 2015-01-06 | 2015-01-10 | 500 | null | null | 4 | Liner gaskets damaged | null | closed | Compressor called back
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Penn Frozen PLtd | Karjat | KC42 | 344K907 | 51 | 2015-07-11 | null | 2015-07-11 | shaft seal leakage | 2015-01-04 | 2015-07-13 | 500 | null | null | 3 | Shaft seal leak | null | closed | Replace shaft seal assly
2015-12-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Ion Exchange Co Ltd | Ankleshwar Gujarat | KC6 | 339K3167 | 063/20152016 | 2015-08-12 | null | 2015-04-12 | stop valve leakage | 2015-01-02 | 2015-11-18 | PC | null | null | 9 | Shaft seal leakage. Tal Valve,s cone assly found loose and teflon sheet cut off. | null | closed | Shaft seal assly, Tal Valve 80
2015-12-08 | Morgan | null | E | Sadruddin & Co | null | KC6 | 339K3185 | Mail | null | null | null | water jacket leakage | 2015-09-06 | 2015-01-12 | ZH | null | null | 3 | water body of compressor is leaking. It has leakages from 4-5 different points. | null | closed | null
2015-12-11 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC42 | 344K972 | 41 | 2015-08-12 | null | 2015-03-12 | oil leakage from discharge filter top housing | 2014-01-12 | 2015-06-24 | 200 | null | null | 6 | Oil leakage from discharge filter top housing - Pipe and union had cracked near ferrule . | null | closed | Replaced disch. Oil filter top housing.
2015-12-14 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | null | KC84 | 330K037 | 44 | 2015-12-14 | 534 | 2015-12-12 | knocking / abnormal sound | 2014-01-10 | 2015-12-10 | 400 | null | null | 12 | C.shaft broken at intermidiate housing | null | closed | Replace C.Shaft,HP connecting rod assly
2015-12-14 | Trade Links | Secunderabad | D | Mhk Ice Plant | null | KCX4 | 3384K908 | 9 | 2015-05-11 | 3573 | 2015-04-11 | knocking / abnormal sound | 2014-07-13 | 2014-06-12 | PC | null | null | 5 | delivery valve leakage | null | closed | Replace piston ,gudgeon pin,bush
2015-12-14 | Trade Links | Secunderabad | D | VV Marine | null | KC31 | 343K1460 | 8 | 2015-08-23 | 3084 | 2015-05-08 | knocking / abnormal sound | 2015-10-03 | 2015-02-07 | PC | null | null | 4 | big end bearing worn out | null | closed | Replace Bigend bearing,thrust ring,bearing bush drive end
2015-12-16 | Trade Links | Secunderabad | D | Kaveri Ice Industries | null | KCX4 | 3384K1024 | 43 | 2015-09-12 | 269 | 2015-01-12 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-01-04 | 2015-07-12 | ZH | null | null | 8 | Error Of 2.5 kg/cm2 in both suction and discharge valves | null | closed | Replace pr. Gauge 16 kg/cm2 & 25.kg/cm2
2015-12-16 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KC21 | 342K876 | 42 | 2015-08-12 | 593 | 2015-11-19 | tah8 valve tight / stem broken / leakage | 2015-01-10 | 2015-11-19 | ZH | null | null | 1 | Leakage from TAH8 valve gland | null | closed | Rplace TAH8 valve
2015-12-18 | Fridge House | null | D | Mandya Dist Co-Op Milk Foods | Manya | KCX6 | 3394K454 | FH014/1516 | 2015-11-15 | null | 2015-12-12 | knocking / abnormal sound | 2014-10-19 | 2015-06-11 | 525 | null | null | 13 | Crankshaft wornout due to all pressure fluctuations , we changed oil pump element but problem cont. | null | closed | Replaced crankshaft ,oil pump assembly & bearings
2015-12-18 | Parag Marketing Services | null | D | Vishweshawar Cold Storage | Sangli | KCX2 | 3364K800 | 57 | 2015-12-16 | 3551 | 2015-01-12 | knocking / abnormal sound | 2014-12-15 | 2015-03-19 | 3500 | null | null | 12 | Delivery valve leakage due to inproper locking of valve rings in discharge stroke limitor . | null | closed | Replaced delivery valve assembly
2015-12-18 | Parag Marketing Services | null | D | Chaman Cold Storage And Ice Factory | Jabalpur | KC3 | 337K4149 | 56 | 2015-12-16 | 263 | 2015-11-12 | pipe damaged in top housing assly | 2014-02-15 | 2014-10-08 | 700 | null | null | 6 | Cracked filter top housing pipe near nut and ferrule . | null | closed | Replaced socket union serew
2015-12-20 | Parag Marketing Services | null | D | Heritage Foods Ltd | null | KC4 | 338K5277 | 58 | 2015-12-17 | 3621 | 2015-12-15 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-03-07 | 2015-12-12 | ZH | null | null | 5 | driving gear tang broken, wearing of cover plate and oil pump housing bore | null | closed | Replace oil pump assly
2015-12-20 | S M Refrigeration | null | D | Shri Balaji Industries | Sandila | KC4 | 338K5229 | 17 | 2015-09-12 | 5330 | 2015-11-25 | knocking / abnormal sound | 2015-01-02 | 2015-05-04 | 3850 | null | null | 2 | Piston worn out ,piston ring set and gudgeon pin worn out | null | closed | replaced piston,piston ring set,gudgeon pin,shaftseal assly
2015-12-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hindustan Chemicals Co | Surat, Gujarat | KCX6 | 3394K423 | 062/20152016 | 2015-04-12 | null | 2015-11-18 | solenoid valve not working / malfunctioning | 2014-01-03 | 2015-11-18 | ZH | null | null | 20 | During commissioning 1 no. valve not working and other 2 nos having rubber expanded. | null | closed | Replaced 03 solenoid valves.
2015-12-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Foods Pvt Ltd | Taloja, Mh | KC72 | 347K766 | 54 | 2015-12-15 | 24 | 2015-12-14 | kc oil pump low oil pressure problem. | 2014-01-06 | 2015-08-08 | 100 | null | null | 2 | scoring marks on oil pump housing | null | closed | replace oil pump assly
2015-12-23 | Fridge House | null | D | Dharwad Dist CoOpMilk Prod Soc Ltd | Dharwad | KC9 | 340K344 | 13 | 2015-12-15 | 35 | 2015-03-12 | knocking / abnormal sound | 2014-12-23 | 2015-05-02 | 1550 | null | null | 2 | During observation scoring marks observed in cyl.no. 4&8,liner gasket bulding | null | closed | Replace cyl. liner, piston, piston ring set
2016-01-01 | Fridge House | null | D | Sagar Ice Plant | Mangalore, Karnataka | PC2 | 331K2754 | 17 | 2015-12-26 | null | 2015-12-21 | high oil consumption / oil carry over | 2015-06-30 | 2015-08-20 | 2201 | null | null | 2 | oil throw from piston and liner | null | closed | replace Liner and pistons,piston rings2Nos.
2016-01-02 | Fridge House | null | D | Mandya Dist CoOp Milk Foods | Mandya Dist | KCX6 | 3394K454 | 15 | 2015-12-21 | 23 | 2015-06-11 | cutouts not working / malfunctioning | 2014-10-19 | 2015-06-11 | 700 | null | null | 13 | cutout not working malfunctioning | null | closed | replace HP cutout
2016-01-02 | Fridge House | null | D | Rinac India Ltd | null | KC31 | 343K1473 | 18 | 2015-12-28 | null | 2015-12-20 | kc oil pump low oil pressure problem. | 2015-05-07 | 2015-12-14 | ZH | null | null | 5 | Driving gear spindel broken due to sudden load | null | closed | Replace oil pump assembly
2016-01-02 | Trade Links | Secunderabad | D | Saraca Laboratories Ltd | null | KC84 | 330K035 | 46 | 2015-12-28 | null | null | knocking / abnormal sound | 2014-01-09 | 2015-11-12 | 172 | null | null | 15 | replace crankshaft,crankshaft assembly, intermidiatebearing assembly, bigend bearing, sol. Coil | null | closed | replace crankshaft,crankshaft assembly, intermidiatebearing assembly, bigend bearing, sol. Coil
2016-01-02 | Fridge House | null | D | Mandya Dist CoOp Milk Foods | Mandya Dist | KCX63 | 3364K001 | 16 | 2015-12-21 | 22 | 2015-05-11 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-03-27 | 2015-05-11 | ZH | null | null | 9 | Error in suction and discharge pressure gauge | null | closed | suction and discharge pressure gauge
2016-01-08 | Geekay Pneumatic Pvt Ltd | null | D | Pallathara Ice Plant | Kottayam | KCX2 | 3364K908 | 24 | 2015-12-16 | 3174 | 2015-11-30 | cylinder overheating | 2015-08-16 | 2015-11-27 | 78 | null | null | 3 | Del. Valve is leaking from 1& 2 | null | closed | Replace del valve assly1No. Suction stroke limitor1no.
2016-01-08 | Trade Links | Secunderabad | D | Venkat Madhavi Ice Factory | Godavari Dist | KCX6 | 3394K425 | 45 | 2015-12-21 | null | 2015-10-12 | cylinder overheating | 2014-01-04 | 2014-09-06 | 8125 | null | null | 2 | Cylinder seize - Delivery ring spring broken , piston overheated seized , buffer spring shrunk . | null | closed | Replaced delivery valve & cylinder assly
2016-01-08 | Trade Links | Secunderabad | D | Vindhya Organics P Ltd | Medak Dist | KC2 | 336K3306 | 47 | 2015-12-31 | null | 2015-12-30 | shaft seal leakage | 2015-01-02 | 2015-12-30 | ZH | null | null | 10 | Shaft seal leakage - Freon gas leakage | null | closed | Replaced shaft seal assly
2016-01-12 | S M Refrigeration | null | D | Aman Enterprises | New Delhi | KCX3 | 3374K776 | 1068 | 2016-01-15 | null | 2016-01-16 | compressor seize / jam. | 2014-01-07 | 2015-06-10 | 178 | null | null | 15 | Compressor sieze | null | closed | Part Replaced pistonassly,del.valve assly,liner,delvalve assly,mani bearings.3Nos. Each
2016-01-12 | Trade Links | Secunderabad | D | Aurobindo Pharma Pvt Ltd | Medak Dist | KC6 | 339K3213 | 48 | 2016-07-01 | null | 2016-06-01 | fitting leakage from suction oil strainer top housing . | 2015-01-09 | 2016-05-01 | ZH | null | null | 3 | Suction filter pipe ferrule is very free . Ppe dia had pinched so ferrule is very free. | null | closed | Replaced suction filter top housing assly & Union socket.
2016-01-12 | Gargi Engineering Enterprices Pvt Ltd | null | D | R S S Ice Factory | null | KCX3 | 3374K907 | 33 | 2015-09-14 | 28 | 2015-03-09 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-10-07 | 2015-03-09 | null | null | null | 2 | During initial commissioning of compressor , it is observed that oil pressure gauge not working , pointer stuck out below zero. | null | closed | Replaced presure gauge 016Kg/cm2.
2016-01-29 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shreedutta Aquaculture Pvt Ltd | null | KC72 | 347K884 | 67 | 2016-01-29 | null | null | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-12 | 2016-05-01 | ZH | null | null | 1 | During the trial tang broken of oil pump gear shaft. | null | closed | Pump replaced
2016-01-30 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Panna Ca Store | J&K | KCX2 | 3364K867 | 1069 | 2016-01-22 | 1176 | 2016-11-01 | fitting leakage from suction pressure gauge | 2015-01-04 | 2015-01-07 | PC | null | null | 2 | threading damaged | null | closed | Replace gauge adaptor
2016-01-30 | null | null | E | Chen Ais Machine & Engg Sb | null | KC6 | 339K3219 | null | null | null | null | kc oil pump seize tang broken, housing , bushes ,gear wornout. | null | null | null | null | null | null | null | null | open | null
2016-01-30 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC42 | 344K996 | 50 | 2016-01-14 | 512 | 2016-11-01 | knocking / abnormal sound | 2015-01-03 | 2015-06-25 | 500 | null | null | 3 | pipe cutting piece observed in HP suction line,HP connecting rod scoring. | null | closed | replace HP conrod,del.valve assly,gudgeon pin,Dish. Filter top housing
2016-01-30 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | null | KC84 | 330K037 | 49 | 2016-01-14 | 447 | 2016-04-01 | knocking / abnormal sound | 2014-01-10 | 2015-12-10 | 400 | null | null | 12 | replaced oil pump assly,suction filter housing,c.shaft,big end bearings,intermidiate housing. | null | closed | replaced oil pump assly,suction filter housing,c.shaft,big end bearings,intermidiate housing.
2016-01-30 | Parag Marketing Services | null | D | Vaishnavadevi Foods Products PvtLtd | Usmanabad | KCX3 | 3374K859 | 62 | 2016-01-27 | null | 2016-01-22 | manifold porous | 2015-01-30 | 2015-03-06 | 1000 | null | null | 5 | Pin hole in manifold - Leakage. | null | closed | Replaced manifold housing due to porous.
2016-02-02 | Trade Links | Secunderabad | D | Vijaya Sree Ice Factory | Godavari Dist | KCX3 | 3374K858 | 53 | 2016-01-29 | null | 2016-01-23 | knocking / abnormal sound | 2015-01-01 | 2015-06-05 | 3759 | null | null | 4 | Bufer spring had shrunk in height | null | closed | Replaced buffer spring
2016-02-02 | Trade Links | Secunderabad | D | Blue Park Sea Foods | Krishna Dist | KC51 | 345K943 | 52 | 2016-01-29 | null | 2016-01-20 | knocking / abnormal sound | 2015-01-03 | 2015-05-27 | 2453 | null | null | 2 | Oil pump gear and bushes had wornout. Observed white metal in the oil. Connecting rod big end bearing wornout , . Both main bearings had wornout. Also observed wearing of intermediate brg , steel thrust ring & bronze . | null | closed | Replaced HP Con rod 1 , Oil pump gearkit 1 , All bearings.
2016-02-02 | Trade Links | Secunderabad | D | Wellcome Fisheries | Godavari Dist | KC93 | 348K113 | 51 | 2016-01-29 | null | 2016-01-27 | knocking / abnormal sound | 2014-01-12 | 2015-08-03 | 2500 | null | null | 3 | Obsrevd 4 no. cylinder touching stroke limitor and axial play was also observed .found white bearing metal in crankcase. Connecting rod of the same had wornout , big end bearing notch had damaged resulted to abnormal wearing of crank pin. Bronze thrust ring 1st intermedate and connecting rod no.5 had wornout up to 1.5mm. | null | closed | Replaced crankshaft assly , thrust ring , intermediate bearing , HP ROD 2 & LP ROD 3
2016-02-02 | Gargi Engineering Enterprices Pvt Ltd | null | D | Inovative Cuisine P Ltd | Karjan | KC63 | 346K215 | 066/20152016 | 2016-01-28 | null | 2015-09-12 | solenoid valve coil not working / malfunctioning | 2015-01-10 | 2015-09-12 | ZH | null | null | 2 | Solenoide valve coil not working properly . | null | closed | Coil
2016-02-05 | Geekay Pneumatic Pvt Ltd | null | D | AMFisheries | Ambalappuzha Secunderabad | KC3 | 337K4265 | 025/201516 | 2016-01-29 | 3585 | 2016-01-13 | oil pressure trip | 2014-09-09 | 2015-09-06 | 5475 | null | null | 9 | Dismentled both the filters and found bronze particles in the oil and the filters were blacked. Observed thrust ring bronze was wornout. | null | closed | Replaced thrust ring bronze
2016-02-08 | S M Refrigeration | null | D | Sesaga Enterprises Pvt Ltd | Raigad | PC2 | 331K2700 | 18 | 2016-01-27 | 5332 | 2015-07-12 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2014-01-11 | 2015-07-12 | ZH | null | null | 13 | oil pressure gauge found defective during commisioning | null | closed | Replace oil pressure gauge
2016-02-09 | Trade Links | Secunderabad | D | Pavitra Agrofresh Cold Storage | Hydrabad | KC3 | 337K4436 | 54 | 2016-05-02 | 522 | 2016-04-02 | knocking / abnormal sound | 2015-01-05 | 2015-07-10 | 1094 | null | null | 5 | lubrication oil hole of connecting rod not straight hence abnormal wearout of gudgeon pin conrod. | null | closed | replace gudgeon pin, conrod.
2016-02-16 | S M Refrigeration | null | D | Vellankanni Enterprises Ice Factory | Bhayander | KCX3 | 3374K798 | 59 | 2016-04-01 | null | 2015-12-31 | knocking / abnormal sound | 2014-01-10 | 2015-03-02 | 5000 | null | null | 4 | Direct liner gasket damaged for 2nd time & step marking found towards strainer side at top of iner. | null | closed | Reppalced liner , Piston ring & Gasket set.
2016-02-16 | Parag Marketing Services | null | D | Finolex Cabale Limited | Urse, Pune | KCX6 | 3394K447 | 63 | 2016-01-27 | 180548 | 2015-07-31 | knocking / abnormal sound | 2014-02-09 | 2014-10-12 | 3939 | null | null | 3 | Observed knocking sound hence opened and checked found delivery valve leakage and broken ring spring , damage limitor stroke suction valve . | null | closed | Replaced kit delivery valve , Limitor stoke , Limitor stroke suction valve
2016-02-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Rg Ice Ltd | Bhivandi | KC4 | 338K5269 | 61 | 2016-01-25 | 64 | 2016-12-01 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-05-15 | 2016-12-01 | ZH | null | null | 8 | Discharge pressure and oil pressure gauge not working | null | closed | Replaced discharge and oil pressure gauge.
2016-02-16 | Parag Marketing Services | null | D | Shree Damond Cold Storage | Sangli | KCX2 | 3364K723 | 64 | 2016-05-02 | 3382 | 2016-01-22 | shaft seal leakage | 2015-01-04 | 2015-04-04 | 1791 | null | null | 1 | Leakage from shaft seal . | null | closed | Replaced shaft seal assly
2016-02-19 | Delhi Branch | null | D | Varun Beverage | Jodhpur | KC6 | null | 1070 | 2016-02-15 | null | 2016-02-15 | customer stock old intermediate housing drill holes not match with kpcl supplied new spare crankcase | null | null | null | null | null | null | Intermediate bearing assembly | null | closed | null
2016-02-19 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K003 | 57 | 2016-02-13 | null | 2016-12-02 | shaft seal leakage | 2014-01-08 | 2015-02-14 | 2194 | null | null | 6 | Shaft seal assembly had wornout. | null | closed | Replaced shaft seal assembly.
2016-02-19 | Trade Links | Secunderabad | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K927 | 56 | 2016-09-02 | null | 2015-12-06 | solenoid valve not working / malfunctioning | 2015-01-09 | 2016-05-01 | ZH | null | null | 3 | Cylinder no. 2 observed solenoid valve not working . Neither electrically nor manually. | null | closed | Replaced solenoide valve assly
2016-02-19 | Trade Links | null | D | Aurbindo Pharma Pvt Ltd | Medak Dist | KC6 | 339K3213 | 55 | 2016-09-02 | null | 2016-06-01 | suction oil filter top fitting leakage | 2015-01-09 | 2016-05-01 | PC | null | null | 3 | Suction oil filter pipe ( Crankcase to Suction Filter) ferrule is very free & pipe dia had pinched so ferrule is very free. | null | closed | Replaced suction oil filter top & Union socket
2016-02-22 | Trade Links | Secunderabad | D | Al-Hijaz Frozen Foods Llp Ltd Saroornagar | R R Dist | KC31 | 343K1480 | 59 | 2016-02-17 | null | 2016-02-17 | knocking / abnormal sound | 2015-01-08 | 2015-11-18 | 1063 | null | null | 3 | Driven gear had stuck and resulted to breakage of driving gear tang. Pump cover bush had also stuck on the driven gear and cover had also damaged. | null | closed | Replaced gear kit
2016-02-22 | Trade Links | Secunderabad | D | Pavitra Agrofresh Cold Storage | Hydrabad | KC3 | 337K4436 | 58 | 2016-02-17 | null | 2016-02-15 | suction oil filter top fitting leakage | 2015-01-05 | 2015-07-10 | 1094 | null | null | 5 | leak from suction filter top housing pipe and ferule fitting. | null | closed | Suction filter rop housing and union socket
2016-02-23 | Morgan | null | E | Morgan | Pakistan | KC6 | 339K3092 | null | 2016-02-17 | null | 2016-02-23 | cutouts not working / malfunctioning | null | null | PC | null | null | null | cutout not working malfunctioning | null | closed | null
2016-02-29 | Parag Marketing Services | null | D | Prathibha Krushi Prakriya Ltd | Kodoli,Kolhapur | KCX6 | 3394K491 | Mail | 2016-02-29 | null | null | knocking / abnormal sound | 2015-01-03 | 2015-10-20 | 215 | null | null | 7 | M16 Nut observed in cylinder,oil suction internal pipe end damaged. | null | closed | null
2016-03-04 | Gargi Engineering Enterprices Pvt Ltd | null | D | Om Cold Storage | Himmatnagar | KC3 | 337K4502 | 069/20152016 | 2016-03-03 | null | 2016-01-03 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-11 | 2016-02-13 | 253 | null | null | 3 | Found driving gear shaft broken . Driving gear jammed in bushing at housing side . Minor scoring found in bottom face at driven gear bore. Cleaned the bottom face and replaced the gear kit and restore the compressor. | null | closed | Replaced gear kit
2016-03-04 | Parag Marketing Services | null | D | Manmandir Dudh Sangh | Sangli | KCX2 | 3364K746 | 65 | 2016-02-22 | 3873 | 2016-05-02 | knocking / abnormal sound | 2015-01-04 | 2015-10-22 | 4000 | null | null | 6 | Knocking sound from direct cylinder due to delivery valve failure. | null | closed | Replaced delivery valve assly , Piston , Piston ring set , Cylinder liner , Buffer spring.
2016-03-09 | Trade Links | Secunderabad | D | Sri Muthyalamma Ice Plant | Vishakhapatanam | KCX4 | 3384K1039 | 60 | 2016-01-03 | null | 2016-02-14 | gas leakage from gland of both tal valves | 2015-01-08 | 2016-02-14 | 24 | null | null | 6 | Observed heavy leakage from gland of both the TAL valves. | null | closed | null
2016-03-11 | Multivista Global Pvt Ltd | null | D | Piramal Enterprises | Ennore Chennai | KC42 | 334K959 | MVGL/15/1613 | 2015-12-21 | null | 2015-12-17 | shaft seal leakage | 2014-07-11 | 2015-01-29 | 2700 | null | null | 2 | Shaft seal assembly checked wornout and broken. | null | closed | Replaced shaft seal assly
2016-03-14 | S M Refrigeration | null | D | K F Cold Storage | Jalandhar | KC4 | 338K5121 | 1071 | 2016-05-03 | 1523 | 2016-04-03 | high oil consumption / oil carry over | 2014-01-10 | 2015-02-04 | 3500 | null | null | 6 | Oil throw observed due to piston rings wornout. | null | closed | Replaced piston ring set4 nos.
2016-03-25 | Hss Solution Pvt Ltd | null | D | Bhansali Engineering Polymers Ltd | Sirohi | KC42 | 344K999 | 1067 | 2015-12-23 | 248 | 2015-07-12 | knocking / abnormal sound | 2015-01-03 | 2015-05-11 | 105 | null | null | 8 | In Cylinder no. 4 observed cut marks on piston , gudgeon pin and piston ring set. | null | closed | Replaced Piston , Piston ring set & Gdgeon pin.
2016-03-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Somsiddha Ice | Vasai | PC2 | 331K2797 | Mail | 2016-03-17 | null | null | delivery valve leakage | 2016-01-01 | 2016-03-16 | ZH | null | null | 3 | suction & discharge pressure showing equal ie 3 kg if single direct piston is running. | null | closed | Replaced delivery valve
2016-03-30 | Hss Solution Pvt Ltd | null | D | Sepau Cold Storage | Dholpur | KC4 | 338K5343 | Mail | 2016-03-31 | null | null | flywheel wobbling | 2015-01-12 | 2016-12-02 | ZH | null | null | 2 | Compressor with our new flywheel & with old flywheel no wobbling was found in new Compressor. | null | closed | Flywheel
2016-04-09 | Trade Links | Secunderabad | D | Vennela Ice Industries | Godavari Dist | KCX3 | 3374K759 | 61 | 2016-03-23 | null | 2016-02-25 | cylinder overheating | 2014-01-06 | 2015-02-26 | 5000 | null | null | 8 | Cylinder no. 2 - Delivery valve ring and spring had broken and valve seat dammaged. | null | closed | Replaced delivery valve assembly 01 no.
2016-04-09 | Trade Links | Secunderabad | D | A A Enterprises Industries Estate | Prakasam Dist | KC3 | 337K4567 | 63 | 2016-03-31 | null | 2016-03-17 | k5 valve thread damaged | 2016-01-02 | 2016-03-17 | ZH | null | null | 1 | Heavy leakage from union nut of discharge line K5 Valve due to K5 Vlave threading damage. | null | closed | Replaced K5 Vlave assembly 01 no.
2016-04-09 | Trade Links | Secunderabad | D | Sri Ice Factory | Nellore | KCX3 | 3374K1001 | 62 | 2016-03-31 | null | 2016-02-18 | solenoid valve not working / malfunctioning | 2015-01-12 | 2016-02-18 | ZH | null | null | 2 | Cylinder no. 2 soleniod valve not working neither manually nor electrically. | null | closed | Replaced solenoid valve assembly 01 no.
2016-04-17 | S M Refrigeration | null | D | Noor Cold Storage | null | KC3 | 337K4552 | 1 | 2016-05-04 | 5366 | 2016-01-03 | cylinder overheating | 2016-06-01 | 2016-01-03 | PC | null | null | 2 | Buffer spring hieght observed 70MM,del. Valve leak | null | closed | Buffer spring hieght observed 70MM,del. Valve leak
2016-04-17 | Geekay Pneumatic Pvt Ltd | null | D | Ambadiyil Dairy | null | PC2 | 331K2690 | 1 | 2016-08-04 | 3070 | 2016-03-16 | high oil consumption / oil carry over | 2015-03-30 | 2015-07-25 | 1100 | null | null | 16 | high oil carryover | null | closed | piston ring sets
2016-04-17 | Trade Links | Secunderabad | D | Ananda Enterprises | null | KC93 | 348K117 | 2 | 2016-09-04 | 568 | 2016-06-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-01-01 | 2015-06-08 | 2389 | null | null | 5 | scoring mark observed on cover & oil pressure decreased up to .8kg/cm2 | null | closed | Replaced oil pump assly
2016-04-17 | S M Refrigeration | null | D | Saraswati Sheet Gruih PvtLtd | null | KCX6 | 3394K76 | 4 | 2016-07-04 | 583 | 2016-05-03 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2019-01-01 | 2019-01-03 | 14000 | null | null | 2 | tang broken,out of warranty ,goodwill basis | null | closed | null
2016-04-17 | Geekay Pneumatic Pvt Ltd | null | D | Kay Kay Exports | Kerala | KCX72 | 3374K001 | 2 | 2016-08-04 | 3107 | 2016-03-30 | op pressure switch malfunctioning | 2015-10-01 | 2015-05-02 | 4500 | null | null | 1 | low oil pressure ok after replacement of oil pressure regulators | null | closed | HP LP OPR
2016-04-17 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX42 | 3444K003 | 1 | 2016-09-04 | 565 | 2016-03-04 | shaft seal leakage | 2014-01-08 | 2015-02-14 | 2300 | null | null | 6 | Frequently failure of shaft seal assembly. | null | closed | Replaced shaft seal assembly.
2016-04-17 | Trade Links | Secunderabad | D | Mukunda Dairy Products | null | KC3 | 337K4242 | 1 | 2016-05-04 | 1 | 2016-04-04 | shaft seal leakage | 2014-07-21 | 2015-01-16 | 3000 | null | null | 6 | oil leakage from shaft seal | null | closed | Replaced shaft seal assly
2016-04-17 | S M Refrigeration | null | D | Hariom Gramodyog | null | KCX2 | 3364K1006 | 2 | 2016-05-04 | 5386 | 2016-03-15 | solenoid valve coil not working / malfunctioning | 2016-04-02 | 2016-03-26 | ZH | null | null | 1 | 24VDC coil fitted instead of 220VAC | null | closed | Coil defective
2016-04-17 | S M Refrigeration | null | D | Luknow Ice Factory | Kanpur | KC3 | 337K4498 | 3 | 2016-05-04 | 5393 | 2016-03-26 | solenoid valve coil not working / malfunctioning | 2015-07-11 | 2016-03-26 | ZH | null | null | 4 | 24VDC coil fitted instead of 220VAC | null | closed | Coil defective
2016-04-27 | null | null | E | Al Amar Ice Plant | Daman & Diu | KCX3 | 3374K856 | 1 | 2016-04-26 | null | 2016-04-13 | knocking / abnormal sound | 2015-01-02 | 2015-04-13 | PC | null | null | 2 | No top clearance , Piston broken | null | closed | Replaced liner gasket .
2016-04-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Nanehemal AgroDaman | null | KC4 | 338K5840 | 2 | 2016-04-29 | 36 | 2016-03-29 | kc oil pump low oil pressure problem. | 2015-04-12 | 2016-01-22 | 250 | null | null | 1 | Field condiitons to be check before replacement of oil pump. | null | closed | Check filter and clenliness of crank case
2016-05-06 | Parag Marketing Services | null | D | S S Agro Urulikanchan | Pune | KC51 | 345K974 | 4 | 2016-02-05 | 10 | 2016-04-12 | cutouts not working / malfunctioning | 2015-12-25 | 2016-04-12 | ZH | null | null | 4 | During commissionning KP55 Cut out not tripping . | null | closed | Replaced pressure switch 1 to 12 BAR. KP55A.
2016-05-06 | Cool Point | null | E | Ksa | null | KC6 | 339K3295 | Mail | 2016-05-06 | null | 2016-05-06 | knocking / abnormal sound | 2016-02-19 | null | ZH | null | null | null | 15 Min after the installation and running the compressor the Piston head got extremely hot and has broken. Due to delivery valve broken. | null | closed | Replaced delivery valve assly , Piston , Piston ring set .
2016-05-06 | Parag Marketing Services | null | D | Guruprasad Ice | Turbhe | KCX6 | 3394K569 | Mail | 2016-05-06 | null | 2016-05-06 | liner bore cut marks | 2016-03-01 | 2016-04-30 | 50 | null | null | 1 | After running of 50 hours,we got the complain of change of oil colour in to black. Compressor was opened on 5.5.16 & following observations were made. 1) oil colour found black in nature. 2)suction strainer was found clean 3)connecting rod gap found 0.05 n 0.06 mm ,within the limit. 4) all heads opened & found cylinder no 1 & 5 step marking at top & both liners has to be replaced with piston ring. 5)cylinder no 4 has marking but within the limit. Party has refused to replace liners with out consulting kpc & Need the quality person involvement to resolve the issus. | null | closed | In existing compressor observed cylinder no. 1,3&5 liner had wornout abnormally . Piston rings under receipt inspection , Crankcasee checked found ok except cylinder X distance out of specification.
2016-05-06 | Parag Marketing Services | null | D | Gokhul Dairy | Kolhapur | KC6 | 339K3075 | 3 | 2016-02-05 | 11 | 2016-04-28 | liner bore cut marks | 2014-01-07 | 2015-10-31 | 221 | null | null | 15 | During visit observed knocking sound from cylinder no.2 . Hence opened and checked found step mark on liner. | null | closed | Replaced Piston , Liner and Bronze thrust ring.
2016-05-06 | Parag Marketing Services | null | D | Shantai Milk & Milk Products | Pune | KCX2 | 3364K811 | 5 | 2016-03-05 | 14 | 2016-04-11 | vld housing leakage due to pin hole | 2015-01-01 | 2016-04-11 | ZH | null | null | 14 | During pree coommissioning cylinder no. 2 VLD Housing leakage due to Pin hole . | null | closed | Replaced VLD Housing & Oring.
2016-05-09 | S M Refrigeration | null | D | Rustam Food PvtLtd Unnao | Uttar Pradesh | KC93 | 348K111 | 7 | 2016-05-16 | 110 | 2016-05-03 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2014-11-01 | 2015-09-14 | 2500 | null | null | 10 | Found cut mark on 2 nos LP Connecting rod , 01 NO. Hp Connecting rod .Also found cut mark on gear shaft & both bushes. Oil pump body damage. | null | closed | Replaced Oil pump assembly , Connecting rods 03 nos. Old type.
2016-05-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chintu Ice | Turbhe | KCX6 | 3394K518 | Mail | 2016-05-09 | null | 2016-05-09 | liner bore cut marks | 2015-08-30 | 2016-05-02 | 50 | null | null | 9 | oil pressure issue & overheating of body : After running of 50 hrs,we got call from customer to attend above problem. 1) visited site on 7.5.16,replaced oil,filters & start compressor. 2)oil pressure difference found 1.3 kg difference & after running half an hour oil colour found dirty with metal particles. 3)suction filter recleaned & refitted 4)oil pressure cut out also replaced from other standby compressor & run the machine as present cutout was tripping even more than1 kg pressure is there. 5)today on 9.5.16,o rings of regulator replaced & found no development. 6)removed all heads & found cylinder no 1 & 4 full step marking at top. 7)cylinder no 2 & 5 also impression of step marking opposite motor. 8)party is fully annoyed for such premature damages after 50 hours of running & asking for replacement of compressor. | null | open | null
2016-05-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Anugrah Cold Storage | Nadiad | KCX4 | 3384K1162 | 12 | 2016-05-16 | 162 | 2016-04-18 | shaft seal leakage | 2016-02-01 | 2016-02-29 | 350 | null | null | 1 | Shaftseal leakage | null | closed | Shaft seal cover replaced.
2016-05-10 | Trade Links | Secunderabad | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K928 | 4 | 2016-04-23 | null | 2016-04-19 | liner bore cut marks | 2015-01-09 | 2015-12-18 | 677 | null | null | 3 | Abnormal sound from cylinder no.1 due to cylinder liner had wornout abnormally. | null | closed | Replaced cylinder liner.
2016-05-10 | Trade Links | Secunderabad | D | Usha Cold Storage | Mahaboobnagar Dist | KCX2 | 3364K962 | 3 | 2016-04-23 | null | 2016-04-13 | oil pressure not buildup | 2015-01-12 | 2016-03-09 | 557 | null | null | 4 | Driving gear tang broken . | null | closed | Replaced oil pump element
2016-05-11 | Cool Comfort Private Limited | West Bengal | D | Finolex Cabale Limited | Urse, Pune | KC9 | 340K345 | 1 | 2016-07-05 | 207 | 2016-06-05 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-02-02 | 2016-06-05 | ZH | null | null | 3 | Oil pump driving gear tang broken after 3 hrs. | null | closed | Replaced gear kit ( Old type pump)
2016-05-15 | Kalp Marketing | Gujrat | D | Angant Cold Storage | Dewas | KCX3 | 3374K992 | 6 | 2016-04-20 | 1237 | 2016-03-16 | high oil consumption / oil carry over | 2015-12-01 | 2016-02-12 | 50 | null | null | 2 | Removed all piston ring close gap observed 0.8 to 1.5 mm and discharge valve assembly found leakage. | null | closed | Replaced Piston ring set 3 nos , Delivery valve ring & spring set.
2016-05-15 | Kalp Marketing | Gujrat | D | Dharti Cold Storage | Sabarkantha | KCX4 | 3384K1036 | 8 | 2016-04-20 | 1265 | 2016-03-26 | k5 valve leakage | 2015-08-01 | 2016-02-05 | 30 | null | null | 6 | Tal valve leakage from welding - Rework by welding ok. and K5 Valve from seat | null | closed | Replaced K5 Vlave assembly 01 no.
2016-05-15 | Kalp Marketing | Gujrat | D | Keshav Cold Storage | Indore | KC3 | 337K4434 | 7 | 2016-04-20 | 1263 | 2016-03-03 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-05-01 | 2016-01-29 | 150 | null | null | 8 | Gear kit broken | null | closed | Replaced gear kit
2016-05-15 | S M Refrigeration | null | D | R N Cold Storage | null | KC6 | 339K3235 | 6 | 2016-05-05 | null | 2016-03-13 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-11-01 | 2016-02-26 | 200 | null | null | 3 | Oil pressure not builtup hence opened the pump assembly and found drive & driven gear was broken. | null | closed | Replaced oil pump gear kit with cover plate.
2016-05-15 | Kalp Marketing | Gujrat | D | Uttam Dairy | Ahmedabad | KC6 | 339K3133 | 5 | 2016-04-20 | 1361 | 2016-03-14 | knocking / abnormal sound | 2014-12-01 | 2015-05-12 | 4550 | null | null | 5 | Observed bufferspring length 110mm hence replaced. | null | closed | Buffer spring replaced
2016-05-15 | Kalp Marketing | Gujrat | D | Dhanlaxmi Cold Storage | Deesa | KCX2 | 3364K971 | 10 | 2016-04-20 | 1362 | 2016-04-11 | oil pressure not buildup | 2015-12-01 | 2016-02-26 | ZH | null | null | 2 | Driving gear shank found broken. | null | closed | Replaced pump element
2016-05-15 | Kalp Marketing | Gujrat | D | Pavan Cold Storage | Sabarkantha | KCX4 | 3384K1114 | 9 | 2016-04-20 | 1266 | 2016-03-26 | oil pressure not buildup | 2015-12-01 | 2016-03-05 | 30 | null | null | 3 | Driving gear shank found broken. | null | closed | Pump Element replaced
2016-05-15 | Kalp Marketing | Gujrat | D | Jagdish Agri Exporters Pvt Ltd | Madhya Pradesh | KC9 | 340K355 | 3 | 2016-04-20 | 1023 | 2016-02-08 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-10-01 | 2015-12-30 | ZH | null | null | 2 | Discharge pressure gauge found error during commisssioning. | null | closed | Replaced discharge pressure gauge
2016-05-15 | Hss Solution Pvt Ltd | null | D | Sanjay Ice Factory | Rajastan | PC2 | 331K2801 | 1073 | 2016-05-10 | 46 | 2016-04-01 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2016-02-01 | 2016-04-01 | ZH | null | null | 2 | During commissioning found suction gauge not working. | null | closed | Suction pressure gauge replaced. 16.00 Kg/cm2.
2016-05-15 | Kalp Marketing | Gujrat | D | Kiri Dyes & Chemicals | Ahmedabad | KC6 | 339K3071 | 2 | 2016-04-20 | 1004 | 2015-12-29 | shaft seal leakage | 2014-07-01 | 2015-09-07 | 780 | null | null | 14 | Found shaft seal wornout | null | closed | Replaced shaft seal assembly
2016-05-15 | Kalp Marketing | Gujrat | D | Bansidhar Cold Storage | Aravalli | KCX4 | 3384K1152 | 4 | 2016-04-20 | 1267 | 2016-03-08 | shaft seal leakage | 2016-01-01 | 2016-02-20 | 30 | null | null | 1 | Removed shaft seal and heavy carbon deposition observed. Lot of discussion had with customer , the free replacement is agreed. | null | closed | Replaced shaft seal assembly
2016-05-15 | S M Refrigeration | null | D | Sarveshwari Cold Storage | Uttar Pradesh | KC4 | 338K5323 | 5 | 2016-05-05 | null | 2016-03-21 | shaft seal leakage | 2015-11-01 | 2016-02-05 | 100 | null | null | 3 | Observed scoring marks on shaft seal. | null | closed | Replaced shaft seal complete
2016-05-15 | Gargi Engineering Enterprices Pvt Ltd | null | D | Anugrah Cold Storage | Nadiad | KCX4 | 3384K1162 | 1 | 2016-04-20 | null | 2016-02-29 | solenoid valve coil not working / malfunctioning | 2016-02-01 | 2016-02-29 | ZH | null | null | 1 | Valve coil get short circut. Due to Supplied 24 V DC instaed of 230V AC. | null | closed | Replaced coil
2016-05-27 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Foods Pvt Ltd | Taloja, Mh | KC3 | 337K4233 | 7 | 2016-05-18 | 55 | 2016-05-17 | bronze ring wearout | 2014-06-01 | 2015-08-08 | 2000 | null | null | 2 | Bronze thrust ring wearout | null | closed | Replaced bronze and MS thrust ring
2016-05-27 | Cam Marketing | null | E | Wai Mah Trading | Malaysia | KCX6 | 3394K107 | Mail | 2016-05-19 | null | 2016-05-19 | c.case weld leakage | 2009-10-20 | null | null | null | null | null | Weld leak at c.case shell | null | open | null
2016-05-27 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chintu Ice | Turbhe | KCX6 | 3394K517 | 6 | 2016-05-18 | 13 | 2016-05-12 | cutouts not working / malfunctioning | 2015-08-01 | 2016-05-12 | ZH | null | null | 9 | OP cutout not working | null | closed | OP cutout
2016-05-27 | Cool Comfort Private Limited | West Bengal | D | Chandimata Himghar | Ajhapur | KCX6 | 3394K441 | 2 | 2016-05-27 | 106 | 2016-05-13 | high oil consumption / oil carry over | 2015-05-25 | 2016-02-18 | 1200 | null | null | 9 | Piston ring position shifted,gap increased | null | closed | replace liner,piston,pistonrings,VLD assly
2016-05-27 | Cool Comfort Private Limited | West Bengal | D | Shashibhushan Cold Storage | null | KCX4 | 3384K1038 | 3 | 2016-05-27 | 211 | 2016-05-23 | high oil consumption / oil carry over | 2015-09-02 | 2016-02-22 | 886 | null | null | 5 | cut mark in cylinder liner at upper portion | null | closed | Liner,pistonrings,piston
2016-06-05 | Hss Solution Pvt Ltd | null | D | Moti Ice Factory | Jaipur | KC6 | 339K3264 | 1074 | 2016-05-21 | 359 | 2016-04-29 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-12-01 | 2016-03-09 | 685 | null | null | 3 | Oil pump gear damage due to driving plate broken.(Old type pump) | null | closed | Replaced gear kit and driving plate.
2016-06-10 | Kalp Marketing | Gujrat | D | Shreenath Cold Storage | Aravalli | KCX3 | 3374K1022 | 19 | 2016-06-01 | null | 2016-03-26 | k5 valve tight / stem broken / leakage | 2016-01-01 | 2016-02-19 | 150 | null | null | 1 | Leakage from K5 Valve assembly | null | closed | Replaced K5 Vlave
2016-06-10 | Kalp Marketing | Gujrat | D | Kum Kum Cold Storage | Deesa | KCX3 | 3374K960 | 16 | 2016-06-01 | 1084 | 2016-02-27 | k5 valve tight / stem broken / leakage | 2015-10-01 | 2016-02-07 | 24 | null | null | 4 | Leakage from K5 Valve assembly | null | closed | Replaced K5 Vlave
2016-06-10 | Kalp Marketing | Gujrat | D | Part Cold Storage | Dantiwada Bk | KCX4 | 3384K1103 | 15 | 2016-06-01 | 187396 | 2016-02-20 | k5 valve tight / stem broken / leakage | 2015-12-01 | 2016-02-18 | 24 | null | null | 2 | Leakage from K5 Valve assembly | null | closed | Replaced K5 Vlave
2016-06-10 | Kalp Marketing | Gujrat | D | Bhumidhan Cold Storage | Dantiwada Bk | KC3 | 337K4530 | 14 | 2016-06-01 | 1083 | 2016-02-19 | k5 valve tight / stem broken / leakage | 2016-01-01 | 2016-02-15 | 50 | null | null | 1 | Leakage from K5 Valve assembly | null | closed | Replaced K5 Vlave
2016-06-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Lupin Limited | Ankleshwar Gujarat | KC72 | 347K855 | 25 | 2016-06-04 | null | 2016-05-31 | knocking / abnormal sound | 2015-01-01 | 2015-08-01 | 6200 | null | null | 7 | knocking sound from cylinder 1 due to displacement of rollar brg & psacer , connecting small end brg and piston also damage. | null | closed | Replaced Piston connecting rod assembly
2016-06-10 | Kalp Marketing | Gujrat | D | Sagar Samrat Food | Veraval, Gujarat | KC72 | 347K947 | 13 | 2016-06-01 | 190336 | 2016-04-07 | low oil pressure | 2015-04-01 | 2015-07-26 | 2800 | null | null | 3 | Connecting rod rubbing and paper filter blocked | null | closed | Replaced HP Con rod 1 & Paper filter.
2016-06-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shree Ganesh Cold Storage | Himmatnagar | KCX4 | 3384K1104 | 21 | 2016-06-01 | 1392 | 2016-04-20 | manifold thrading damage. | 2015-12-01 | 2016-02-13 | 150 | null | null | 2 | Oil leakage through threading of oil filter housing manifold . | null | closed | Replaced manifold housing due to thrading damage
2016-06-10 | Kalp Marketing | Gujrat | D | Arvalli Cold Storage | Modasa | KCX3 | 3374K1031 | 18 | 2016-06-01 | 1391 | 2016-03-21 | manifold thrading damage. | 2016-02-01 | 2016-03-14 | 250 | null | null | 1 | Oil leakage through threading of oil filter housing manifold . | null | closed | Replaced manifold housing due to thrading damage
2016-06-10 | Kalp Marketing | Gujrat | D | Brahmani Cold Storage | Gandhinagar | KCX4 | 3384K1084 | 17 | 2016-06-01 | 1388 | 2016-03-01 | manifold thrading damage. | 2015-11-01 | 2016-02-19 | 342 | null | null | 3 | Oil leakage through threading of oil filter housing manifold . | null | closed | Replaced manifold housing due to thrading damage
2016-06-10 | Kalp Marketing | Gujrat | D | Bhopal Greeves Ltd | Bhopal | KC3 | 337K4449 | 20 | 2016-06-01 | 1374 | 2016-04-08 | oil pressure not buildup | 2015-06-01 | 2015-08-21 | 300 | null | null | 2 | Oil pump element cover and bushing wornout hence replaced oil pump gear kit. | null | closed | Replced gear kit
2016-06-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Inovative Cuisine P Ltd | Karjan | KC4 | 338K5127 | 24 | 2016-06-04 | 8 | 2016-05-03 | solenoid valve coil not working / malfunctioning | 2014-10-01 | 2016-05-03 | PC | null | null | 19 | Solenoide valve coil not working / Malfunctioning. | null | closed | Replaced coil
2016-06-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jay Ambe Cold Storage | Aravalli | KCX3 | 3374K1013 | 23 | 2016-06-01 | 1390 | 2016-05-15 | stop valve leakage | 2016-01-01 | 2016-02-20 | 640 | null | null | 1 | Gland nut of stop valve found crack or broken hence need to be replaced. | null | closed | Replaced Cap nut
2016-06-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kumkum Cold Storage | Deesa | KCX4 | 3384K1089 | 22 | 2016-06-01 | 1393 | 2016-05-16 | stop valve leakage | 2015-11-01 | 2016-03-06 | 230 | null | null | 4 | Gland nut of stop valve found crack or broken hence need to be replaced. | null | closed | Replaced Cap nut
2016-06-11 | Trade Links | Secunderabad | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K871 | 6 | 2016-05-24 | null | 2016-05-18 | high oil consumption / oil carry over | 2015-03-01 | 2015-12-15 | 1470 | null | null | 9 | Customer informed very high oil consumption of 5 lit/24hrs of running. Inspection of VLD assemblies & Oil return valve (ORV) were done . VLD Orings had wornout & ORV's were replaced. Put back compressor in operation & observed running of compressor for 15hrs. Oil consumption was not observed and overall performance of compresor found satisfactory. | null | closed | Replaced ORV & Orings
2016-06-11 | Trade Links | Secunderabad | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K928 | 5 | 2016-05-24 | null | 2016-05-19 | liner bore cut marks | 2015-09-01 | 2015-12-18 | 1117 | null | null | 3 | Observed abnormal sound from cylinder no. 1 due to cylinder liner had wornout on one side abnormally. Cylinder liner and piston ring set replaced found ok. | null | closed | Replaced cylinder liner & Piston ring set.
2016-06-17 | Kalp Marketing | Gujrat | D | Shree Ganesh Cold Storage | null | KCX3 | 3374K983 | 27 | 2016-06-13 | 14 | 2016-06-08 | cutouts not working / malfunctioning | 2015-12-07 | 2016-02-13 | 127 | null | null | 2 | leakage from OP pressure switch | null | closed | replace pressure switch
2016-06-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Karnataka Stae Fishreies | Karnataka | KCX2 | 3364K773 | 2 | 2016-06-06 | 6 | 2016-05-29 | delivery valve leakage | 2014-09-30 | 2015-03-31 | 3600 | null | null | 6 | del valve ring broken | null | closed | del.valve kit
2016-06-17 | Cool Comfort Private Limited | West Bengal | D | Moti Ice Factory | Jaipur | KC6 | 339K3264 | 1075 | 2016-06-06 | 3 | 2016-05-25 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-12-06 | 2016-03-09 | 918 | null | null | 3 | driving gear siezed | null | closed | Replace oil pump
2016-06-17 | Morgan | null | E | Nawaz Ice Plant | Pakistan | KCX4 | 3384K1216 | null | 2016-06-01 | null | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | null | null | PC | null | null | null | oil pump tang broken | null | closed | replace outer rotor
2016-06-17 | Kalp Marketing | Gujrat | D | Jagdish Agri Exporters Pvt Ltd | Madhya Pradesh | PC2 | 331K2771 | 26 | 2016-06-08 | 11 | 2016-06-01 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2015-09-01 | 2016-01-08 | 24 | null | null | 4 | Replace pressure gauge | null | closed | replace pressure gauge25kg/cm2
2016-06-17 | Kalp Marketing | Gujrat | D | Ashapura Milk Agency | null | KC2 | 336K3202 | 28 | 2016-06-13 | 1367 | 2016-05-23 | shaft seal leakage | 2014-08-01 | 2014-11-28 | 63 | null | null | 3 | Shaft seal leakage | null | closed | Shaft seal assly
2016-06-17 | Morgan | null | E | Ikram Ilha Ice Plant | Pakistan | KC6 | 339K3224 | null | 2016-06-15 | null | 2016-05-10 | solenoid valve coil not working / malfunctioning | 2015-10-07 | 2016-05-30 | ZH | null | null | 7 | solenoid coil not working,stop valve leak | null | closed | replace sol.valve coil & stop vlave
2016-06-17 | Fridge House | null | D | Protac Foods | null | KC93 | 348K122 | 3 | 2016-06-06 | 7 | 2016-05-26 | stop valve leakage | 2015-03-14 | 2016-05-26 | ZH | null | null | 14 | Suction stop valve leak,passing gas | null | closed | Stop valve 125NB
2016-06-22 | Trade Links | Secunderabad | D | Al-Aaqib Traders Llp | R R Dist | KC42 | 344K1040 | 8 | 2016-06-08 | null | 2016-05-26 | k5 valve tight / stem broken / leakage | 2015-12-01 | 2016-05-25 | ZH | null | null | 5 | 2 Nos. K-5 Valve threading had damaged and Discharge pressure gauge having error. | null | closed | Replaced K5 Vlave 02 Nos & Pressure Gauge 01 no.
2016-06-22 | Trade Links | Secunderabad | D | Inogent Laboratories Ltd | Hydrabad | KC6 | 339K3267 | 7 | 2016-06-08 | null | 2016-05-23 | knocking / abnormal sound | 2016-01-01 | 2016-05-23 | ZH | null | null | 4 | Abnormal sound due to piston touches to delivery valve , Liner gasket crushed and tornout . Also Flywheel wobbling due to Crankshaft key & retaining plate loose . | null | closed | Replaced liner gasket , Shaft key and retaining plate.
2016-06-24 | S M Refrigeration | null | D | Shree Bankey | null | KC6 | 338K5418 | 1076 | 2016-06-16 | 6703 | 2016-03-17 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2016-02-06 | 2016-03-17 | PC | null | null | 1 | Driving gear broken | null | closed | Replaced gear kit & cover
2016-06-24 | S M Refrigeration | null | D | Bundelkhand Cold Storage | null | KC3 | 337 K 4402 | 1078 | 2016-06-16 | 4249 | 2016-04-30 | knocking / abnormal sound | 2015-03-06 | 2015-08-28 | 1775 | null | null | 5 | knocking sound observed in compressor | null | closed | Liner,piston,piston ring set,gudgeon pin
2016-06-24 | S M Refrigeration | null | D | Tomar Cold Storage | null | KC4 | 338K5426 | 8 | 2016-06-16 | 117 | 2016-06-15 | solenoid valve not working / malfunctioning | 2016-02-03 | 2016-03-20 | 850 | null | null | 1 | sol.valve assly not working | null | closed | Solenoid valve assly
2016-06-24 | S M Refrigeration | null | D | Chaudhary Jairam Cold Storage | null | KC4 | 338K5307 | 1077 | 2016-06-16 | 4248 | 2016-04-28 | solenoid valve not working / malfunctioning | 2015-10-06 | 2016-02-15 | 390 | null | null | 4 | sol.valve assly not working | null | closed | Solenoid valve assly
2016-06-29 | Parag Marketing Services | null | D | Shrisamarth Factory | Pune | PC2 | 331K2803 | 9 | 2016-06-15 | 26 | 2016-05-31 | high oil consumption / oil carry over | 2016-03-01 | 2016-04-02 | 650 | null | null | 1 | Observed oil throw from both pistons Also wearing of pisto rings . | null | closed | Replaced Piston ring sets
2016-06-29 | Trade Links | Secunderabad | D | Talarai Ice Factory | Goa | PC2 | 331K2757 | 1 | 2016-04-13 | 5 | 2016-03-20 | pc2 oil pump failure | 2015-07-12 | 2015-10-19 | PC | null | null | 3 | The oil pump driving & driven gears were getting jammed in the bushes/housing . Due to lubrication failure crankshaft seized . Mr . Vishal barot came specially from KPC Ahmedabad to investigate new pump not replaced. | null | closed | Replaced shaft seal assly , Bearings , Drive and driven shafts.
2016-06-29 | Trade Links | Secunderabad | D | Talarai Ice Factory | Goa | PC2 | 331K2757 | 66 | 2016-03-02 | 4 | 2016-03-07 | pc2 oil pump failure | 2015-07-12 | 2015-10-19 | PC | null | null | 3 | There was lubrication failure due to oil pump seize resulted into failure of shaft seal and crankshaft berings . Tha oil pump was jammed and compressor stopped. | null | closed | Replaced shaft seal assly , Bearings , Drive and driven shafts.
2016-07-09 | S M Refrigeration | null | D | Devyani Food Industries Ltd | null | KC93 | 348K139 | 1079 | 2016-06-29 | 68 | 2016-06-23 | crank shaft pin wear. | 2016-02-16 | 2016-04-01 | 1158 | null | null | 2 | Scoring on pump cover plate, crank pin wear out. | null | closed | Replaced crank shaft,bearings.
2016-07-09 | S M Refrigeration | null | D | Sarveshwari Cold Storage | Uttar Pradesh | KC4 | 338K5323 | 9 | 2016-06-27 | 4254 | 2016-05-13 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-11-04 | 2016-02-05 | 1302 | null | null | 3 | Gear kit and pump cover scoring | null | closed | Gear kit and pump cover
2016-07-09 | S M Refrigeration | null | D | Kandhri Beverages | Eithigad | KC6 | 339K3240 | 1080 | 2016-07-06 | 25 | 2016-04-18 | oil pressure not buildup | 2015-11-06 | 2016-03-25 | 10 | null | null | 4 | Parts wearout , conrod,bearings, piston,liner | null | closed | bearings, piston,liner
2016-07-13 | null | null | D | M/S India Seafoods | Kannamally | KCX42 | 3444K004 | mail | 2016-07-13 | null | 2016-07-13 | no partition for lp & hp ( on suction side) | null | null | ZH | null | null | null | Due to no drop on suction pressure, they started investigation to find out the problem. Today they dismantled the compressor & found there was no partition for LP & HP ( on suction side) . Discharge side ok. | null | closed | Replaced cylinder liner.
2016-07-18 | Trade Links | Secunderabad | D | Nagrajuna Milk Products | Karimanagar | KC3 | 337K4482 | 12 | 2016-07-05 | null | 2016-06-29 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-12-01 | 2015-12-19 | 1125 | null | null | 1 | Driving gear tang had sheared , Driven gear stuck in the bush and resulting to shearing of tang. | null | closed | Replaced gear kit with cover
2016-07-18 | Trade Links | Secunderabad | D | Tirumala Milk Pproducts | Prakasam Dist | KC6 | 339K3189 | 11 | 2016-07-05 | null | 2016-06-27 | knocking / abnormal sound | 2015-05-01 | 2016-02-20 | 2160 | null | null | 9 | Abnormal sound from cylinder no. 5 due to piston had seized - delivery valve back leakaing. | null | closed | delivery valve assembly
2016-07-18 | Trade Links | Secunderabad | D | Telagana Foods (P) Ltd | Medak Dist | KC72 | 347K819 | 9 | 2016-06-14 | null | 2016-06-07 | low oil pressure | 2014-12-01 | 2015-06-25 | 4000 | null | null | 6 | Max oil pressure observed 3.00Kg/cm2 but during running gratually decrease up to 1.00 kg/cm2 and compressor trip. Again oil pump dismentled checked found ok but oil pressure not increase more than 1.00 Kg/cm2 , Discussed with KPCL H.O. And changed with modified pump. | null | closed | Replaced oil pump with modified pump ( Old pump problem)
2016-07-20 | Trade Links | Secunderabad | D | M/S Dharwad Dairy At | Hubli | KC9 | 340K344 | Mail | 2016-07-20 | null | 2016-04-01 | water jaket leakage | 2014-12-23 | 2015-05-02 | PC | null | null | 2 | Customer started complaining about over heating of the Cylinder Heads and leakage of water jacket. Mr.Muniraju from Fridge House has attended on 1st April 2016 and advised them for cleaning of water jacket . Customer had done the descaling but could not bring down the temperature, and leakage of water jacket got increased further. We have received a complaint from the plant to depute KPC service engineer to rectify the problem and also it was conveyed to us during AAR meeting at Bangalore. We had deputed Mr.Narsimha to check once again for over heating and leakages. As per him the cylinders water passage choaked at Discharge pipe connection due to which water is passing once side only resulting in over heating of the Heads compared to other heads. It seems customer is using RO water for Head cooling . | null | open | Compressoer called back
2016-07-26 | Gargi Engineering Enterprices Pvt Ltd | null | D | Angat Cold Storage | Indore | KCX3 | 3374K992 | 31 | 2016-07-16 | null | 2016-06-06 | high oil consumption / oil carry over | 2015-12-01 | 2016-02-12 | 250 | null | null | 2 | Observed all liner bores/piston rings wornout | null | closed | Replaced Liners /Piston & Piston rings.
2016-07-26 | Kalp Marketing | Gujrat | D | Modasa | Gujrat | KCX3 | 3374K1031 | 1909801464 | 2016-07-02 | null | 2016-06-29 | k5 valve tight / stem broken / leakage | 2016-02-07 | 2016-03-14 | 924 | null | null | 1 | K5 Valve & Shaft seal leakage | null | closed | K5 Vlave & Shaft seal.
2016-07-26 | Gargi Engineering Enterprices Pvt Ltd | null | D | Anupam Rasayan Ltd | Surat, Gujarat | KCX3 | null | 30 | 2016-07-16 | 34 | 2016-06-27 | kcx oil pump purging problem. | null | null | null | null | null | null | Air purging observed in new oil pump assly OP LC 06 16 141 - Replaced. | null | closed | Oil pump assembly replaced.
2016-07-26 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vinod Ice Factory | Surat, Gujarat | KCX6 | 3394K579 | 29 | 2016-07-16 | null | 2016-06-03 | knocking / abnormal sound | 2016-03-01 | 2016-06-02 | 24 | null | null | 3 | Observed safety valve assembly passed or leakage which resulted in to overheating of cylinder no.3 and siezed. | null | closed | Replaced Cyliner assembly .(Liner /Piston/Delivery valve kit/Piston ring set/Gudgeon pin & Taflon Safety valve spring etc.)
2016-07-26 | Gargi Engineering Enterprices Pvt Ltd | null | D | Ahemedabad Phase 4 | Gujrat | KCX3 | 3374K933 | 1907681463 | 2016-07-01 | null | 2016-06-18 | loadingunloadding problem | 2015-10-10 | 2016-06-18 | 50 | null | null | 8 | Solenoid valve & VLD repaired for blockages & Oil level glass crack ??. | null | closed | Replaced oil level glass
2016-07-26 | Kalp Marketing | Gujrat | D | Bhumi Cold Storage | Vadaval Deesa | KCX3 | 3374K 946 , 1073,1074 | 33 | 2016-07-16 | 18 | 2016-05-31 | shaft seal leakage | 2015-11-01 | 2016-02-09 | 550 | null | null | 3 | Shaft seal for both compressor and found Orings in rubbing condition. Eventhough Kirloskar oil used , carbon deposition found in seal port hence recommended free replacement. | null | closed | Replaced Seal Oring kit 03 nos.
2016-07-26 | Kalp Marketing | Gujrat | D | Dwarkesh Ice Factory | Vatva | KC6 | 3394K3247 | 32 | 2016-07-16 | 17 | 2016-06-09 | stop valve leakage | 2015-11-01 | 2016-02-11 | PC | null | null | 3 | Leakage observed from gland nut which is found crack | null | closed | Replaced Gland Nut
2016-07-31 | S M Refrigeration | null | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K928 | Mail | 2016-07-16 | null | 2016-07-16 | liner bore cut marks | 2015-09-01 | 2015-12-18 | 2100 | null | null | 3 | piston ring impression on liner bore | null | closed | Replaced cylinder liner & Piston ring set.
2016-08-01 | Trade Links | Secunderabad | D | Athulitha Laboratories | null | KCX3 | 3374K917 | 13 | 2016-07-19 | 11 | 2016-07-11 | buffer spring shrunk | 2015-08-04 | 2015-11-21 | 4400 | null | null | 3 | buffer spring shrunk | null | closed | Buffer spring
2016-08-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bismilha Frozen | null | KC2 | 336K3247 | 14 | 2016-07-21 | null | 2016-06-18 | cutouts not working / malfunctioning | 2014-10-01 | 2016-04-04 | ZH | null | null | 16 | Op cutout not working | null | closed | OP cutout
2016-08-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bismilha Frozen | null | KC42 | 344K983 | 13 | 2016-07-21 | null | 2016-06-18 | cutouts not working / malfunctioning | 2015-01-06 | 2016-06-17 | ZH | null | null | 17 | OP cutout not working | null | closed | OP cutput
2016-08-01 | Parag Marketing Services | null | D | Agro Fresh Cold Storage | Pawane | KC4 | 338K5396 | 15 | 2016-07-27 | null | 2016-06-17 | high oil consumption / oil carry over | 2016-01-04 | 2016-06-07 | 500 | null | null | 5 | oil carryover 2ltr/24hrs , cyl.no.02&04 high oil throw | null | closed | replace piston rings
2016-08-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aarti Drugs Limited | null | KC6 | 339K3218 | 11 | 2016-06-24 | 27 | 2016-06-22 | kc oil pump low oil pressure problem. | 2015-09-04 | 2016-06-22 | ZH | null | null | 9 | No Ball and spring in oil pressure regulator | null | closed | null
2016-08-01 | Parag Marketing Services | null | D | Deccan Cold Storage | null | KC4 | 338K5372 | 10 | 2016-06-15 | 151 | 2016-05-31 | solenoid valve not working / malfunctioning | 2016-01-01 | 2016-02-06 | 392 | null | null | 1 | solenoid valve leak from seat,loading unloading problem | null | closed | sol.valve assly.
2016-08-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sruvi Crystal Ice | null | PC2 | 331K2813 | 16 | 2016-07-28 | 73 | 2016-06-25 | stop valve leakage | 2016-03-19 | 2016-06-25 | ZH | null | null | 3 | Both stop valves passing gas. | null | closed | null
2016-08-06 | Model Pneumatic Co | Punjab | D | Avtar Cold Storage | Bhatinda | KC4 | 338K5339 | 4 | 2016-08-01 | 36 | 2016-06-28 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-12-04 | 2016-02-29 | 1400 | null | null | 2 | Tang broken, scoring on cover plate | null | closed | Gear kit and cover plate
2016-08-06 | Model Pneumatic Co | Punjab | D | Metro Milk Products | null | KCX6 | 3394K571 | 2 | 2016-07-06 | 30 | 2016-05-08 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-03-06 | 2016-05-03 | ZH | null | null | 2 | Pump elelment tang broken. | null | open | Pump Element replaced
2016-08-06 | Trade Links | Secunderabad | D | Heritage Foods Ltd | null | KC21 | 342K885 | 10 | 2016-06-21 | 547 | 2016-06-08 | stop valve nut crack | 2016-03-05 | null | ZH | null | null | null | Gland cap nut crack | null | closed | Gland nut
2016-08-06 | Cool Comfort Private Limited | West Bengal | E | Kinjore Brewery (P) Ltd | Bhutan | KCX4 | 3384K1012 | Mail | 2016-08-06 | null | 2016-08-06 | suction strainer element missing | 2015-03-06 | 2016-03-27 | PC | null | null | 12 | Suction stariner element missing | null | closed | null
2016-08-12 | Trade Links | Secunderabad | D | Karimnagar Milk Producers Co-Op Union | Karimanagar | KCX3 | 3374K928 | 14 | 2016-08-11 | null | 2016-08-12 | liner bore cut marks | 2015-09-01 | 2015-12-18 | 2100 | null | null | 3 | piston ring impression on liner bore | null | closed | Replaced cylinder liner & Piston ring set.
2016-08-12 | Trade Links | Secunderabad | D | Green House Agro Pproducts | Nillore Dist | KC72 | 347K871 | 15 | 2016-08-11 | null | 2016-08-08 | suction filter hsg fitting leakage | 2015-09-01 | 2016-08-12 | PC | null | null | 11 | Oil leakage was observed from union of suction filter housing. Tried to arrest leakage by tightning but leakage increased. Pipe dia had pinched. | null | closed | Replaced Suction filter top hsg assly
2016-08-14 | S M Refrigeration | null | D | GSSharma Ice Cold Storage | null | KC4 | 338K5441 | 10 | 2016-07-12 | 5242 | 2016-06-22 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2016-03-01 | 2016-06-29 | ZH | null | null | 3 | Marks on cover plate driving gear shaft broken | null | closed | gearkit and cover plate
2016-08-14 | S M Refrigeration | null | D | GSSharma Ice Cold Storage | null | KC4 | 338K5441 | 11 | 2016-07-12 | 126 | 2016-07-07 | knocking / abnormal sound | 2016-03-04 | 2016-06-29 | 36 | null | null | 3 | Replaced crank shaft,connecting rod ,main bearings,piston ring | null | closed | replace crank shaft ,connecting rod,piston ring set main bearings. Gudgeonpin
2016-08-16 | Trade Links | Secunderabad | D | Green House Agro Pproducts | Nillore Dist | KC72 | 347K870 | 18 | 2016-08-16 | null | 2016-08-16 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-08-06 | 2016-08-14 | ZH | null | null | 12 | oil pump cover bush stuck in to driving shaft. | null | closed | Oil pump
2016-08-16 | Kalp Marketing | Gujrat | D | Kumkum Cold Storage | Deesa | KCX3 | 3374K960 | 34 | 2016-08-08 | 6 | 2016-07-18 | solenoid valve not working / malfunctioning | 2015-10-01 | 2016-02-07 | 968 | null | null | 4 | Leakage from Sol. Valve | null | closed | Replace sol. Valve2Nos.
2016-08-17 | Trade Links | Secunderabad | D | Green House Agro | Nellore | KC42 | 344K1032 | Mail | 2016-08-16 | null | 2016-08-16 | c.case weld leak at discharge pipe. | 2015-08-04 | 2016-08-16 | ZH | null | null | 12 | crank case weld leak at discharge pipe. | null | open | null
2016-08-17 | S M Refrigeration | null | D | Ekta Dairy Pvt Ltd | null | KC4 | 338K5445 | 12 | 2016-07-29 | 6787 | 2016-07-09 | knocking / abnormal sound | 2016-03-06 | 2016-05-04 | 725 | null | null | 2 | cutmarks on piston, del. Valve leak, | null | closed | Piston,pistonring set,gudgeon pin,del.valve assly
2016-08-17 | S M Refrigeration | null | D | Devyani Food Industries Ltd | null | KC93 | 340K139 | 1083 | 2016-08-11 | 39 | 2016-08-09 | oil pressure not buildup | 2016-02-06 | 2016-04-01 | 1158 | null | null | 2 | Shaft tight in intermidiate housing | null | closed | Replace intermidiate housing
2016-08-23 | Model Pneumatic Co | Punjab | D | Avtar Cold Storage | Bhatinda | KC4 | 338K5339 | 1084 | 2016-07-06 | 31 | 2016-06-07 | shaft seal leakage | 2016-12-06 | 2016-02-24 | 1200 | null | null | 2 | Shaft seal leakage | null | closed | Shaft seal assly
2016-08-23 | Trade Links | Secunderabad | D | Vimal Drugs Vishakahpattanam | null | KC21 | 342K880 | 17 | 2016-08-16 | 413 | 2016-08-03 | solenoid valve not working / malfunctioning | 2015-12-03 | 2016-07-04 | 125 | null | null | 7 | Sol. Valve not operating | null | closed | Sol. Valve assly
2016-08-23 | Trade Links | Secunderabad | D | S F C Ice Factory | null | KCX4 | 3384K1226 | 16 | 2016-08-16 | 1 | 2016-07-02 | tah8 valve stem broken | 2016-06-03 | 2016-06-28 | 40 | null | null | 1 | TAH8 valve stem broken and leak from 6mm tubing | null | closed | TAH8 valve
2016-08-29 | Vietbon Co. | null | E | Vinh Luong Ice Factory | null | KCX9 | 3404K16 | Mail | 2016-08-11 | 16 | 2016-08-07 | knocking / abnormal sound | 2015-05-02 | 2016-08-07 | ZH | null | null | 15 | Piston touches to delivery valve in cyl.no.05,06 & 07 | null | closed | null
2016-08-29 | Vietbon Co. | null | E | Vinh Luong Ice Factory | null | KCX9 | 3404K17 | Mail | 2016-08-11 | 17 | 2016-08-07 | loadingunloadding problem | 2015-05-02 | 2016-08-07 | ZH | null | null | 15 | Cylinder no. 06 not coming on load | null | open | null
2016-08-29 | Kirloskar Dmcc | null | E | Cascade Marine Foods Llc | null | KC42 | 344K1009 | 1 | 2016-08-17 | 1 | 2016-08-17 | low oil pressure big end bearing , piston, gudgeon pin worn out | 2015-04-06 | 2015-09-07 | 7500 | null | null | 5 | Needel roller bearing broken,piston worn out,big end bearing worn out | null | closed | piston, gudgeon pin, needel roller bearing
2016-08-29 | Kirloskar Dmcc | null | E | Cascade Marine Foods Llc | null | KC63 | 346K201 | 2 | 2016-08-17 | 2 | 2016-08-17 | shaft seal leakage | 2014-01-05 | 2014-11-16 | 12000 | null | null | 6 | Shaft seal leakage | null | closed | Shaft seal required to replaced.
2016-09-10 | null | null | D | Varun Beverages Limited | null | KC6 | 339K3232 | null | null | 31 | 2016-09-10 | abnormal noise | 2015-11-21 | 2016-03-05 | PC | null | null | 4 | COMPRESSOR TRIPPED WITH ABNORMAL NOISE,CONNECTING ROD BOLT BROKEN | null | closed | null
2016-09-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chintu Ice | Turbhe | KCX6 | 3394K509 | 17 | 2016-08-04 | 33 | 2016-08-01 | cutouts not working / malfunctioning | 2015-07-01 | 2016-08-01 | ZH | null | null | 12 | During commissioning though oil pressure is 2.00 Kg/cm2 , more than suction pressure oil pressure cut out was tripping and very difficult to reset as top push button was not pressing to the plate. Also pressure gauges not working and was showing wrong pressure reading. | null | closed | Replaced cut out , sol valve & pressure gauges.
2016-09-10 | Parag Marketing Services | null | D | Vaishnodevi Food Products PvtLtd | Solapur | KCX3 | 3374K859 | 20 | 2016-08-29 | 261 | 2016-08-18 | high oil consumption / oil carry over | 2015-01-01 | 2015-06-03 | 900 | null | null | 5 | High opn oil throw from piston no. 3 due to wearing of piston rings also delivery valves leakages - 02 nos . | null | closed | Replaced set piston ring and delivery valve ring/spring kit
2016-09-10 | Trade Links | Secunderabad | D | Tropical Mushrooms Pvt Ltd | Goa | KC3 | 337K4413 | 12 | 2016-07-14 | null | 2016-06-08 | high oil consumption / oil carry over | 2015-04-12 | 2015-10-15 | 3206 | null | null | 6 | Piston ring set and ORV replaced | null | closed | Piston ring set and ORV replaced
2016-09-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Mahad | KCX2 | 3364K977 | 18 | 2016-08-12 | 62 | 2016-08-12 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-01-01 | 2016-02-29 | 652 | null | null | 2 | Outer rotor tang broken | null | closed | Replaced pump element
2016-09-10 | Parag Marketing Services | null | D | Indapur Dairy And Milk Product | Baramati | KCX3 | 3374K1087 | 19 | 2016-08-24 | 174 | 2016-08-13 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-05-13 | 2016-07-05 | 172 | null | null | 2 | Inner rotor jammed and broken outer rotor tang. | null | closed | Replaced pump element.
2016-09-12 | Trade Links | Secunderabad | D | Wellcome Fisheries | Godavari Dist | KCX6 | 3394K565 | 19 | 2016-08-24 | null | 2016-08-12 | knocking / abnormal sound | 2016-02-01 | 2016-09-12 | ZH | null | null | 7 | Cylinder no. 3 knocking sound observed after 20 min running of compressor due to liner gasket damaged, delivery valve back leaking . Also NO type solenoide valve not operating. | null | closed | Replaced , Liner gaskets ,Delivery valve assembly & No type solenoid valve.
2016-09-14 | null | null | D | Kc Dairy Products Pvt Ld | null | KCX3 | 3374K1044 | null | null | null | 2016-09-14 | abnormal noise | 2016-02-16 | 2016-07-06 | PC | null | null | 5 | abnormal sound. liner gasket damaged and due to that liner misalligned | null | closed | null
2016-09-14 | null | null | D | M/SIndo Fisheries | null | KC51 | 345K988 | null | null | null | 2016-09-14 | abnormal noise | 2016-06-25 | 2016-08-22 | PC | null | null | 3 | Knocking sound in Cyl.No.5 liner gasket damaged & Oil leakage through 22mm Pipe at Discharge Filter Top Housing side. | null | closed | null
2016-09-20 | null | null | D | Sk Cold Storage | null | KC3 | 337K4643 | null | null | null | 2016-09-20 | abnormal noise | 2016-05-18 | 2016-09-15 | PC | null | null | 4 | KNOCKING SOUND IN CYLINDER NO-3 | null | closed | LINER, PISTON, PISTON RING SET, DV ASSEMBLY & BUFFER SPRING.
2016-09-21 | null | null | D | BMEngineers & Consultants | null | KCX3 | 3374K932 | null | null | null | 2016-09-21 | comp cylinder overheat | 2015-10-06 | 2015-11-20 | PC | null | null | 1 | Knocking Sound & Cyl.No.3 Over Heat Checked & found piston damaged, Buffer Spring tension reduced i.e.98-100mm.D.V.Assy leakage and also found limit stroke legs ununiformed. | null | closed | Buffer Spring tension reduced i.e.98100mm.D.V.Assy
2016-09-21 | S M Refrigeration | null | D | Flex Foods Ltd | Tamil Nadu | KC93 | 348K093 | email | 2016-09-20 | null | 2016-09-20 | heavy system dust found in cylinders | 2013-11-08 | 2013-06-01 | null | null | null | null | spourios parts used by customer, system dust | null | closed | null
2016-09-24 | Trade Links | Secunderabad | D | Vizaq Food P Ltd | Vishakhapatanam | KC72 | 347K806 | 20 | 2016-09-06 | null | 2016-09-02 | knocking / abnormal sound | 2014-11-01 | 2016-08-27 | PC | null | null | 21 | After running for 22 hrs observed abnormal sound from cylinder 4 , cylinder seized due to delivery valve back leaking & Overheated cylinder . | null | closed | Replaced delivery valve and cylinder assembly .
2016-09-28 | Cool Point | null | E | Dorar Dammam Trading Est | null | KCX6 | 3394K588 | Mail | 2016-09-28 | null | 2016-09-28 | side cover bolt missing | 2016-05-01 | null | ZH | null | null | null | 01 no. bolt missing | null | null | null
2016-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Al-Baser Exports Neptune | Parbhani | KC21 | null | null | null | null | null | wrong labelling of pressure name plates | null | null | ZH | null | null | null | wrong labelling At intermediate pressure labeled as Discharge pressure & at Discharge pressure labeled as intermediate pressure | null | null | null
2016-10-02 | null | null | D | M/SHatsun Agro Product Ltd | null | KC4 | 338K3963 | null | null | null | 2016-10-02 | overhauling servicing | 2009-03-31 | null | PC | null | null | null | Checked & found there was a problem in Oil Pump Assy. | null | closed | null
2016-10-03 | null | null | D | Girnar Dairy P Ltd | null | KC3 | 337K4622 | null | null | null | 2016-10-03 | direct piston loading problem in compressor starting time | 2016-03-31 | 2016-05-26 | PC | null | null | 2 | KC Oil Pump Time Delay Problem | null | closed | TD plunger
2016-10-04 | null | null | D | M/S SL Ice & Chilling Plant | null | KC3 | 337K4616 | null | null | 6829 | 2016-10-04 | oil lifting | 2016-03-26 | 2016-06-05 | PC | null | null | 3 | Oil lifting problem | null | closed | Piston and liner
2016-10-05 | null | null | D | M/SSeutic Labs PvtLtd | null | KCX42 | 3444K014 | null | null | null | 2016-10-05 | knocking / abnormal sound | 2016-05-24 | 2016-09-10 | PC | null | null | null | Observed & found there is no any sound in the compressor. | null | closed | null
2016-10-06 | null | null | D | Tata Projects Limited | null | KCX6 | 3394K648 | null | null | null | 2016-10-06 | abnormal noise | 2016-09-27 | 2016-10-04 | PC | null | null | null | null | null | closed | null
2016-10-07 | null | null | D | Samson Enterprises | null | KCX2 | 3364K841 | null | null | null | 2016-10-07 | abnormal noise | 2015-03-16 | 2015-07-15 | PC | null | null | 4 | LINER GASKETS FOUND DAMAGE | null | closed | null
2016-10-07 | S M Refrigeration | null | D | Yadav Cols Storage And Ice Factry | null | KC6 | 339K3293 | 1632 | 2016-10-06 | 5465 | 2016-10-06 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2016-02-17 | 2016-04-08 | 1351 | null | null | 2 | Oil pump assly | null | closed | Oil pump assly
2016-10-07 | Cool Comfort Private Limited | West Bengal | D | Akj Cold Storage | null | KC51 | 345K941 | 1622 | 2016-10-04 | 263 | 2016-10-04 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-03-27 | 2016-10-03 | ZH | null | null | 18 | Both gears ceased into oil pump body, cover and body damaged. | null | closed | Oil pump assembly
2016-10-07 | S M Refrigeration | null | D | Giriraj Ice Factory & Milk Chilling | null | KC3 | 337K4445 | 1633 | 2016-10-06 | 633 | 2016-10-06 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-06-10 | 2016-01-02 | 633 | null | null | 7 | Replace gearkit old type | null | closed | Gearkit
2016-10-07 | Gargi Engineering Enterprices Pvt Ltd | null | D | Versova Koli Sahkari Sarvoday Societyu | null | KCX6 | 3394K544 | 1631 | 2016-10-06 | 88 | 2016-10-06 | liner bore cut marks and oil carryover | 2015-12-06 | 2015-12-11 | 5000 | null | null | 1 | 04 liners found cut marks in bore and pistonring sets wearout | null | closed | liner 04 nos.,piston ring set6nos.
2016-10-07 | Hss Solution Pvt Ltd | null | D | Snow Planet | null | KC3 | 337K4532 | 1621 | 2016-10-03 | 34 | 2016-10-03 | shaft seal leakage | 2016-01-20 | 2016-04-07 | 2694 | null | null | 3 | Shaft seal leakage | null | closed | shaft seal assly
2016-10-07 | S M Refrigeration | null | D | Bhanwal Bhatt Co | null | KCX4 | 3384K1208 | 1620 | 2016-10-03 | 12 | 2016-09-03 | solenoid valve coil not working / malfunctioning | 2016-04-24 | 2016-05-23 | ZH | null | null | 1 | 24VDC coils burnt during commissioning | null | closed | 24VDC coils
2016-10-10 | null | null | D | Grand Marine Foods | null | KCX72 | 3474K018 | null | null | 4736 | 2016-10-10 | abnormal noise | 2016-07-27 | 2016-08-19 | PC | null | null | 1 | 1st Piston hitting on the Delivery Valve. Also found the Big End Bearing of the same worn out. The Crank Shaft also worn out approx. 15mm to 20mm. | null | closed | Crankshaft & bearings
2016-10-12 | null | null | D | Lakhani Dyestuff(P)Ltd | null | KCX3 | 3374K875 | null | null | null | 2016-10-12 | abnormal noise,piston touching to dv assy due to liner gaskets damaged | 2015-03-22 | 2015-11-08 | PC | null | null | 6 | liner gasket all 3 liners found damaged | null | closed | null
2016-10-12 | null | null | D | Sai Cold Storage | null | KC3 | 337K4522 | null | null | 1003 | 2016-10-12 | leakage from shaft seal cover | 2015-12-21 | 2016-03-23 | PC | null | null | null | null | null | closed | null
2016-10-13 | null | null | D | M/S Kissan Cold Storage & General Mills | null | KCX6 | 3394K556 | null | null | 6832 | 2016-10-13 | oil pressure not buildup | 2016-01-06 | 2016-02-17 | PC | null | null | 1 | Oil Pressure not build up properly | null | closed | Pump element
2016-10-14 | null | null | D | Pahalwan Cold Storage | null | KC3 | 337K4528 | null | null | null | 2016-10-14 | loading unloading problem. | 2016-01-02 | 2016-02-09 | PC | null | null | null | Load / Unloading Problem | null | closed | null
2016-10-15 | null | null | D | M/SAlpha Agro & Cold Storage | null | KCX31 | 3434K0019 | null | null | null | 2016-10-15 | shaft seal leakage and low oil pressure. | 2016-07-31 | 2016-09-20 | PC | null | null | 2 | Checked and found more scratch marks on Stationary Ring and dirty particles.And also found insufficient Oil Circulation in to Shaft Seal.And observed loading problem due to more foreign particles in VLD Housing of HP Cylinder. | null | closed | shaft seal assly
2016-10-17 | null | null | D | M/SAbhiman Ice & Cold Storage | null | KCX4 | 3384K1231 | null | null | null | 2016-10-17 | shaft seal leakage | 2016-06-13 | 2016-08-05 | PC | null | null | 2 | Run the Comp observed little bit of oil leakage through Shaft Seal end.Opened & found moisture contents or liquid form in Shaft Seal. | null | closed | null
2016-11-08 | Trade Links | Secunderabad | D | Varun Beverage Limited | Goa | KC6 | 339K3232 | 21 | 2016-10-19 | 35 | 2016-10-08 | abnormal noise | 2015-11-21 | 2016-03-05 | PC | null | null | 4 | COMPRESSOR TRIPPED WITH ABNORMAL NOISE,CONNECTING ROD BOLT BROKEN | null | closed | null
2016-11-23 | Fridge House | null | D | Karnataka State Agriculture Produce Processing And Export | Karnataka | KC42 | 344K1050 | 194778 | null | null | 2016-11-14 | abnormal noise | 2015-03-13 | 2016-05-05 | PC | null | null | 14 | Observed Knocking sound in Cyl.No1,Checked & found Piston & Piston Rings damaged.D.V.Assy leakage,Buffer Spring Tension lower.Reg:Loading & Unloading Problem found VLD Bush Jammed. | null | closed | Replaced piston,piston ring,del.valve assly,buffer spring
2016-11-23 | Fridge House | null | D | Bangera Oversease Pvt Ltd | null | KCX4 | 3384K119 | 194590 | null | null | 2016-11-05 | oil leakage from cylinder head covers | 2016-03-21 | 2016-07-15 | PC | null | null | 4 | First of all this model is not suitable for this much of capacity application.This model running with 100% of SP 0.5Kg/Cm2.Thus Comp will be becomes Super Heat and it will be effected comp parts. | null | open | null
2016-11-23 | Fridge House | null | D | Fouress Foods | null | KC72 | 347K922 | 194780 | null | null | 2016-11-16 | shaft seal leakage | 2016-03-31 | 2016-10-10 | ZH | null | null | 7 | Scratches on shaft seal seat face | null | closed | Shaft seal assly
2016-11-27 | Kirloskar Dmcc | null | E | Cascade Marine Foods Llc | null | KC42 | 344K1009 | null | null | null | null | low oil pressure & crankshaft wornout | 2015-03-13 | 2016-05-05 | 8618 | null | null | 5 | The Crankshaft has been damaged on the both the high stage side of the big end bearing. | null | open | null
2016-11-29 | null | null | D | Maa Ratantikalimata Cold Storage PvtLtd | null | KCX4 | 3384K1061 | 195074 | null | 319 | 2016-11-08 | abnormal noise | 2015-11-04 | 2016-03-01 | PC | null | null | 4 | Cylinder liner seating gasket damaged. | null | closed | null
2016-11-29 | null | null | D | Maa Ratantikalimata Cold Storage PvtLtd | null | KCX4 | 3384K1053 | 195104 | null | 320 | 2016-11-09 | abnormal noise | 2015-10-24 | 2016-01-22 | PC | null | null | 3 | Cylinder liner seating gasket damage. | null | closed | null
2016-11-29 | null | null | D | Rahis Cold Storage PvtLtd | null | KCX4 | 3384K1068 | 195070 | null | 363 | 2016-11-14 | abnormal noise | 2015-11-10 | 2016-02-26 | PC | null | null | 3 | Open 3nos cylinder liner change damage liner seating gasket maintan top clearance refetting the compressor, After than running satisfactorily. | null | closed | null
2016-11-29 | null | null | D | Damal Cold Storage | null | KCX3 | 3374K1016 | 195068 | null | 359 | 2016-11-09 | comp cylinder overheat | 2016-01-20 | 2016-02-23 | PC | null | null | 1 | Delivary valve minor leakage. | null | closed | null
2016-11-29 | null | null | D | Periyar Ice Plant | null | KCX4 | 3384K1129 | 195122 | null | 4022 | 2016-11-21 | cylinder liner worn out. | 2016-06-12 | 2016-07-23 | PC | null | null | 1 | Cylinder Liner Worn out. | null | closed | Changed Liner, Rings, VLD O Ring, Safety Plate
2016-11-29 | null | null | D | Aqua Marine | Odisha | KCX21 | 3424K007 | 195076 | null | 342 | 2016-11-18 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2015-04-10 | 2016-11-19 | ZH | null | null | 17 | While commissioning of the compressor pump element tang broken during free air run. | null | open | null
2016-11-29 | null | null | D | Rahis Cold Storage PvtLtd | null | KCX6 | 3394K545 | 195088 | null | 365 | 2016-11-15 | knocking / abnormal sound | 2015-12-09 | 2016-02-26 | PC | null | null | 2 | Cylinder liner seating gasket damaged. | null | open | null
2016-11-29 | null | null | D | M/SProtac International Foods | null | KCX3 | 3374K873 | 195080 | null | null | 2016-11-27 | knocking / abnormal sound | 2015-03-14 | 2016-05-14 | PC | null | null | 14 | Checked & found VLD Guide Bush & Actuating Plungers are Jammed.And also found liner gaskets damaged in all Cylinders. | null | closed | null
2016-11-29 | null | null | D | East India Cold Storage (P) Ltd | null | KC4 | 338K5180 | 195110 | null | 321 | 2016-11-14 | loading & unloading problem. | 2015-01-07 | 2015-04-06 | PC | null | null | 3 | Open solenoid valve, polish expended plunger rubber, After then compressor running satisfactorily. | null | closed | null
2016-11-29 | null | null | D | Dihibatpur Cold Storage Pvt Ltd | null | KC3 | 337K4411 | 195066 | null | 289 | 2016-11-09 | shaft seal leakage | 2015-03-31 | 2016-03-12 | PC | null | null | 12 | Scratch mark in shaft seal meeting face and inner, outer 'O'Ring dameged. | null | closed | null
2016-11-29 | null | null | D | B K Spices & Floors | null | KCX2 | 3364K1073 | Mail | 2016-11-22 | null | 2016-11-22 | wrong cutout fitted | 2016-04-27 | 2016-10-20 | ZH | null | null | 6 | two Nos HP (KP-5A) pressure cut outs fitted in the safety cut outs panel box. | null | closed | null
2016-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Supreet Chemicals | Vapi, Gujarat | KC6 | 339K3309 | Mail | null | null | null | abnormal noise | 2016-03-01 | 2016-12-21 | ZH | null | null | 9 | Noise after running of four hours & found cylinder -1 , buffer spg length down to 90 mm & dv assy was passing as ring spg of dv assy was broken. | null | open | Need to replace Buffer spring & delivery valve
2016-12-21 | null | null | D | Heritage Foods Ltd | null | KCX4 | 3384K1221 | null | null | null | 2016-12-15 | abnormal noise | 2016-05-17 | 2016-06-21 | PC | null | null | 1 | Replace cylinder liner gaskets and piston ring set | null | closed | Replace cylinder liner gaskets and piston ring set
2016-12-21 | null | null | D | Avla Nettos Export | null | KC51 | 345K964 | null | null | 4221 | 2016-12-14 | high oil consumption / oil carry over | 2015-08-26 | 2016-08-05 | PC | null | null | 12 | replaced VLD Orings | null | closed | replaced VLD Orings
2016-12-21 | null | null | D | Godrej Agrovet | null | KC21 | 342K654 | null | null | null | 2016-12-12 | high oil consumption / oil carry over | 2016-02-05 | 2016-04-11 | PC | null | null | 2 | replaced piston and piston rings | null | closed | piston and piston rings
2016-12-21 | null | null | D | St Xavier Ice | Goa | KCX2 | 3364K243 | Mail | null | null | null | liner bore cut marks and oil carryover | 2009-04-01 | null | null | null | null | null | Replaced liner and piston ring sets in july-16 | null | null | null
2016-12-21 | null | null | D | Al Balshir Export | null | KC72 | 347K946 | Mail | null | null | null | loading & unloading problem. | 2015-07-04 | 2016-10-02 | PC | null | null | 15 | Suction valve ring not fitted properly in liner step bore | null | closed | Replace liner and suction valve ring
2016-12-21 | null | null | D | Sankar Ice Factory | null | KCX1 | 3354K008 | 195348 | 2016-12-03 | 451 | null | loading & unloading problem. | 2016-05-14 | 2016-07-20 | PC | null | null | 2 | Solenoid valve coil replaced | null | closed | null
2016-12-21 | null | null | D | A A Enterprises Industries Estate | Prakasam Dist | KC3 | 337K4567 | null | 2016-12-06 | null | null | shaft seal leakage | 2016-02-07 | 2016-03-17 | PC | null | null | 1 | Bronze thrust ring wearout resulting in to shaft seal worn out | null | closed | Shaft seal assly
2016-12-27 | Fridge House | null | D | Fouress Foods | null | KC51 | 345K981 | 195724 | null | null | 2016-12-20 | leakage from ferule fitting of discharge filter housing | 2016-03-31 | 2016-10-10 | PC | null | null | 7 | Observed Oil leakage in 22mm Dia pipe(Ferrule placed area) which is connected from Oil Pump to Discharge Filter.Even replaced the Ferrules problem not solved.Hence,thoroughly inspected by our Service Engineer he found Ferrule is not Seating Properly. | null | null | Discharge filter housing top
2016-12-27 | Fridge House | null | D | Fouress Foods | null | KC42 | 344K1062 | 195754 | null | null | 2016-12-20 | leakage from ferule fitting of discharge filter housing | 2016-03-31 | 2016-10-10 | PC | null | null | 7 | Observed Oil leakage in 22mm Dia pipe(Ferrule placed area) which is connected from Oil Pump to Discharge Filter.Even replaced the Ferrules problem not solved.Hence,thoroughly inspected by our Service Engineer he found Ferrule is not Seating Properly. | null | null | Discharge filter housing top
2016-12-27 | Fridge House | null | D | Kappec Ltd | null | KC2 | 336K2966 | 195760 | null | null | 2016-12-21 | shaft seal leakage | 2013-02-04 | null | PC | null | null | null | Found Shaft Seal Leakage due to more dust particles in the Comp & Shaft Seal Cover.Suction Strainer Cloth Bag NT removed. | null | null | Shaft seal assly replaced
2016-12-30 | null | null | E | null | null | KCX6 | 3394K0001 | null | null | null | null | tubing quantity short | null | null | ZH | null | null | null | null | null | null | null
2016-12-31 | null | null | D | Pabitro Agrotech (P) Ltd | null | KCX3 | 3374K934 | 195996 | null | 346 | 2016-12-25 | abnormal noise | 2015-10-11 | 2016-09-15 | PC | null | null | 11 | Excessive gap in between piston & cylinder liner bore, also damage in piston ring. | null | null | Replaced liner and piston ring sets
2016-12-31 | null | null | D | Versova Koli Sahakari Sarvodaya Society Ltd | null | KCX6 | 3394K544 | 195924 | null | 609 | 2016-12-25 | liner bore cut marks in cyl no.01,02,04&05 | 2015-12-06 | 2015-12-11 | PC | null | null | 1 | Replaced liner and piston ring sets | null | null | Replaced liner and piston ring sets
2016-12-31 | null | null | D | Sagar Samrat Sea Foods | null | KC72 | 347K781 | 195856 | null | null | 2016-12-26 | low oil pressure | 2014-08-10 | 2014-11-28 | PC | null | null | 3 | null | null | null | null
2016-12-31 | null | null | D | Milsha Agro Exports (P) Ltd | null | KCX72 | 3474K011 | 195764 | null | 435 | 2016-12-19 | shaft seal leakage | 2016-03-27 | 2016-05-18 | PC | null | null | 2 | Shaft seal 'o'ring damaged. | null | null | null
2016-12-31 | null | null | D | Celebrity Breweries | West Bengal | KCX4 | 3384K1052 | 195986 | null | 529 | 2016-12-19 | shaft seal leakage | 2015-10-21 | 2016-12-08 | PC | null | null | 14 | Scratch mark on sealing face and O ring damaged | null | null | Replace shaft seal assly
2016-12-31 | null | null | D | Maa Ratantikalimata Cold Storage PvtLtd | null | KCX4 | 3384K1053 | 195984 | null | 529 | 2016-12-19 | shaft seal leakage | 2015-10-24 | 2016-01-22 | PC | null | null | 3 | Replace shaft seal assly | null | null | Replace shaft seal assly
2016-12-31 | Trade Links | Secunderabad | D | Ananda Enterprises | null | KC72 | 347K815 | 195874 | null | null | 2016-12-14 | shaft seal leakage | 2014-12-24 | 2015-08-06 | PC | null | null | 7 | Thrust ring worn out ,shaft seal assly worn out | null | null | Shaft seal assly replaced
2016-12-31 | null | null | E | Morgan | Pakistan | KC42 | 344K10587 | Mail | 2017-01-01 | null | 2017-01-01 | tubing qty.short | 2016-11-15 | 2016-12-25 | ZH | null | null | 1 | There were only two tubes instead of four. Client is asking for remaining tubes. | null | null | null
2017-01-04 | null | null | D | Fortune Industries | null | KCX2 | 3364K1044 | 196080 | null | null | 2017-01-02 | damage problem in vld piston & lever. | 2016-03-23 | 2016-07-25 | PC | null | null | 4 | In according to previous visit @ site, that time found problem in VLD piston ( cylinder No.01) and lever . The lever is damage condition. Remove Piston assembly and Linear assembly. At that time found tap bolt ( 02 Nos. )was broken condition. So, Replace Spare parts like a VLD Piston (01 Nos.), Lever (01 Nos.), Tap bolt (02 Nos.), Tap bolt nut(04 Nos.), Head cover gasket (02 Nos.), Linear Gasket(02 nos.). Refitting Compressor and take a full load trial. it's working ok. | null | null | VLD piston and lever
2017-01-21 | Trade Links | Goa | D | Varun Beverage Limited | null | KC6 | 339K3232 | 21 | 2016-10-19 | 35 | 2016-10-08 | abnormal noise | 2015-11-01 | 2016-03-06 | PC | null | null | 4 | connecting rod bolt broken, and liner damaged | null | null | connecting rod bolt broken, and liner damaged
2017-01-23 | Kalp Marketing | Gujrat | D | Devansh Industries | null | KCX4 | 3384K1274 | 1960721785 | 2017-01-03 | null | 2016-12-28 | flywheel key damaged | 2016-09-17 | 2016-11-09 | 988 | null | null | 2 | Flywheel key damaged | null | closed | null
2017-01-23 | Trade Links | Secunderabad | D | Lakshmi Saras Chem Tech | null | KCX4 | 3384K1213 | 1962061788 | 2017-01-09 | null | 2017-01-06 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-05-04 | 2016-09-20 | 450 | null | null | 4 | Driven gear had struck & resulted t o shearing of driving gear tang | null | closed | null
2017-01-23 | Trade Links | Secunderabad | D | Heritage Foods Ltd | null | KCX2 | 3364K1107 | 1963241794 | 2017-01-13 | null | 2017-01-04 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2016-07-13 | 2017-01-07 | ZH | null | null | 5 | One pressure gauge not working & other Pressure gauge is having error of 0.5 Kg/cm2 | null | closed | null
2017-01-23 | Trade Links | Secunderabad | D | Heritage Foods Ltd | null | KCX2 | 3364K1108 | 1963261795 | 2017-01-13 | null | 2017-01-04 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2016-07-13 | 2017-01-07 | ZH | null | null | 5 | Suction pressure gauge having error of 0.5 Kg/cm2 | null | closed | null
2017-01-23 | Kalp Marketing | Gujrat | D | Fortune Industries | null | KCX2 | 3364K1044 | 1960481781 | 2017-01-03 | null | 2016-12-27 | shaft seal leakage | 2016-03-23 | 2016-07-25 | 1500 | null | null | 4 | Shaft seal leakge , worn out. | null | closed | null
2017-01-24 | null | null | D | Mandya Milk DistCoOp Milk Prod'S Societies Union Ltd | Mandya Dist | KCX6 | 3394K593 | 196662 | null | null | 2017-01-15 | 1) high oil consumption 2) abnormal sound in unloading time @ cyl.no.3 & 6 3) air purging problem. | 2016-05-28 | 2016-07-09 | PC | null | null | 2 | Replaced 4 Nos.of Piston Ring Set & rectified the problem.Replaced liner gaskets of Cyl.No.3 & 6. And also Serviced for Oil Pump Assy & put back same. Now Comp is running with good condition. | null | closed | Changed piston ring set
2017-01-24 | null | null | D | Maa Tara Cold Storage | null | KCX2 | 3364K997 | 196102 | null | 501 | 2017-01-01 | abnormal noise from cylinder. | 2016-01-25 | 2016-03-29 | PC | null | null | 2 | Total compressor clean, Replace both sied buffer spring, Replace paper filter, wire filter & VLD 'O'ring, Reffitting the compressor, Run the compressor free & full load compressor running satisfactorily. | null | closed | null
2017-01-24 | null | null | D | M/S Bp Frozen Food | null | KC6 | 339K3323 | 196622 | null | 6882 | 2017-01-15 | abnormal noise problem | 2016-09-11 | 2017-01-03 | PC | null | null | 3 | Required following spares to set right the compressor | null | closed | null
2017-01-24 | null | null | D | Vedant Ediable Product Pvt Ltd | null | KC93 | 348K142 | 196606 | null | 120 | 2017-01-16 | compressor has been breakdown due to thrust ring bronze broken in running condition . | 2016-06-21 | 2017-01-04 | PC | null | null | 6 | Thrust ring bronze broken | null | closed | Replaced thrust ring bronze
2017-01-24 | null | null | D | Mother Agro Cold Storage Pvt Ltd | null | KCX3 | 3374K937 | 196490 | null | null | 2017-01-11 | high oil consumption | 2015-10-13 | 2015-11-18 | PC | null | null | 1 | Open up all three head. Checked direct piston and measure Piston ring gap 0.8 mm with second and third cylinder piston ring gap 0.6 mm. So, Change direct cylinder piston ring set . These change approved by Mr. Vishal Barot from KPC - Ahmedabad. Change VLD inner & Outer "O" Ring & NRV. Check found OK. Then refitting all spare parts & take full load trial OK. | null | closed | null
2017-01-24 | null | null | D | Front Line Exports Pvt Ltd | null | KC51 | 345K986 | 196612 | null | 4072 | 2017-01-19 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2016-05-06 | 2016-12-01 | PC | null | null | 7 | REPLACED THE OIL PUMP | null | closed | REPLACED THE OIL PUMP
2017-01-27 | null | null | D | Fortune Industries | null | KCX2 | 3364K1044 | 196796 | null | null | 2017-01-20 | loading unloading problem. | 2016-03-23 | 2016-07-25 | PC | null | null | 3 | null | null | null | null
2017-01-27 | null | null | D | Mohit Cold Agro | null | KC3 | 337K4609 | 196724 | null | null | 2017-01-21 | machine jam condition | 2016-03-22 | 2016-06-14 | PC | null | null | 2 | OPEN ALL HEAD AND REMOVE PISTON AND ALL PARTS CLEAN BY PETROL APPLY ONE SET PISTON RING REFITTING COMPRESSOR TAKE TRAIL FULLY LOAD DONE. | null | null | null
2017-01-27 | null | null | D | Aapni Sales Agency Fish Market | null | KCX3 | 3374K918 | 196726 | null | null | 2017-01-23 | shaft seal leakage | 2015-08-11 | 2015-10-15 | PC | null | null | 2 | OPEN SEAL AND BOTH BEARING COVER CHANGE ALL ORING AND SERVICE OF SEAL. REFITTING ALL OVER COMPRESSOR START FULLY LOAD TRAIL DONE. | null | null | null
2017-01-28 | Kalp Marketing | Gujrat | D | Honest Frozen Foods | null | KC31 | 343K1497 | null | null | 141 | 2017-01-23 | c.case weld leak at hp suction | 2016-08-01 | 2017-01-23 | ZH | null | null | 5 | weld leak from c.case HP suction | null | null | null
2017-01-28 | null | null | D | RS Cold Storage | null | KC3 | 337K4341 | 196756 | null | null | 2017-01-23 | high oil consumption | 2014-12-30 | 2015-02-16 | PC | null | null | 2 | null | null | null | null
2017-02-10 | null | null | D | Vedant Ediable Product Pvt Ltd | null | KC93 | 348K142 | 196606 | null | 120 | 2017-01-16 | compressor has been breakdown due to thrust ring bronze broken in running condition . | 2016-06-21 | 2017-01-04 | PC | null | null | 6 | Thrust ring bronze broken | null | closed | Replace crankshaft,bearinhgs,piston,piston ring sets2
2017-02-13 | Acr Engg | null | D | Tanzania | null | KCX4 | 3384K1185 3384K1186 3384K1187 | Mail | null | null | null | after stopping the compressor for 12 days oil pressure is not developed | 2016-03-20 | null | PC | null | null | null | null | null | closed | null
2017-02-13 | Parag Marketing Services | null | D | Finolex Cables | null | KC6 | 339K3208 | 1872441849 | 2017-02-10 | 1196 | 2017-02-08 | high oil consumption | 2015-08-12 | 2015-09-09 | 3850 | null | null | 1 | piston ring set warnout | null | closed | replace piston ring set
2017-02-13 | Trade Links | Secunderabad | D | Kwality Animals Feeds PvtLtd | null | KCX4 | 3384K1054 | 1972481852 | 2017-02-10 | 1172 | 2016-11-29 | liner gasket damaged | 2015-10-28 | 2016-05-28 | 656 | null | null | 7 | liner gasket damaged,ring with hinge point damaged,sol. Valve leak | null | closed | replace liner,sol.valve
2017-02-13 | Parag Marketing Services | null | D | Ahura Ice And Cold Storage | Pune | KC3 | 337K4669 | 1972041845 | 2017-02-09 | 500 | 2017-02-02 | loading unloading problem. | 2016-08-09 | 2016-10-16 | 200 | null | null | 2 | Solenoid valve defective | null | closed | replace Sol. Valve
2017-02-13 | Parag Marketing Services | null | D | Pm Industries | null | KCX3 | 3374K899 | 1972081846 | 2017-02-09 | 1029 | 2017-01-16 | shaft seal leakage | 2015-06-10 | 2016-06-01 | 310 | null | null | 12 | leak from shaft seal and manifold. | null | closed | replace shaft seal assly and manifold
2017-02-24 | null | null | D | Amardeep Ice And Cold Storage | null | KC4 | 338K5286 | 197076 | null | null | 2017-02-01 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2015-11-20 | 2016-02-16 | PC | null | null | null | Change oil pump | null | closed | KC oil pump
2017-02-24 | Parag Marketing Services | null | D | M/SFrigorifico Allana Limited | null | KC9 | 340K363 | 197276 | null | 821 | null | loading unloading problem | 2016-03-26 | 2016-05-24 | PC | null | null | null | solenoid valve rubber seat problem | null | closed | null
2017-02-24 | Trade Links | Secunderabad | D | Lakshmi Cold Storage | null | KC3 | 337K4497 | 197418 | 2017-02-01 | null | null | loading unloading problem | 2016-02-16 | 2015-11-20 | PC | null | null | null | Trail run of compressor was taken & observed unloading problem for No. 1 & 2 Cylinders. Inspection of solenoid valves was done & found rubber swelling of the plunger. Excess rubber was removed & assembled back solenoid valves. Put back compressor in operation. Loading & unloading of cylinders found OK. Overall performance of compressor found satisfactory. | null | closed | null
2017-02-24 | null | null | D | Anekal Chilling Center | null | KCX4 | 3384K1179 | 197388 | 2017-02-13 | null | 2017-02-13 | shaft seal leakage | 2016-02-28 | 2016-10-25 | PC | null | null | null | Found more dirty particles inside the shaft seal. | null | closed | null
2017-02-24 | null | null | D | Devi Fisheries Ltd | null | KCX4 | 3384K1277 | 197416 | null | null | null | shaft seal leakage | 2016-09-19 | 2017-01-16 | PC | null | null | null | Observed shaft seal leakage. Inspection of the shaft seal was done. Shaft seal 'O' rings had damaged & shaft seal had worn out slightly. Shaft seal lapping was done. Changed 'O' rings & assembled back shaft seal assembly. Changed oil & paper filter. put back compressor in operation. Shaft seal leakage was not observed. Overall performance of compressor found satisfactory. | null | closed | Shaft seal 'O' rings
2017-02-28 | S M Refrigeration | null | D | Smc Foods Ltd | Uttar Pradesh | KC6 | 339K3311 | null | null | 6868 | 2016-12-29 | abnormal noise problem | 2016-03-26 | 2016-07-12 | 3678 | null | null | 7 | piston ring set damged , scratch marks in liner | null | closed | liner and piston ring set
2017-02-28 | Trade Links | Secunderabad | D | Freeze Exim | null | KC72 | 347K896 | null | null | 3145 | 2017-01-31 | abnormal noise problem | 2016-01-23 | 2016-05-05 | 2178 | null | null | 4 | Buffer sping shrunk | null | closed | buffer spring
2017-02-28 | Trade Links | Secunderabad | D | Al Badr Sea Foods | null | KC72 | 347K864 | null | null | 4683 | 2017-01-27 | no oil pressure | 2015-08-11 | 2017-01-12 | ZH | null | null | 5 | oil pump driving gear broken,scoring mark on cover plate | null | closed | oil pump
2017-02-28 | Trade Links | Secunderabad | D | Heritage Foods Ltd | null | KCX2 | 3364K1107 | null | null | null | 2017-01-26 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2016-07-13 | 2017-01-07 | ZH | null | null | 5 | Replace pressure gauge | null | closed | pressure gauge
2017-03-10 | Kalp Marketing | Gujrat | D | Dharti Cold Storage | Sabarkantha | KCX3 | 3374K1312 | 197940 | 2017-03-04 | null | 2017-02-22 | k5 valve leakage | 2017-02-15 | 2017-02-23 | ZH | null | null | 1 | K5 Valve leakage | null | closed | K5 valve
2017-03-10 | Trade Links | Secunderabad | D | Bherunath Ice Factory | null | KCX3 | 3374K1286 | 197962 | 2017-03-04 | null | 2017-02-21 | solenoid coil burnt | 2017-01-31 | 2017-02-23 | ZH | null | null | 1 | Sol. Valve coil burnt | null | closed | sol. Valve coil
2017-03-10 | Kalp Marketing | Gujrat | D | Umiya Cold Storage | null | KCX4 | 3384K1502 | 197958 | 2017-03-04 | null | 2017-02-23 | solenoid valve leakage | 2017-02-01 | 2017-02-25 | ZH | null | null | 1 | solenoid valve leakage | null | closed | K5 valve
2017-03-10 | Kalp Marketing | Gujrat | D | Jay Bhole Cold Staorage | null | KCX4 | 3384K1480 | 197966 | 2017-03-04 | null | 2017-02-24 | solenoid valve leakage | 2017-02-18 | 2017-02-24 | ZH | null | null | 1 | Leak from sol. Valve | null | closed | K5 valve and sol. Valve
2017-03-10 | Trade Links | Secunderabad | D | Kanakdurga Cold Storage | null | KC2 | 336K3358 | 197954 | 2017-03-04 | null | 2017-02-21 | stop valve leakage | 2016-10-14 | 2017-02-07 | ZH | null | null | 4 | Stop vlave leak from gland | null | closed | Bush
2017-03-14 | Morgan | null | E | Nooreka Cold Storage | null | KCX6 | 3394K680 | Mail | null | null | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | null | null | PC | null | null | null | KCX pump element broken | null | closed | pump element
2017-03-15 | null | null | D | Jai Hanuman Cold Storage | Bihar | KCX3 | 3374K1261 | 198276 | null | 727 | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2017-01-20 | 2017-02-26 | PC | null | null | 1 | KCX pump element broken | null | closed | pump element
2017-03-17 | null | null | D | Kk Ice Plant | null | KCX4 | 3384K1236 | 198372 | null | null | null | flywheel bolt loose | null | null | PC | null | null | null | Flywheel bolt loose | null | null | null
2017-03-17 | null | null | D | Periyar Ice Plant | null | KCX4 | 3384K1229 | 198488 | null | 509 | null | low oil pressure and liner cut mark | 2016-06-12 | 2016-06-23 | PC | null | null | 1 | Low oil pressure and liner cut mark | null | closed | liner and piston ring set
2017-03-27 | null | null | D | Bp Frozen Foods | null | KC42 | 344K1082 | 198256 | 2017-03-09 | 6887 | 2017-01-25 | abnormal noise | 2016-09-11 | 2017-01-04 | 146 | null | null | 3 | Piston ring sets damaged and scratch marks in liner | null | closed | liner and piston ring set
2017-03-27 | null | null | D | Chintu Ice | Turbhe | KCX6 | 3394K518 | 198950 | 2017-03-08 | 141 | null | abnormal noise | 2015-08-30 | 2016-05-02 | PC | null | null | 9 | Liner gaskets damaged | null | closed | null
2017-03-27 | null | null | D | Chintu Ice | Turbhe | KCX6 | 3394K514 | 198948 | 2017-03-01 | 109 | null | abnormal noise | 2015-08-30 | 2016-05-07 | PC | null | null | 9 | cut marks of liner 1,2,4,5 & Liner gaskets damaged | null | closed | liner and piston ring set
2017-03-27 | null | null | D | Jawahar Cold Storage | null | KC4 | 338K5505 | 198908 | 2017-03-21 | 5511 | 2017-03-16 | kc oil pump seize tang broken, housing , bushes ,gear wornout. | 2016-10-19 | null | PC | null | null | null | Replace gearkit | null | closed | Gerakit
2017-03-27 | null | null | D | Gurukrupa Cold Storage | null | KCX4 | 3384K1324 | 198528 | 2017-03-15 | null | 2017-03-01 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-11-11 | 2017-02-03 | 69 | null | null | 2 | Pump element tang broken. | null | closed | pump element
2017-03-27 | null | null | D | Debogram Agro | null | KCX4 | 3384K1292 | 198746 | 2017-03-18 | 648 | 2017-03-14 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-09-26 | 2017-03-03 | PC | null | null | 6 | Pump element tang broken. | null | closed | pump element
2017-03-27 | null | null | D | Chaudhary Dulare Singh CS | null | KCX4 | 3384K1511 | 189914 | 2017-03-21 | 5512 | 2017-03-17 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2017-02-22 | 2017-03-21 | PC | null | null | 1 | Pump element tang broken. | null | closed | pump element
2017-03-27 | null | null | D | Swami Atamanand Cold Storage | null | KCX4 | 3384K1356 | 198892 | 2017-03-13 | null | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-12-07 | 2017-01-04 | PC | null | null | 1 | Pump element tang broken. | null | closed | pump element
2017-03-27 | null | null | D | Ashok Raj Preserve Cold Storage P Ltd | Bihar | KCX4 | 3384K1321 | 198204 | null | 605 | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-11-09 | 2017-02-17 | PC | null | null | 3 | Outer rotor tang broken | null | closed | pump element
2017-03-27 | null | null | D | KPCold Storage | null | KCX4 | 3384K1222 | 198282 | null | 726 | null | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2017-01-20 | 2017-02-26 | PC | null | null | null | Pump element tang broken. | null | closed | pump element
2017-03-27 | null | null | D | Kollegala Chilling | null | KCX2 | 3364K1223 | 198010 | 2017-03-04 | null | null | op cutout not working | 2017-02-06 | 2017-02-16 | ZH | null | null | 1 | Op cutout not working | null | closed | OP cutout
2017-03-27 | null | null | D | Debogram Agro | null | KCX6 | 3394K644 | 189984 | 2017-03-23 | 649 | 2017-03-14 | shaft seal leakage | 2016-09-27 | 2017-03-03 | 90 | null | null | 5 | Shaft seal leakage | null | closed | shaft seal aasly
2017-03-27 | Trade Links | Secunderabad | D | Sai Radha Krishna Cold Strorage | null | KC3 | 337K4578 | 198192 | 2017-03-06 | null | null | shaft seal leakage | 2017-01-10 | 2017-03-05 | PC | null | null | null | Shaft seal leakage | null | closed | Shaft seal assly
2017-03-27 | Kalp Marketing | Gujrat | D | Jay Vadvala Cold Storage | null | KCX4 | 3384K1428 | 198752 | 2017-03-05 | null | null | shaft seal leakage | 2016-02-24 | 2016-05-07 | PC | null | null | 3 | Shaft seal leakage | null | closed | Shaft seal assly
2017-03-27 | null | null | D | Mandya Milk DistCoOp Milk Prod'S Societies Union Ltd | Mandya Dist | KCX6 | 3394K591 | 197902 | null | null | null | shaft seal leakage | 2016-05-28 | 2016-07-02 | PC | null | null | 2 | shaft seal leakage | null | closed | Shaft seal assly
2017-03-27 | Kalp Marketing | Gujrat | D | Shivdhara Cold Strorage | null | KCX4 | 3384K1437 | 198382 | 2017-03-03 | null | null | solenoid valve leakage | 2017-01-16 | 2017-02-16 | PC | null | null | 1 | Leak from sol. Valve | null | closed | Sol.valve
2017-03-30 | null | null | D | Nagendra Singh Raja Bhaiya Cold Storage | null | KC4 | 338K5309 | 198314 | 2017-03-09 | 5471 | 2017-01-05 | abnormal noise | 2015-10-28 | 2016-03-07 | 1770 | null | null | 4 | Piston ring set worn out | null | closed | piston ring set
2017-03-30 | null | null | D | Sterling Agro | null | KCX21 | 3424K013 | 197844 | 2017-03-02 | 39 | 2016-11-02 | hp side safety valve leak | 2016-05-09 | 2016-09-21 | 60 | null | null | 4 | HP side safety valve leak | null | closed | valve guide and teflon
2017-03-30 | Cool Comfort Private Limited | West Bengal | D | Kp Cold Storage | null | KCX4 | 3384K1222 | 198356 | 2017-03-10 | 630 | 2017-03-01 | leak from kcx manifold and hair crack on kcx oil pump housing and cover | 2016-05-17 | 2017-02-26 | 7 | null | null | 9 | Leak from KCX manifold and hair crack on KCX pump housing and cover | null | closed | manifold and KCX oil pump
2017-03-30 | null | null | D | Hari Om Gram Udyog | null | KCX2 | 3364K1006 | 198308 | 2017-03-09 | 5465 | 2016-12-03 | loading & unloading problem. | 2016-02-08 | 2016-03-15 | 3338 | null | null | 1 | Sol. Valve coil not working | null | closed | Sol. Valve coil
2017-03-30 | Trade Links | Secunderabad | D | Ananda Aqua Exports | null | KC51 | 345K980 | 198800 | 2017-03-20 | null | 2017-03-13 | shaft seal leakage | 2016-03-26 | 2016-04-14 | 4560 | null | null | 1 | Shaft seal leak | null | closed | shaft seal aasly
2017-03-30 | null | null | D | Fouress Foods | null | KC51 | 345K981 | 198718 | 2017-03-18 | null | 2017-03-13 | shaft seal leakage | 2016-03-31 | 2016-10-10 | 738 | null | null | 7 | Scratches on shaft seal seat face | null | closed | shaft seal assly
2017-03-30 | null | null | D | Mvsd Foods | null | KCX3 | 3374K1105 | 198270 | 2017-03-10 | 6900 | 2017-02-08 | shaft seal leakage | 2016-07-08 | 2017-01-11 | PC | null | null | 4 | Shaft seal leak | null | closed | shaft seal assly
2017-04-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Alpha Marine | Andhra Pradesh | KC72 | 347K901 | 1996022001 | 2017-04-18 | null | 2017-04-02 | abnormal noise | 2016-02-09 | 2016-06-09 | 860 | null | null | 4 | Abnormal sound from cyl 4 , Piston seized due to overheating. Delivery valve backleaking resulted into overheating of cylinder and damaged. | null | closed | Piston , Piston ring set, liner , Disch valve , Gudgeon pin and bearings replaced.
2017-04-19 | Trade Links | Secunderabad | D | Chappid Hanumanth Rao Cold Storage | Andhra Pradesh | KC3 | 337K4589 | 199592199 | 2017-04-17 | null | 2017-03-26 | kc pump lubrication pressure not develop. | 2016-02-29 | 2016-05-20 | 1836(03) | null | null | 3 | Oil pressure not develop - Oil filters , Pump components found ok but pressure not develop hence after taking clearance from KPCL-Hyderabad interchanged oil pump assly and found ok. | null | closed | Oil pump assembly replaced.
2017-04-19 | Fridge House | null | D | Heritage Foods Ltd | Karnataka | KCX4 | 3384K1263 | 1996741984 | 2017-04-12 | null | 2017-04-10 | kcx oil pump seize tang broken, inner,outer and housing wornout.(element broken) | 2016-08-24 | 2017-03-22 | 28(03) | null | null | 7 | Tang broken , Driving gear jammed and dowel pin broken. | null | closed | Pump Element replaced
2017-04-19 | S M Refrigeration | null | D | Shree Ganesh Cold Storage | null | KC4 | 338K5605 | 1997961994 | 2017-04-15 | 71 | 2017-04-14 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2017-03-09 | null | ZH | null | null | 1 | Suction pressure gauge not working | null | closed | Suction pr gauge
2017-04-19 | Trade Links | Secunderabad | D | Aquatic Frozen Foods Global Private Ltd | Andhra Pradesh | KCX72 | 3474K058 | 1991481996 | 2017-04-17 | null | 2017-03-13 | solenoid valve 1/8 bsp thrd damaged | 2017-01-30 | 2017-03-17 | ZH | null | null | 2 | Oil leakage from extended feamale adaptor NO solenoid valve . Threading of solenoid valve and adaptor was damaged. | null | closed | NO Solenoid valve and Adaptor
2017-04-23 | S M Refrigeration | null | D | Jai Maa Durga Cold Storage | null | KC4 | 338K5409 | 1993421973 | 2017-04-03 | 5505 | 2017-03-04 | abnormal noise from compressor | 2016-02-10 | 2016-05-07 | 823 | null | null | 3 | open castle nut in delivery valve assly and broken piston | null | closed | replace piston,piston ring set,del.valve assly.
2017-04-23 | Trade Links | Secunderabad | D | India Sea Foods | null | KCX42 | 3444K004 | 1992741970 | 2017-04-01 | 4008 | 2017-03-29 | high oil carryover | 2015-06-28 | 2016-07-30 | 1579 | null | null | 13 | excessive gap in piston rings | null | closed | replace piston rings
2017-04-23 | Kalp Marketing | Gujrat | D | Usmani Ice Factory | null | KCX4 | 3384K1338 | 1993621975 | 2017-04-04 | null | 2017-04-03 | orv leak | 2016-11-23 | 2017-04-03 | ZH | null | null | 4 | Problem in ORV | null | closed | ORV 4nos.
2017-04-29 | Trade Links | Secunderabad | D | Aquatic Frozen Foods Global Private Ltd | Andhra Pradesh | KCX72 | 3474K058 | 2000202008 | 2017-04-24 | 384 | 2017-04-18 | crankshaft failure | 2017-01-30 | 2017-03-17 | PC | null | null | 2 | Crank shaft assembly wornout , HP Cylinder piston seized also all bearings wornout due to LP oil pump pressure not developed. | null | closed | Replaced Crankshaft , Oil pump , HP Piston and piston ring sets , All bearings etc.
2017-04-29 | Trade Links | Secunderabad | D | Aquatic Frozen Foods Global Private Ltd | Andhra Pradesh | KCX72 | 3474K058 | 2000202008 | 2017-04-24 | 384 | 2017-04-18 | crankshaft failure | 2017-01-30 | 2017-03-17 | PC | null | null | 2 | Crank shaft assembly wornout , HP Cylinder piston seized also all bearings wornout due to LP oil pump pressure not developed. | null | closed | Replaced Crankshaft , Oil pump , HP Piston and piston ring sets , All bearings etc.
2017-04-29 | Kalp Marketing | Gujrat | D | Usmani Ice Factory | Gujrat | KCX4 | 3384K1335 | 1993741977 | 2017-04-05 | null | 2017-04-02 | high oil consumption | 2016-11-22 | 2017-03-09 | 450(03) | null | null | 4 | Open VLD Piston , changed Orings ,Pistons & ORV | null | closed | Replaced Orings ,Pistons & ORV
2017-04-29 | Kalp Marketing | Gujrat | D | Shital Ice FactoryJamnagar | Gujrat | KCX3 | 3374K1198 | 1998822003 | 2017-04-19 | null | 2017-04-13 | knocking sound & overheating | 2016-12-09 | 2017-01-19 | 2000 | null | null | 1 | Observed direct piston seized and broken so replaced piston and cylinder liner , also liner gasket was damaged . | null | closed | Replaced new gasket , Piston , Buffer spring , Safety valve spring and teflon , Gudgeon pin .
2017-04-29 | S M Refrigeration | null | D | Jawahar Cold Storage & Baraf Factory | Gujrat | KC4 | 338K5505 | 1998862004 | 2017-04-19 | 55215522 | 2017-04-30 | oil pressure not buildup | 2016-10-19 | 2017-02-25 | 193 | null | null | 4 | Oil pressure not builtup | null | closed | Replaced oil pump assembly
2017-04-29 | S M Refrigeration | null | D | M/S Kiran Agro | Haryana | KCX4 | 3384K1433 | 1998102007 | 2017-04-24 | 6970 | 2017-04-07 | oil pressure not buildup | 2017-01-15 | 2017-03-24 | 88(03) | null | null | 2 | Oil pressure not developed due to pump element broken | null | closed | Replaced pump element
2017-04-29 | S M Refrigeration | null | D | Ashok Raj Preserve Cold Storage P Ltd | Bihar | KCX4 | 3384K1321 | 1996201982 | 2017-04-10 | 623 | 2017-04-08 | oil seal leak & excessive sound | 2016-12-09 | 2017-02-17 | 600 | null | null | 2 | Attend the compressor while change the oil seal assly. Found that white metal partical inside the compressor . So dismentled the main bearings and found damage. | null | closed | Replaced Crankshaft , All bearings, Shaft seal & Pump element.
2017-04-29 | Kalp Marketing | Gujrat | D | Dev Shakti Ice & Milk Plant | Madhya Pradesh | KCX2 | 3364K1273 | 2001242021 | 2017-04-26 | null | 2017-04-23 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2017-03-21 | 2017-04-24 | PC | null | null | 1 | Discharge pressure gauge not properly working | null | closed | Discharge pressure gauge replaced
2017-04-29 | Kalp Marketing | Gujrat | D | Jay Vadvala Cold Storage | Gujrat | KCX4 | 3384K1428 | 1987521979 | 2017-04-05 | null | 2017-03-05 | shaft seal leakage | 2017-01-10 | 2017-03-05 | ZH | null | null | 2 | Shaft seal leak dt.27/02/2017 , replaced o ring after 5/3/2017 replaced with new seal and found ok. | null | closed | Replaced shaft seal assembly
2017-04-29 | S M Refrigeration | null | D | Larsen & Toubro | Tamil Nadu | KC72 | 347K932 | 2000522014 | 2017-04-25 | null | 2017-04-21 | solenoid valve coil not working | 2016-05-18 | 2016-11-23 | 595 | null | null | 6 | 2 nos coil not working , replaced new coil then one observed oil leakage , hence replaced solenoid valve assly. | null | closed | Replaced coil and Valve
2017-04-29 | Kalp Marketing | Gujrat | D | Bileshwar Cold Storage Pvt Ltd | Gujrat | KCX3 | 3374K1232 | 2000242013 | 2017-04-25 | null | 2017-04-20 | unloading problem | 2017-01-03 | 2017-02-10 | 1248 | null | null | 1 | Unloading problem replaced SV and found ok. | null | closed | Received old type valve ?
2017-05-12 | S M Refrigeration | null | D | Shanti Sheetgrah Pvt Ltd | Uttar Pradesh | KCX72 | 3474K047 | 2003402043 | 2017-05-02 | 684 | 2017-04-25 | abnormal noise | 2017-01-02 | 2017-04-26 | ZH | null | null | 3 | During Commissioning found abnormal sound from cylinder no. 6 due to heavy rusty. | null | closed | Delivery valve
2017-05-12 | Gargi Engineering Enterprices Pvt Ltd | null | D | United Breweries Ltd | Taloja, Mh | KCX9 | 3404K027 | 2004062049 | 2017-05-05 | 118 | 2017-05-03 | abnormal noise & oil carry over | 2016-01-27 | 2016-05-23 | 4837 | null | null | 4 | All 8 piston are touching to DV . One buffer spring lenght short resut to damage of liner, Pison , DV. | null | closed | Replaced Piston ring set9 , Piston 1, DV1,Buffer spring 1, Gasket & Oring set
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | India Dairy Products Ltd | West Bengal | KCX6 | 3394K678 | 2004762052 | 2017-05-06 | 752 | 2017-05-02 | abnormal noise & oil carry over | 2016-12-11 | 2017-04-20 | 150(03) | null | null | 4 | Abnormal sound and excessive oil consumption . | null | closed | Replaced Piston 02 no. , Ring set 04 nos, Liner 02 no Gudgeon pin1 no.
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Padmashree Export | null | KCX72 | 3474K002 | 2005182053 | 2017-05-08 | 708 | 2017-05-01 | abnormal noise & oil carry over | 2015-09-08 | 2016-03-15 | 3105 | null | null | 6 | Excessive gap between liner and piston, Also damage in gudgeon pin & Bush, Piston ring wornout. | null | closed | Replaced Piston ring set, Piston , Gudgeon pin , Bush
2017-05-12 | Kalp Marketing | Gujrat | D | Gurudev Cold Storage | Gujrat | KCX4 | 3384K1380 | 2004682054 | 2017-05-09 | null | 2017-05-02 | high oil consumption | 2016-12-16 | 2017-02-14 | 285 | null | null | 2 | NRV Defective. | null | closed | Replaced all 4 NRV
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Reliable Cold Storage | Assam | KCX3 | 3374K1366 | 2006082057 | 2017-05-10 | 782 | 2017-05-08 | kcx oil pressure not develop | 2017-03-07 | 2017-05-06 | 49(03) | null | null | 2 | Driven gear seized with cover plate bush and hence tang broken. | null | closed | Replaced pump elemnt
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Radha Damodar Multipurpose Cold Storage | West Bengal | KCX6 | 3394K738 | 2003682045 | 2017-05-03 | 777 | 2017-05-01 | kcx oil pressure not develop | 2017-02-08 | 2017-03-15 | 330(03) | null | null | 1 | Pump element broken | null | closed | Pump element replaced.
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Celebrity Breweries | West Bengal | KCX4 | 3384K1052 | 2003382044 | 2017-05-02 | 592 | 2017-04-27 | kcx oil pressure not develop | 2016-10-21 | 2016-12-08 | 1440 | null | null | 2 | Pump element broken | null | closed | Pump element replaced.
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Jai Hanuman Cold Storage | Bihar | KCX3 | 3374K1261 | 2006102059 | 2017-05-10 | 731 | 2017-03-31 | kcx oil pressure not develop | 2017-01-20 | 2017-02-26 | 220 | null | null | 1 | Drive gear seized with bush and tang broken | null | closed | Pump element replaced.
2017-05-12 | Cool Comfort Private Limited | West Bengal | D | Ganga Dairy Cold Storage | Bihar | KCX6 | 3394K562 | 2004622051 | 2017-05-06 | 730 | 2017-03-31 | kcx oil pressure not develop | 2017-02-05 | 2017-03-09 | 228(03) | null | null | 1 | Drive gear seized with bush and tang broken | null | closed | Pump element replaced.
2017-05-12 | Parag Marketing Services | null | D | Ahura Ice And Cold Storage | Pune | KC3 | 337K4669 | 2003882047 | 2017-05-04 | 1140 | 2017-03-29 | loading / unloading problem | 2016-08-09 | 2016-10-16 | 813 | null | null | 2 | Cylinder no.2 not getting unload due to solenoid valve malfunctioning. | null | closed | Replaced solenoid valve assembly 01 no.
2017-05-14 | Kalp Marketing | Gujrat | D | Swagat Cold Storage | Gujrat | KCX4 | 3384K1489 | 2004662055 | 2017-05-10 | null | 2017-05-01 | cylinder overheating | 2017-02-08 | 2017-02-19 | 493 | null | null | 1 | Damage in cylinder buffer spring , Piston , Piston ring set , DV Sring set. | null | closed | Replaced Buffer spring & Valve rings.
2017-05-14 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kamla Cold Storage | Gujrat | KCX4 | 3384K1568 | 2006122058 | 2017-05-10 | 55 | 2017-04-01 | kcx oil pressure not develop | 2017-03-24 | 2017-05-10 | ZH | null | null | 2 | No observations mentioned in FRR & FSR | null | closed | Replaced pump elemnt
2017-05-14 | Cool Comfort Private Limited | West Bengal | D | Sarba Mangala Agro Products | null | KCX4 | 3384K1497 | 2011022075 | 2017-05-23 | 201102 | 2017-05-23 | shaft seal leakage | 2017-02-13 | 2017-03-18 | 931 | null | null | null | Oil seal stationary sealing ring face damage. | null | closed | Shaft seal assly
2017-05-29 | Trade Links | Secunderabad | D | Frigerio Conserva Allana Ltd | Telangana | KC6 | 339K3297 | 2008342068 | 2017-05-18 | null | 2017-05-07 | abnormal vibrations | 2016-02-22 | 2016-05-15 | 6330 | null | null | 3 | Cylinder liner wearing due to improper lubrication. Cylinder no. 1,3,4 & 6 had worn-out and all gudgeon pins & bushes wornout. | null | closed | Replaced Cylinder liner , Piston ring sets, Gudgeon pins and bushes.
2017-05-29 | Cool Comfort Private Limited | West Bengal | D | Ashok Raj Preserve Cold Storage P Ltd | Bihar | KCX3 | 3374K1158 | 2007142061 | 2017-05-12 | 619 | 2017-04-04 | kcx oil pressure not develop | 2016-11-09 | 2017-02-17 | 400(03) | null | null | 3 | Driven gear tang is broken due to driven gear bush seized with cover plate | null | closed | Pump element
2017-05-29 | Trade Links | Secunderabad | D | Jaya Laxmi Ice & Cold Storage | Andhra Pradesh | KCX3 | 3374K1331 | 2008262070 | 2017-05-18 | null | 2017-05-09 | loading / unloading problem | 2017-02-24 | 2017-03-14 | 1110(03) | null | null | 1 | Solenoid valve malfunctioning , Also OPR problem | null | closed | Solenoid valve
2017-05-29 | Trade Links | Secunderabad | D | Sristi Fish International | Andhra Pradesh | KCX6 | 3394K655 | 2008282069 | 2017-05-18 | null | 2017-05-11 | oil charging probleem/suction manifold threading damaged | 2016-10-22 | 2017-03-15 | 1159 | null | null | 5 | Manifold threading damaged | null | closed | Replaced manifold
2017-05-29 | Kalp Marketing | Gujrat | D | Shrinath Agro Care | Madhya Pradesh | KCX4 | 3384K1570 | 2011342078 | 2017-05-24 | null | 2017-05-19 | pressure gauges (suc./disch./oil) not working/malfunctioning | 2017-03-26 | 2017-05-20 | ZH | null | null | 2 | Pressure gauge not working properly | null | closed | Replaced Pressure gauges 01602 & 02501 no.
2017-05-29 | Kalp Marketing | Gujrat | D | Prayosha Cold Storage | Gujrat | KCX3 | 3374K972 | 2012162017 | 2017-05-26 | null | 2017-05-21 | shaft seal leakage | 2015-12-07 | 2016-02-18 | 1294 | null | null | 2 | Leakage due to rotory seal wornout | null | closed | Replaced shaft seal assly
2017-05-29 | Kalp Marketing | Gujrat | D | Mother Agro Cold Storage | Gujrat | KCX3 | 3374K937 | 2012122086 | 2017-05-26 | null | 2017-05-12 | shaft seal leakage | 2015-10-13 | 2015-11-18 | 4021 | null | null | 1 | Shaftseal Oring wornout , Replaced Orings and Lapping done. | null | closed | Replaced Orings
2017-05-29 | Kalp Marketing | Gujrat | D | Mother Agro Cold Storage | Gujrat | KCX3 | 3374K937 | 2011642080 | 2017-05-25 | null | 2017-04-16 | shaft seal leakage | 2015-10-13 | 2015-11-18 | 3922 | null | null | 1 | Shaftseal Oring wornout , Replaced Orings and Lapping done. | null | closed | Replaced Orings
2017-06-17 | Geekay Pneumatic Pvt Ltd | null | D | Al Madeena Ice Plant | null | KCX3 | 3374K1091 | 2020782120 | 2017-06-07 | 4901 | 2017-05-29 | abnormal noise suction over heat and oil carry over | 2016-05-29 | 2016-09-17 | 971 | null | null | 5 | Damaged the liner gasket and due to that the compressor suction overheat. Also oil throw at all 3 pistons. | null | closed | Replaced Set piston ring 3 Nos.
2017-06-17 | Fridge House | null | D | Mandya Milk DistCoOp Milk Prod'S Societies Union Ltd | Mandya Dist | KCX6 | 3394K591 | 2020102118 | 2017-06-07 | null | 2017-06-03 | compressor knocking sound | 2016-05-28 | 2016-07-02 | 6314 | null | null | 3 | Knocking sound in cyl 4 , suction valve ring broken . | null | closed | Replaced valve spring , ring , piston , cylinder liner & set ring.
2017-06-17 | Cool Comfort Private Limited | West Bengal | D | M/S Falcon Marine Export | Odisha | KCX3 | 3374K1343 | 2019862116 | 2017-06-06 | 803 | 2017-05-20 | high oil consumption and abnormal sound. | 2017-02-27 | 2017-05-04 | 272(03) | null | null | 4 | Cylinder liner , Gudgeon pin & Bush damaged condition. - for 1 cylinder | null | closed | Replaced Cylinder liner , Piston , Ring set , Gudgeon pin & Bush connecting rod.
2017-06-17 | Kalp Marketing | Gujrat | D | Khyati Chemicals Pvt Ltd | null | KCX6 | 3394K668 | 2020542115 | 2017-06-06 | null | 2017-06-05 | knocking sound in cylinder no. 01,03,04 & 06. | 2016-11-26 | 2017-05-02 | 622(03) | null | null | 7 | Knocking sound in cylinder no 1,3,4&6 due to liner gasket damaged , One liner , piston & ring set & delivery valve damaged | null | closed | Replaced liner , piston & ring set & delivery valve .
2017-06-17 | Geekay Pneumatic Pvt Ltd | null | D | Grand Marine Foods | null | KCX72 | 3474K018 | 2020942122 | 2017-06-07 | 4982 | 2017-05-30 | oil pressure dp trip | 2016-07-27 | 2016-08-19 | 1042 | null | null | 1 | Journal Brgs, Intermediate brg, main bearing & Crankshaft wornout | null | closed | Replaced crankshaft
2017-06-17 | Kirloskar Pneumatic Co Ltd | null | D | Sangha Cold Storage & Ice Factory | null | KCX4 | 3384K1553 | 2022822136 | 2017-06-14 | 201 | 2017-06-06 | oil pressure not buildup | 2017-03-14 | 2017-05-08 | 539(03) | null | null | 3 | Oil pressure not develop | null | closed | Replaced oil pump assembly.
2017-06-17 | Cool Comfort Private Limited | West Bengal | D | Reliable Cold Storage (P) Ltd | null | KCX3 | 3374K1366 | 2019822109 | 2017-06-05 | 689 | 2017-05-23 | oil pressure not buildup | 2017-03-07 | 2017-05-06 | 180 | null | null | 3 | Driven gear seized with cover plate bush and hence tang broken. | null | closed | Replaced pump elemnt
2017-06-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX4 | 3384K1267 | 2018602111 | 2017-06-06 | 96 | 2017-04-27 | piston touches to delivery valve | 2016-08-27 | 2017-04-28 | PC(03) | null | null | 8 | Compressed liner gasket & impression on delivery valve for 01 cylinder. | null | closed | Replaced Buffer spring , piston , set ring piston, Bearings , thrust ring & Pressure gauge found blackish.
2017-06-17 | Cool Comfort Private Limited | West Bengal | D | Maa Biraja Cold Storage (P) Ltd | null | KCX2 | 3364K1047 | 2019542108 | 2017-06-02 | 809 | 2017-05-28 | pump inner rotor missing | 2016-03-25 | 2017-05-30 | ZH | null | null | 14 | Pump inner rotor missing | null | closed | null
2017-06-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | New Khurshid Ice Factory | Gujrat | KCX3 | 3374K1122 | 2020402113 | 2017-06-06 | 65 | 2017-05-09 | shaft seal leakage | 2016-09-16 | 2016-12-12 | 250 | null | null | 4 | Scrap found on shaft seal , lapping done but leakage cont. | null | closed | Replaced shaft seal
2017-06-17 | Kalp Marketing | Gujrat | D | Shree Krishna Cold Storage | Madhya Pradesh | KC3 | 337K4689 | 2000842135 | 2017-06-13 | null | 2017-03-31 | stop valve not working | 2016-11-12 | 2017-04-01 | PC | null | null | 5 | Tal 50 valve not properly working. | null | closed | Replaced TAL50
2017-06-27 | Trade Links | Secunderabad | D | Maharastra Hybrid Seeds Co Ltd | Telangana | KC3 | 337K4653 | 2021382139 | 2017-06-16 | null | 2017-06-07 | loading / unloading problem | 2016-06-10 | 2016-12-22 | 845 | null | null | 7 | Unloading problem to cyl no.1 , open delivery valve and observed plunger neorrene seat swelled excessively and spring tention also increase. | null | closed | Replaced solenoid valve assly
2017-06-27 | Trade Links | Secunderabad | D | Gopika Ice Factory | Andhra Pradesh | KCX4 | 3384K1605 | 2020382112 | 2017-06-06 | null | 2017-06-03 | low oil pressure | 2017-05-07 | 2017-06-05 | ZH | null | null | 1 | After running compressor for 4 hrs observed loading/unloading problem due to low oil pressure , checked element & regulator found ok but oil pressure not improved hence suggested by KPCL Hyd office , replaced oil pump. | null | closed | Replaced oil pump assly (LC 03 17 1324)
2017-06-27 | S M Refrigeration | null | D | Pankhuri Chilling & Ice Plant | Uttar Pradesh | KCX4 | 3384K1256 | 2024822145 | 2017-06-22 | 3054 | 2017-04-26 | oil pressure not buildup | 2016-07-29 | 2016-08-30 | 139 | null | null | 1 | Found oil pressure not builtup due to broken oil pump element. | null | closed | Replaced oil pump element.
2017-06-30 | Trade Links | Secunderabad | D | Grand Cold Storage | Telangana | KCX2 | 3364K1296 | 2020322119 | 2017-06-07 | null | 2017-06-01 | fitting lekage | 2017-04-16 | 2017-06-03 | PC | null | null | 2 | Obsrerved leakage from discharge pressure gauge due to gauge adaptor threading damaged. Fitting leakage | null | closed | Obsrerved leakage from discharge pressure gauge due to gauge adaptor threading damaged. Fitting leakage
2017-06-30 | Kalp Marketing | Gujrat | D | Tulsi Cold Storage | Gujrat | KCX3 | 3374K1393 | 2019162138 | 2017-06-15 | null | 2017-05-28 | hour meter not working | 2017-03-27 | 2017-05-29 | PC | null | null | 2 | Hour meter not working | null | closed | Replaced Hour meter
2017-06-30 | Kalp Marketing | Gujrat | D | Sarvottam Dairy Shree Bhavnagar | Gujrat | KCX6 | 3394K622 | 2019222107 | 2017-06-01 | null | 2017-05-30 | k5 valve leakage | 2016-08-01 | 2017-05-19 | PC | null | null | 10 | K5 Valve leakage | null | closed | Replaced K5 Valve 03 nos.
2017-06-30 | Kalp Marketing | Gujrat | D | Dharti Cold Storage | Gujrat | KCX4 | 3384K1475 | 2021662131 | 2010-06-10 | null | 2017-06-06 | k5 valve leakage | 2017-01-31 | 2017-02-23 | 768 | null | null | 1 | K5 Valve leakage from gland , retighten but leakage not stop. | null | closed | Replaced K5 Valve 02 nos.
2017-06-30 | Morgan | null | E | Ali Cold Storage | Pakistan | KC4 | 338K5487 | email | null | null | 2017-04-16 | kc oil pressure low | 2016-09-30 | 2017-04-10 | PC | null | null | 4 | oil pressure not develops | null | closed | KC oil pump
2017-06-30 | Morgan | null | E | Arif Sadrr Ice Plant | Pakistan | KC6 | 339K3395 | email | null | null | 2017-04-16 | kc oil pressure low | 2017-01-26 | 2017-04-12 | 48 | null | null | 3 | oil pressure low only 1.0 kg/cm2 | null | closed | KC oil pump
2017-06-30 | Morgan | null | E | Bag-O | Bihar | KC4 | 338K5486 | null | null | null | null | solenoid valve not working | 2016-09-01 | 2017-02-03 | 1417 | null | null | 5 | Solenoid valve not working | null | closed | Replaced sol valve
2017-06-30 | Morgan | null | E | Wassem FarooqIce Factory | null | KC6 | 339K3388 | email | null | null | 2017-04-20 | stop valve leakage | 2017-01-25 | 2017-04-07 | PC | null | null | 2 | Leakage in discharge stop valve | null | closed | Stop valve
2017-06-30 | Morgan | null | E | Ikram Ilha Ice Plant | Pakistan | KC6 | 339K3324 | email | null | null | 2017-04-20 | stop valve leakage | 2016-05-20 | 2016-06-30 | PC | null | null | 1 | Stop valve leak | null | closed | Stop valve
2017-07-17 | Trade Links | Secunderabad | D | Sri Vaishnavi | Andhra Pradesh | KCX6 | 3394K743 | 202928 | 2017-07-01 | 352 | 2017-07-26 | abnormal noise | 2017-02-13 | 2017-07-28 | PC(03) | null | null | 5 | Wearing of 02 cylinders due to insufficient lubrication | null | closed | Replaced Piston , liner and piston ring sets
2017-07-17 | Trade Links | Secunderabad | D | Anitha Dairy Products | null | KCX4 | 3384K1295 | 202934 | 2017-07-01 | 7 | 2017-07-29 | abnormal noise | 2016-09-30 | 2016-11-18 | 124 | null | null | 1 | piston rings and liner wearout | null | closed | liner and pistonring sets
2017-07-17 | S M Refrigeration | null | D | K A Cold Storage | Uttar Pradesh | KC4 | 338K5497 | 202956 | 2017-07-11 | 5563 | 2017-06-22 | abnormal noise from compressor | 2016-10-08 | 2017-03-07 | 729 | null | null | 4 | Piston ring wearout | null | closed | Piston ring set
2017-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Tulsi Cold Storage | Gujrat | KCX3 | 3374K1394 | 202760 | 2017-06-28 | 472 | 2017-06-21 | delivery valve leakage | 2017-03-27 | 2017-05-29 | 130(03) | null | null | 2 | Replaced Delivery valve ring springs | null | closed | Replaced Delivery valve ring springs
2017-07-17 | Parag Marketing Services | null | D | Paliwal Milk Products | Rajastan | KCX1 | 3354K027 | 202734 | 2017-06-28 | 1 | 2017-06-26 | high oil consumption | 2017-04-19 | 2017-05-21 | 590(03) | null | null | 1 | oil throw | null | closed | Piston ring set
2017-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Dauji Ice Plant | Goa | KCX3 | 3374K1101 | 202668 | 2017-06-27 | 53 | 2017-03-10 | high oil consumption | 2016-06-30 | 2016-07-30 | 28597 | null | null | 1 | Replaced ORV -3nos. | null | closed | ORV3nos.
2017-07-17 | Kalp Marketing | Gujrat | D | Sarhad Dairy | Gujrat | KCX3 | 3374K1337 | 200788 | 2017-06-30 | null | 2017-05-14 | k5 valve leakage | 2017-02-25 | 2017-05-15 | ZH | null | null | 2 | leak from k5 valve gland | null | closed | K5 Valve
2017-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Tasty Bites | Solapur | KCX4 | 3384K1563 | 203378 | 2017-07-17 | 1 | 2017-07-13 | knocking / abnormal sound | 2017-03-18 | 2017-07-07 | PC(03) | null | null | 4 | crankpin no2 wearout | null | closed | Crank shaft,piston,piston ring set, valve kit.
2017-07-17 | Kalp Marketing | Gujrat | D | Kamdhenu Cold Storage | null | KCX4 | 3384K1488 | 202728 | 2017-06-28 | 25 | 2017-06-26 | knocking / abnormal sound | 2017-02-07 | 2017-02-25 | 985 | null | null | 1 | piston and liner siezed, liner gasket damaged | null | closed | Piston,liner piston ring set
2017-07-17 | Trade Links | Secunderabad | D | Grren House Agro Products | null | KC72 | 347K871 | 202932 | 2017-07-01 | 30 | 2017-07-21 | oil pressure not buildup | 2015-09-21 | 2016-08-21 | 2665 | null | null | 1 | Driving gear tang broken | null | closed | Gear kit
2017-07-17 | Kalp Marketing | Gujrat | D | Navdurga Ice Factory | Gujrat | KCX4 | 3384K1298 | 202724 | 2017-06-28 | 573 | 2017-06-24 | op cutout not working | 2016-10-07 | 2017-04-08 | 1817(03) | null | null | 5 | Replace OP cutout | null | closed | OP cutout
2017-07-17 | Kalp Marketing | Gujrat | D | Navrang Ice Factory | null | KCX3 | 3374K1385 | 202926 | 2017-07-08 | 74 | 2017-05-14 | pressure gauge not working | 2017-03-25 | 2017-05-18 | ZH | null | null | 1 | Replaced pressure gauge | null | closed | Pressure gauge
2017-07-17 | S M Refrigeration | null | D | Santosh Bhunesh Cold Strorage | Uttar Pradesh | KC6 | 339K3362 | 202748 | 2017-06-28 | 8314 | 2017-03-05 | solenoid valve not working | 2016-12-10 | 2017-03-08 | 4 | null | null | 2 | Solenoid valve coil burn | null | closed | Sol. Valve
2017-08-08 | Gargi Engineering Enterprices Pvt Ltd | Baroda | D | Deepak Nitrile Limited | Gujrat | KCX9 | 3404K042 | 2038222226 | 2017-08-01 | 99 | 2017-07-01 | low oil pressure | 2016-12-17 | 2017-07-02 | ZH | null | null | 7 | Low oil pressure within 2 Hrs. | null | closed | Replaced oil pump element
2017-08-08 | S M Refrigeration | null | D | Shri Sai Cold Storage | Uttar Pradesh | KCX6 | 3394K748 | 2038382230 | 2017-08-02 | 8355 | 2017-06-29 | oil pressure not buildup | 2017-02-18 | 2017-03-05 | 1375 | null | null | 1 | Oil pressure not builtup due to oil pump element not working. | null | closed | Replaced oil pump element
2017-08-08 | S M Refrigeration | null | D | Surbhi Cold Storage | Uttar Pradesh | KCX2 | 3364K1176 | 203788/2227 | 2017-08-01 | 5575 | 2017-07-25 | oil pressure not buildup | 2016-12-12 | 2017-01-21 | 3291 | null | null | 1 | Oil pressure not builtup | null | closed | Replaced oil pump element
2017-08-20 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KC21 | 342K899 | 2039622239 | 2017-08-05 | 8 | 2017-07-13 | abnormal noise | 2017-06-12 | 2017-07-14 | ZH | null | null | 1 | Abnormal sound from HP cylinder due to no lubrication and delivery valve back leaking. | null | closed | Replaced Liner , Piston , Piston ring set, Gudgeon pin , HP Connecting rod ,& Discharge valve assly.
2017-08-20 | S M Refrigeration | null | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX42 | 3444K006 | 2025522229 | 2017-08-01 | 8351 | 2017-06-04 | cylinder rusty & delivery valve leakage | 2015-10-28 | 2017-06-10 | ZH | null | null | 20 | Found rust on cylinder liner and Discharge valve leakage. | null | closed | Replaced Discharge valve assly 02 nos, Suction ring spring & Pressure gauge 16 Kg/cm2.
2017-08-20 | S M Refrigeration | null | D | Narayan Fruits & Vegetables | Uttar Pradesh | KC6 | 339K3409 | 2038182225 | 2017-08-01 | 8360 | 2017-07-14 | loading / unloading problem | 2017-03-07 | 2017-04-04 | 30 | null | null | 1 | Found oil pressure problem in compressor. | null | closed | Replaced oil pump assembly
2017-08-20 | Kalp Marketing | Gujrat | D | Shree Lunai Ice & Cold Storage | Gujrat | KCX3 | 3374K1439 | 2038242228 | 2017-08-01 | 51 | 2017-07-28 | pressure gauge out | 2017-05-13 | 2017-07-29 | ZH | null | null | 2 | Oil pressure gauge out & OLG broken. | null | closed | Replaced Pressure gauge & OLG
2017-08-20 | S M Refrigeration | null | D | Gangotri Ice & Cold Storage | Uttar Pradesh | KC6 | 3394K3403 | 2039802240 | 2017-08-05 | 3074 | 2017-07-06 | suction pressure gauge not working. | 2017-02-11 | 2017-02-28 | 1498 | null | null | 1 | found pasting problem of the suction gauge inside round sheet. ??? | null | closed | Replaced pressure gauge
2017-08-26 | Vietbon Co. | null | E | Nguyen Phoc Dien | Vietnam | KC6 | 339K3223 | null | null | 371 | 2017-08-09 | abnormal noise | 2015-10-12 | 2016-12-07 | 4000 | null | null | 14 | Delivery valve leakage due to system dust | null | closed | cylinder liner,delivery valve
2017-08-26 | Kirloskar Pneumatic Co Ltd | New Delhi | D | United Breweries Ltd | null | KCX9 | 3404K040 | 2043562269 | 2017-08-21 | 258 | 2017-08-17 | abnormal noise | 2016-06-20 | 2016-08-03 | 3000 | null | null | 2 | Failure due to broken ring / spring of delivery valve . | null | closed | Replaced Piston , Piston rings & Delivery valve assly.
2017-08-26 | S M Refrigeration | null | D | Anjani Cold Storage | Uttar Pradesh | KC3 | 337K4688 | 2041482255 | 2017-08-14 | 5582 | 2017-08-10 | loading / unloading problem | 2016-10-28 | 2017-05-01 | 250 | null | null | 7 | Lubrication pressure very low. Oil pump checked found cut mark on drive shaft , cover & bush. | null | closed | Replaced gear kit
2017-08-26 | Trade Links | Secunderabad | D | S N J Dis Global Pvt Ltd | Andhra Pradesh | KCX9 | 3404K043 | 2041082251 | 2017-08-12 | 6 | 2017-08-06 | loading / unloading problem | 2016-12-31 | 2017-06-08 | 24(03) | null | null | 6 | Pr. Set at LP 3.0 Kg/cm2 & HP 6.0Kg/cm2 . Loading was done both oil pressure drop to 1.0 & 4.0 Kg/cm2. Inspection of pump was done found ok, Both regulators adjusted after taken air run trial abnormal oil pressure were developed. | null | closed | Replaced both OPR
2017-08-26 | Hss Solution Pvt Ltd | null | D | Gavya Milk Specialities Pvt Ltd | Rajastan | KCX4 | 3384K1603 | 2041742259 | 2017-08-16 | 10 | 2017-07-19 | oil carry over | 2017-04-24 | 2017-05-30 | 563 | null | null | 1 | suction strainer damage & paper filter chock hence cylinder wornout | null | closed | Replaced Piston, set ring ,gudgeon pin, bush connecting rod , pump element,bearings..
2017-08-26 | Trade Links | Secunderabad | D | Heritage Foods Ltd | Telangana | KCX2 | 3364K1107 | 2041722258 | 2017-08-16 | null | 2017-08-10 | oil carry over | 2016-07-13 | 2017-01-07 | 957 | null | null | 6 | In open oil throw no oil throw observed .ORV found leakage | null | closed | Replaced ORV
2017-08-26 | Trade Links | Secunderabad | D | Al | Kareem Exports | KC31 | 343K1492 | 2040162243 | 2017-08-08 | null | 2017-08-04 | op cutout not working | 2016-06-20 | 2017-01-16 | 442 | null | null | 6 | OP cutout malfunctioning | null | closed | Replaced OP cutout
2017-08-26 | Kalp Marketing | Gujrat | D | Shree Samji Ice Factory | Gujrat | KCX3 | 3374K1482 | 2041142257 | 2017-08-14 | 35 | 2017-08-10 | pressure gauge thrd damaged | 2017-07-15 | 2017-08-11 | 5 | null | null | 1 | Replaced gauge adaptors. | null | closed | null
2017-08-26 | Cool Comfort Private Limited | West Bengal | D | Khudiram Cold Storage | West Bangal | KCX4 | 3384K1302 | 2041362254 | 2017-08-14 | 863 | 2017-08-09 | shaft seal leakage and low oil pressure. | 2016-10-16 | 2017-03-07 | 1573 | null | null | 5 | Flywheel side main bearing worn-out, Also scratch mark on shaft seal mating face. | null | closed | Replaced main bearing bush & Kit shaft seal.
2017-08-26 | Pakistan | null | E | Umar Cold Storage | Pakistan | KC4 | 338K5481 | 531 | 2017-07-31 | 531 | 2017-07-31 | solenoid valve coil not working | 2016-05-01 | 2017-03-02 | 2381 | null | null | 10 | Coil not working for sol. Valve | null | closed | Sol vlave coil
2017-08-29 | Trade Links | Fh | D | Malpefresh Marine Export | Kundapura | KCX42 | 3444K036 | null | null | 1 | 2017-08-05 | piston touches to delivery valve | 2016-12-11 | 2017-08-05 | ZH | null | null | 8 | the sound was coming from in LP Cyl.No.6 while ''AIR RUN TRAIL TESTING TIME''. Hence,he has opened the head cover and found the piston was touches in to D.V.Assy | null | closed | Replaced liner gasket
2017-09-15 | Fridge House | null | D | Airtech Cooling Process | Karnataka | KCX3 | 3374K1282 | 2047042306 | 2017-09-01 | null | 2017-08-29 | oil pump cracked while transit time | 2017-01-30 | 2017-09-20 | ZH | null | null | 8 | Oil leaking while compressor running through oil pump cracked point. | null | closed | Oil pump assly
2017-09-16 | Pakistan | null | E | Soni Dharati Cold Storage | Sahiwal Pakistan | KCX6 | 3394K608 | null | null | null | 2017-08-26 | low oil pressurepiston sieze | 2016-07-01 | 2017-02-04 | 1134 | null | null | 7 | OP cutout setting not ok i.e. set at 0 kg/cm2 instead 1.0 kg/cm2 Cause of failure:-1) This breakdown may be happened due to liquid stroke in compressor . 2) Compressor not tripped even low oil pressure. So compressor may be operated on bypassing OP switch. | null | closed | null
2017-09-20 | Multivista Global Pvt Ltd | null | D | Kc Dairy Products Pvt Ltd | Tamil Nadu | KCX3 | 3374K1044 | 2047922318 | 2017-09-06 | null | 2017-09-02 | compressor abnormal sound | 2016-02-16 | 2016-07-06 | 1092 | null | null | 5 | Abnormal sound from cyl no 1 . All cylinder assly damaged ( Delivery valve , Piston ,Piston rings , liner , bearings & gudgeon pin etc.) Also crankshaft damaged. This complaint due to plant problem , Ammonia liquid enter in compressor. | null | closed | Replaced Crankshaft , Delivery valve , Piston ,Piston rings , liner assembly , bearings & gudgeon pin .
2017-09-20 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Telangana | KCX4 | 3384K1171 | 2048702322 | 2017-09-07 | null | 2017-08-31 | k5 valve thread damaged | 2016-02-22 | 2017-09-01 | ZH | null | null | 19 | Suction pressure K5 valve leakage due to threading damage. | null | closed | Replaced K5 Valve.
2017-09-20 | S M Refrigeration | null | D | Rajesh Cold Storage | null | KC6 | 339K3334 | 2050142325 | 2017-09-09 | null | 2017-08-29 | oil pump pressure not builtup | 2016-10-12 | 2017-02-22 | 717 | null | null | 4 | Oil pressure not develop due to drive shaft broken. | null | closed | Replaced gear kit.
2017-09-20 | Fridge House | null | D | Ag Tech Expo Cold Storage Pvt Ltd | Karnataka | KCX2 | 3364K1268 | 2047722314 | 2017-09-05 | null | 2017-09-01 | shaft seal leakage | 2017-03-20 | 2017-05-19 | 651 | null | null | 2 | Wornout stationary sealing ring. | null | closed | Replaced shaft seal.
2017-09-29 | Trade Links | Secunderabad | D | Satya Sea Foods P Ltd | Andhra Pradesh | KC93 | 348K151 | 2060802362 | 2017-09-29 | null | 2017-09-11 | compressor seized | 2017-05-09 | 2017-06-07 | 1344 | null | null | 1 | Intermediate bearing housing is not cylindrical -Ovality was observed.All damaged parts replaced but crankshaft not free hence replaced intermediate housing and found free. | null | closed | Replaced intermediate bearing complete.
2017-09-29 | Kalp Marketing | Gujrat | D | Laxmi Hi Tech Cold Storage | Gujrat | KCX4 | 3384K1442 | 2052502342 | 2017-09-19 | 75 | 2017-09-08 | discharge pressure gauge broken | 2017-01-16 | 2017-02-24 | 2890 | null | null | 1 | Discharge pressure gauge broken & not working | null | closed | Replaced pressure gauge
2017-09-29 | S M Refrigeration | null | D | R V S Cold Storage Pvt Ltd | Uttar Pradesh | KC4 | 338K5509 | 2050902330 | 2017-09-13 | 3084 | 2017-08-16 | oil lifting | 2016-10-29 | 2017-02-15 | 450 | null | null | 4 | Oil lifting due to ORV leakage | null | closed | Replaced ORV
2017-09-29 | S M Refrigeration | null | D | S N Cold Storage Pvt Ltd | Uttar Pradesh | KC4 | 338K5531 | 2049902326 | 2017-09-11 | 8364 | 2017-07-31 | oil lifting | 2016-11-30 | 2017-04-06 | 1500 | null | null | 5 | Oil lifting due to ORV leakage | null | closed | Replaced ORV
2017-09-29 | S M Refrigeration | null | D | C S Cold Storage | Agra | KC6 | 339K3339 | 2050442328 | 2017-09-11 | 8367 | 2017-08-20 | oil lifting | 2016-10-28 | 2017-04-01 | 2000 | null | null | 6 | Oil lifting due to ORV leakage | null | closed | Replaced ORV
2017-09-29 | S M Refrigeration | null | D | Kishori Kirpa Cold Storage | Uttar Pradesh | KCX6 | 3394K673 | 2050422327 | 2017-09-11 | 8365 | 2017-08-02 | oil lifting | 2016-12-05 | 2017-02-12 | 2586 | null | null | 2 | Oil lifting due to ORV leakage | null | closed | Replaced ORV
2017-09-29 | S M Refrigeration | null | D | S N Cold Storage Pvt Ltd | Uttar Pradesh | KC4 | 338K5500 | 2049862324 | 2017-09-09 | 8363 | 2017-07-31 | oil lifting | 2016-10-13 | 2017-03-11 | 1225 | null | null | 5 | Found leakage in ORV due to oil lifting of 2.5 liters within 24 hrs. | null | closed | Replaced ORV
2017-09-29 | Kalp Marketing | Gujrat | D | Badrinath Cold Storage | Gujrat | KCX4 | 3384K1523 | 2052482343 | 2017-09-19 | 76 | 2017-09-07 | pressure gauge not working | 2017-02-28 | 2017-03-16 | 375 | null | null | 1 | Ammonia leakage in pressure gauge , Dial of pressure gauge not working properly. | null | closed | Replaced discharge pressure gauge
2017-09-29 | Parag Marketing Services | null | D | Harekrishana Cold Storage | Sangli | KCX3 | 3374K1254 | 2047622311 | 2017-09-04 | 25 | 2017-08-20 | shaft seal leakage | 2017-01-16 | 2017-02-16 | 2642 | null | null | 1 | Scoring on shaft seal assly. Replaced assembly , Oil filters & new oil. | null | closed | Replaced shaft seal assembly
2017-09-29 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KC42 | 344K1089 | 2059382354 | 2017-09-25 | null | 2017-08-31 | solenoid valve coil not working | 2016-10-28 | 2017-09-01 | ZH | null | null | 11 | Solenoid valve was not working electrically . But working manually . Checked electrical coil and found problem in coil, Solenoid coil has to be replaced. | null | closed | Replaced coil
2017-10-15 | Kalp Marketing | Gujrat | D | Satyam Marine Export | null | KCX51 | 3454K041 | 2061602369 | 2017-10-04 | 79 | 2017-10-20 | no oil pressure | 2017-07-19 | 2017-08-28 | 595(03) | null | null | 1 | Pump element tang broken. | null | closed | KCX oil pump element
2017-10-15 | Kalp Marketing | Gujrat | D | Vinayak Agroindustries | null | KCX42 | 3444K070 | 202162372 | 2017-10-06 | 45 | 2017-10-01 | overheating of cylinder | 2017-09-01 | 2017-09-17 | 1494 | null | null | 1 | delivery valve leakage | null | closed | delivery valve
2017-10-15 | Fridge House | null | D | Airtech Cooling Process | Karnataka | KCX4 | 3384K1613 | 2061102374 | 2017-10-06 | null | 2017-09-20 | solenoid valve malfuctioning | 2017-05-18 | 2017-09-27 | ZH | null | null | 4 | plunger stuckup | null | closed | sol. Valve
2017-10-29 | Trade Links | Secunderabad | D | Satya Sea Foods P Ltd | Andhra Pradesh | KC93 | 348K151 | 2060802362 | 2017-09-29 | null | 2017-09-11 | compressor seized | 2017-05-09 | 2017-06-07 | 1344 | null | null | 1 | Intermediate bearing housing is not cylindrical -Ovality was observed. | null | closed | Replaced intermediate bearing.
2017-10-29 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sarna Checmicals Pvt Ltd | Mumbai | KCX3 | 3374K1480 | 2060382360 | 2017-09-27 | 29 | 2017-09-27 | crankcase heater leak | 2017-06-28 | 2017-09-22 | ZH | null | null | 3 | Pin hole on heater body . | null | closed | Heater to be replaced.
2017-10-29 | Trade Links | Secunderabad | D | Heritage Foods Ltd | Telangana | KC21 | 342K883 | 2062622377 | 2017-10-09 | 27 | 2017-09-18 | flywheel not rotating | 2016-07-19 | 2017-02-17 | 890 | null | null | 7 | Compressor seize . | null | closed | null
2017-10-29 | Kalp Marketing | Gujrat | D | Satyanarayana Cold Storage | Gujrat | KC4 | 338K5547 | 2063002379 | 2017-10-10 | 201 | 2017-08-10 | flywheel wobbling | 2016-12-25 | 2017-02-14 | 1204 | null | null | 2 | Removed flywheel and observed shaft key laid out side on the crankshaft. Crankshaft damaged. | null | closed | null
2017-10-29 | Fridge House | null | D | Abhiman Ice & Cold Storage | Karnataka | KCX4 | 3384K1231 | 2046222307 | 2017-09-02 | null | 2017-08-22 | high oil consumption | 2016-06-13 | 2016-08-05 | 5482 | null | null | 2 | 2.5 lit/20 hr . All four liner , piston , piston ring set worn-out. | null | closed | Replaced all four liner , piston , piston ring set , gudgeon pin & bearings.
2017-10-29 | S M Refrigeration | null | D | International Agro Food | Uttar Pradesh | KCX72 | 3474K108 | 2060502364 | 2017-09-29 | 261 | 2017-09-25 | k5 valve leakage | 2017-07-21 | 2017-09-27 | ZH | null | null | 2 | Found 2 K5 Vlave leakage during commissioning. Also wrong connection in control panel - Correction done. | null | closed | Replaced K5 Valve
2017-10-29 | Trade Links | Secunderabad | D | Sri Chakra Milk Products Llp | Andhra Pradesh | KCX3 | 3374K1086 | 2060322359 | 2017-09-27 | 47 | 2017-09-20 | loading problem | 2016-05-13 | 2016-07-05 | 3490 | null | null | 2 | Oil pump element had wornout & liner gasket damaged for cyl no. | null | closed | Replaced oil pump element & liner gasket.
2017-10-29 | Trade Links | Secunderabad | D | Satya Sea Foods P Ltd | Andhra Pradesh | KC93 | 348K151 | 2048282320 | 2017-09-07 | null | 2017-08-29 | low oil pressure & metal dust in filters. | 2017-05-09 | 2017-06-07 | 1344 | null | null | 1 | All bearings and thrust ring wornout. | null | closed | Replaced all bearings & Thrust ring.
2017-10-29 | Model Pneumatic Co | Punjab | D | Gupta Brothers Cold Storage | Punjab | KCX3 | 3374K1146 | 2059122349 | 2017-09-22 | 122 | 2017-03-31 | no oil pressure | 2016-10-22 | 2017-02-10 | 250 | null | null | 4 | Oil pump element broken. | null | closed | Replaced pump element.
2017-10-29 | Model Pneumatic Co | Punjab | D | Momi Cold Storage | Punjab | KCX6 | 3394K721 | 2059182351 | 2017-09-22 | 135 | 2017-04-14 | no oil pressure & shaft seal leakage. | 2017-01-28 | 2017-03-06 | 255 | null | null | 2 | Oil pump element broken & shaft seal leakage. | null | closed | Replaced oil pump assly & seal.
2017-10-29 | Trade Links | Secunderabad | D | Umr Ice Factory | Andhra Pradesh | KCX3 | 3374K1148 | 2060302358 | 2017-09-27 | 14 | 2017-09-12 | oil lifting | 2017-10-23 | 2016-12-26 | 3817 | null | null | 2 | Oil consumption 3 lit/24Hrs of running. Oil throw observed from all 3 cylinders and cyl no. 2 &3 ORV back leaking. | null | closed | Replaced Set piston rings & ORV
2017-10-29 | Trade Links | Secunderabad | D | Sai Krishna Ice Factory | Andhra Pradesh | KCX3 | 3374K1070 | 2050122368 | 2017-09-29 | 45 | 2017-09-04 | oil lifting | 2016-03-29 | 2016-05-11 | 5802 | null | null | 2 | Piston rings wornout due to more oil consumption. 10 lit/weak | null | closed | Replaced set piston ring set
2017-10-29 | Model Pneumatic Co | Punjab | D | Momi Cold Storage | Punjab | KCX6 | 3394K721 | 2059162350 | 2017-09-22 | 126 | 2017-04-06 | oil pressure not buildup | 2017-01-28 | 2017-03-06 | 126 | null | null | 2 | Oil pump tang broken. | null | closed | Replaced oil pump element
2017-10-29 | Trade Links | Secunderabad | D | Grand Cold Storage | Telangana | KCX42 | 3444K025 | 2060722363 | 2017-09-29 | 4 | 2017-07-07 | oil pressure not buildup | 2016-07-11 | 2016-11-09 | 2936 | null | null | 4 | Oil pump tang broken. | null | closed | Replaced oil pump element
2017-10-29 | Hss Solution Pvt Ltd | null | D | Vrindavan Dairies | Rajastan | KCX4 | 3384K1330 | 2060222356 | 2017-09-27 | 24 | 2017-09-27 | shaft seal leakage | 2016-11-13 | 2017-04-05 | 2210 | null | null | 5 | Shaft seal bronze ring wornout . | null | closed | Replaced shaft seal.
2017-10-29 | Trade Links | Secunderabad | D | Krishna Ice Factory | Andhra Pradesh | KCX3 | 3374K1458 | 2060442378 | 2017-10-09 | null | 2017-09-18 | solenoid valve stukup in manual operating. | 2017-06-10 | 2017-09-27 | 12 | null | null | 3 | Solenoid valve - 2 nos had stuck in manually loading condition. Due to urgency to commission from customer & non availability of solenoid valve in stock. Machining of plunger were done informed KPCL-Mr. Anjaiah. Assembled back the solenoid valve and taken air run trial. Loading / Unloading ok. | null | closed | null
2017-11-03 | Fridge House | null | D | Suhas Enterprises Fish Curing Yard | Karnataka | KCX6 | 3394K611 | 2046262308 | 2017-09-02 | null | 2017-08-22 | high oil consumption & knocking sound. | 2016-07-13 | 2016-10-07 | 4947 | null | null | 3 | Oil consumption 3 lit/24Hrs of running. All piston , Piston ring set , Liners worn-out damaged. | null | closed | Replaced All piston , Piston ring set , Liners , Gudgeon pin , Bearings .
2017-11-17 | Trade Links | Goa | D | M B Ice Plant | Goa | KCX3 | 3374K1362 | Mail | 2017-11-17 | null | 2017-11-17 | cloth piece inside crankcase | 2017-03-03 | 2017-11-17 | ZH | null | null | 8 | While commissioning of the compressor observed cotton cloth/duster inside the crankcase. | null | closed | null
2017-11-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX72 | 3474K004 | 2063102437 | 2017-11-14 | 274 | 2017-09-30 | kcx oil pumppurging | 2016-10-12 | 2017-04-16 | 638 | null | null | 6 | oil purging problem | null | closed | Replace oil pump
2017-11-22 | Kalp Marketing | Gujrat | D | Khyati Chemicals Pvt Ltd | null | KCX6 | 3394K668 | 2070442431 | 2017-11-09 | 247 | 2017-11-02 | knocking sound in compressor | 2016-11-26 | 2017-05-02 | 2444 | null | null | 5 | Buffer spring length sortened | null | closed | replace buffer spring,Gasket
2017-11-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Versova Koli Sahakari Sarvodaya Society Ltd | Mumbai | KCX6 | 3394K544 | 27 | 2017-09-08 | 4 | 2017-08-23 | loading and unloading problem | 2015-12-01 | 2015-12-11 | 200 | null | null | 1 | Solenoid valve problem | null | closed | replaced sol. Valve
2017-11-22 | Trade Links | Secunderabad | D | Sai Krishna Ice Factory | Andhra Pradesh | KCX6 | 3394K578 | 2046082297 | 2017-08-30 | 40 | 2017-08-19 | low oil pressure | 2016-03-29 | 2016-05-12 | 7752 | null | null | 2 | Piston , piston rings and liner siezed | null | closed | Replace c.shaft,piston,liner and piston ring set, bearngs.
2017-11-22 | Cool Comfort Private Limited | West Bengal | D | Sarabmngala Cold Storage | null | KCX4 | 3384K1449 | null | null | 1101 | 2017-11-10 | oil lifting | 2017-01-01 | 2017-03-15 | 1200 | null | null | 2 | Cylinder no.03 Blind ORV fitted | null | closed | ORV
2017-11-22 | Kalp Marketing | Gujrat | D | Mcc Agar 1601 | null | PC2 | 331K2919 | 2070602432 | 2017-11-09 | 203 | 2017-10-25 | oil pressure not buildup | 2017-06-05 | 2017-10-12 | 80 | null | null | 4 | oil pressure not develops | null | closed | Bush and gears of oil pump siezed
2017-11-22 | Fridge House | null | D | Airtech Cooling Process | Karnataka | KCX4 | 3384K1614 | 2061122375 | 2017-10-06 | null | 2017-09-20 | op cutout not working | 2017-05-19 | 2017-09-27 | ZH | null | null | 4 | OP cutout not trip after oil pressure drop | null | closed | Repalce OP cutout
2017-11-22 | Morgan | null | E | Diamond Ice Factory | null | KCX6 | 3394K835 | null | null | null | 2017-11-07 | paint problem | null | 2017-11-06 | ZH | null | null | null | paint discolouring due to overheating of cylinders | null | closed | null
2017-11-22 | Fridge House | null | D | Tolar Ocean Products | null | KC72 | 347K971 | 2061142376 | 2017-10-06 | null | 2017-09-20 | pressure gauge out | 2017-06-28 | 2017-09-28 | ZH | null | null | 3 | pressure gauge shows negative pressure | null | closed | Pressure gauge
2017-11-24 | Trade Links | Goa | D | Taralai Ice Factory | Goa | PC2 | 331K2786 | 2021422130 | 2017-06-09 | 58 | 2017-04-05 | failure of oil pump | 2015-12-04 | 2017-01-18 | 35 | null | null | 13 | Oil pump gear jammed. | null | closed | Replaced oil pump assembly.
2017-11-24 | Parag Marketing Services | null | D | Krishna Green Field Multistate Co | Sangli | KCX2 | 3364K1310 | 2066462409 | 2017-10-28 | 50 | 2017-10-15 | loading / unloading problem | 2017-05-03 | 2017-07-03 | 1150 | null | null | 2 | solenoid valve coil burned and jammed in solenoid valve. | null | closed | Replaced solenoid valve
2017-11-24 | Hss Solution Pvt Ltd | null | D | Rajendra Ursula Joshi Foods Pvt Ltd | Rajastan | KC4 | 338K5524 | 2066102404 | 2017-10-26 | 39 | 2017-10-16 | oil pressure not buildup | 2016-11-20 | 2017-10-17 | 3 | null | null | 12 | Gear set damaged within 20 min. | null | closed | Replaced gearkit
2017-11-24 | Kalp Marketing | Gujrat | D | Satyam Marine Export | Veraval, Gujarat | KCX51 | 3454K041 | 2070702433 | 2017-11-09 | 102 | 2017-11-04 | oil pressure not buildup | 2017-07-19 | 2017-08-28 | 955 | null | null | 1 | Compressor seized. | null | closed | Replaced Crankshaft & all bearings.
2017-11-24 | Parag Marketing Services | null | D | Amul Satelite Dairy | Pune | KCX4 | 3384K1608 | 2066602410 | 2017-10-28 | 139 | 2017-10-04 | oil pressure not delvelop & shaft seal leakage. | 2017-05-08 | 2017-08-09 | 999 | null | null | 3 | Oil pump element broken & seal leakage | null | closed | Replaced element
2017-11-24 | Kalp Marketing | Gujrat | D | Vinayak Agroindustries | null | KCX42 | 3444K070 | 2067362412 | 2017-10-31 | 40 | 2017-10-28 | overheating of cylinder | 2017-09-01 | 2017-09-17 | 1545 | null | null | 1 | Delivery valve leakage | null | closed | Delivery vlave
2017-11-24 | Kalp Marketing | Gujrat | D | Bhagwat Industries | Gujrat | KCX4 | 3384K1619 | 2069302421 | 2017-11-07 | 100 | 2017-11-05 | shaft seal leakage & overheat compressor. | 2017-05-23 | 2017-10-26 | 140 | null | null | 5 | Shaft seal leakage & one delivery valve leakage. After lapping of shaft seal & valve rings both delivery valve & seal found ok. | null | closed | After lapping of shaft seal & valve rings both delivery valve & seal found ok.
2017-11-24 | Trade Links | Goa | D | Albys Agro Pvt Ltd | Goa | KCX4 | 3384K1198 | 2065062393 | 2017-10-23 | 3 | 2017-07-18 | stop valve leakage | 2016-03-30 | 2017-04-26 | 61 | null | null | 13 | Spindle was broken , spindle welding done and replaced Teflon ring , inner & Outer gaskets. | null | closed | Replaced Teflon ring , inner & Outer gaskets.
2017-12-19 | Fridge House | null | D | Fiza Exports | Karnataka | KC72 | 347K952 | 2079622474 | 2017-12-07 | null | 2017-12-04 | abnormal noise | 2016-10-19 | 2017-11-03 | ZH | null | null | 13 | Run the comp observed more knocking sound in direct HP Cyl no. 4 due to delivery valve leakage and buffer spring shrink to 108mm. The gas has bypass through piston and stroke limitor. Cylinder seized. | null | closed | Replaced cylinder assembly.
2017-12-19 | Parag Marketing Services | null | D | Priyanka Ice Factory | Pune | KCX2 | 3364K1357 | 2078682471 | 2017-12-06 | 2129 | 2017-11-19 | cylinder overheating problem | 2017-06-27 | 2017-08-11 | 1850 | null | null | 2 | Replaced buffer spring , kit delivery valve , spring & Ring teflon. | null | closed | Replaced bufferspring , kit delivery valve , spring & Ring taflon.
2017-12-19 | Parag Marketing Services | null | D | SL Agro Foods | Pune | KCX42 | 3444K030 | 2075982460 | 2017-11-28 | 110 | 2017-09-06 | delivery valve leakage | 2016-09-30 | 2017-09-07 | ZH | null | null | 12 | Cylinder overheating problem due to delivery valve leakage. Cyl no.4, Replaced ring/spring but not succeed. | null | closed | Replaced delivery valve assembly
2017-12-19 | Kirloskar South East Asia Co Ltd | Thailand | E | Ksea | Thailand | KCX9 | 3404K26 | email | 2017-12-12 | null | null | knocking / abnormal sound | 2016-01-01 | 2017-10-15 | PC(03) | null | null | 12 | Piston touching delivery valve , bearing wornout and Piston worn-out. | null | closed | null
2017-12-19 | Trade Links | null | D | Albys Agro Pvt Ltd | Goa | KCX4 | 3384K1198 | 2080042477 | 2017-12-08 | 18 | 2017-11-14 | low oil pressure | 2016-03-30 | 2017-04-26 | 1036 | null | null | 1 | Oil pressure regulators not functioning | null | closed | OPR
2017-12-19 | Trade Links | null | D | Albys Agro Pvt Ltd | Goa | KC72 | 347K917 | 2079642475 | 2017-12-07 | 15 | 2017-11-14 | low oil pressure | 2016-03-30 | 2017-04-26 | 1036 | null | null | 13 | Pump housing wornout | null | closed | Oil pump
2017-12-19 | S M Refrigeration | null | D | Ranjeet Singh Cold Storage | Uttar Pradesh | KCX4 | 3384K1532 | 2069082418 | 2017-11-06 | 8376 | 2017-10-29 | oil pressure not buildup | 2017-03-03 | 2017-03-29 | 1308 | null | null | 1 | Oil pressure problem. | null | closed | Replaced pump element.
2017-12-19 | Fridge House | null | D | Fiza Exports | Karnataka | KC72 | 347K952 | 2079602470 | 2017-12-04 | null | 2017-12-04 | shaft seal leakage | 2016-10-19 | 2017-11-03 | ZH | null | null | 13 | Run the comp observed more knocking sound in direct HP Cyl no. 4 due to delivery valve leakage and buffer spring shrink to 108mm. The gas has bypass through piston and stroke limitor. Cylinder seized. | null | closed | Replaced shaft seal assembly
2017-12-19 | Trade Links | Goa | D | Albys Agro Pvt Ltd | Goa | KCX4 | 3384K1198 | 2069502443 | 2017-11-17 | 14 | 2017-10-24 | shaft seal leakage | 2016-03-30 | 2017-04-26 | 936 | null | null | 13 | Due to casting defect of bearing cover housing replaced shaft seal assly | null | closed | Replaced shaft seal & Bearing cover
2017-12-19 | Fridge House | null | D | Mysuru Dist Co-Operative Milk Prods Society Union | Karnataka | KCX4 | 3384K1200 | 2062262384 | 2017-10-12 | null | 2017-11-03 | shaft seal leakage | 2016-03-30 | 2017-01-23 | 855 | null | null | 9 | Obsrevd and found foregin particles in shaft seal assly and found wornout of rotary ring. | null | closed | Replaced shaft seal assembly
2017-12-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Seasaga Enterprises Pvt Ltd | Panvel | KCX4 | 3384K1583 | 2077602470 | 2017-12-04 | 194 | 2017-12-02 | shaft seal leakage | 2017-03-30 | 2017-08-28 | 807 | null | null | 5 | Stationary sealing ring damaged. | null | closed | Replaced shaft seal assembly
2017-12-19 | Trade Links | Secunderabad | D | Godavari Mega Aqua Food Park | null | KC6 | 339K3221 | 2060282357 | 2017-09-27 | 49 | 2017-09-12 | shaft seal leakage & low oil pressure. | 2015-10-24 | 2017-08-30 | 82 | null | null | 18 | Shaft seal , thrust ring & oil pump had wornout. | null | closed | Replaced Shaft seal , thrust ring & oil pump.
2017-12-23 | S M Refrigeration | null | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX72 | 3474K126 | Mail | 2017-12-02 | null | 2017-12-02 | control pannel box wrong oil pressure connection | 2017-08-25 | 2017-12-02 | ZH | null | null | 4 | Control pannel box - Wrong oil pressure connection | null | closed | null
2017-12-23 | Geekay Pneumatic Pvt Ltd | null | D | Badriya Ice Plant | Kerala | KCX2 | 3364K1303 | 2080142478 | 2017-12-09 | 5034 | 2017-08-30 | pressure gauge out | 2017-04-25 | 2017-09-02 | ZH | null | null | 5 | Suction pressure gauge out by 0.75Kg/cm2. | null | closed | null
2018-01-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Mahad | KCX3 | 3374K1151 | 2081062483 | 2017-12-24 | 195 | 2017-12-09 | abnormal noise | 2016-10-28 | 2017-02-16 | 3828 | null | null | 4 | Cylinder no. 2 , Delivery valve leakage and Shaft seal leakage. | null | closed | Replaced delivery valve , Shaft seal and suction ring.
2018-01-20 | S M Refrigeraion Pvt Ltd | null | D | S R Cold Storage | Uttar Pradesh | KCX3 | 3374K1518 | 2082622498 | 2017-12-21 | 4134 | 2017-12-19 | drain adaptor broken | 2017-09-12 | 2017-12-19 | ZH | null | null | 3 | TAH8 valve / Drain adaptor was broken. In multiple TAH8 Vlave damage cases found . It may be handling damage. | null | closed | Replaced Drain adaptor
2018-01-20 | Kalp Marketing | Gujrat | D | Dashing Cold Storage | Gujrat | KCX3 | 3374K1528 | 2082302512 | 2018-01-05 | 113 | 2017-12-17 | k5 valve leakage | 2017-09-29 | 2017-12-18 | ZH | null | null | 3 | K5 Vlave leakage. | null | closed | Replaced K5 Vlave
2018-01-20 | Parag Marketing Services | null | D | Naik Sea Foods | Ratnagiri | KCX72 | 3474K017 | 2082542497 | 2017-12-21 | 2085 | 2017-12-15 | knocking / abnormal sound | 2016-07-01 | 2016-08-09 | 4322 | null | null | 1 | LP OPR crclip fall down, compressor bearings siezed | null | closed | Crank shaft,main bearings,gudgeon pin,locking plate.
2018-01-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Mahad | KCX3 | 3374K1151 | 2066182403 | 2017-10-26 | 154 | 2017-08-28 | oil carry over | 2016-10-28 | 2017-02-16 | 2269 | null | null | 4 | Oil carry over 2 liter /24 Hrs. | null | closed | Replaced piston ring sets & VLD Orings
2018-01-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Mahad | KCX3 | 3374K1152 | 2066142402 | 2017-10-26 | 153 | 2017-08-29 | oil carry over | 2016-10-28 | 2017-02-16 | 2479 | null | null | 4 | Oil carry over 2 liter /24 Hrs. | null | closed | Replaced piston ring sets & VLD Orings
2018-01-20 | S M Refrigeration | null | D | Rahul Sheetgrah Pvt Ltd | Uttar Pradesh | KC6 | 3394K3410 | 2083182499 | 2017-12-23 | 838083818382 | 2017-12-13 | oil pressure not buildup | 2017-03-08 | 2017-04-05 | 834 | null | null | 1 | Gear kit broken -Replaced gear kit. Again within 2 Hr gear kit broken , bushes seized. | null | closed | Replaced Oil pump assly & Gear kit
2018-01-20 | Geekay Pneumatic Pvt Ltd | null | D | K M Fisheries | Kerala | KCX51 | 3454K013 | 2089182533 | 2018-01-16 | 5054 | 2017-12-07 | pressure gauge leak | 2016-09-12 | 2017-12-08 | 7 | null | null | 3 | Intermediate pressure gauge leakage.( Glycerin Leak) | null | closed | Replaced Pressure gauge
2018-01-20 | Kalp Marketing | Gujrat | D | Ismani Krupa Cold Storage | Gujrat | KCX4 | 3384K1386 | 2082362495 | 2017-12-20 | 243 | 2017-12-07 | shaft seal leakage | 2016-12-23 | 2017-02-14 | 421 | null | null | 2 | Shaft seal leakage | null | closed | Replaced Oring kit
2018-01-25 | Trade Links | Secunderabad | D | Radical Boi Organic Ltd | Telangana | KCX72 | 3474K087 | 2089602532 | 2018-01-16 | null | 2018-01-04 | abnormal noise | 2017-05-21 | 2018-01-07 | ZH | null | null | 8 | Abnormal wearing of HP Connecting rod and Piston rings due to oil hole not straight resulted into lubrication not proper. | null | closed | Replaced Piston ring set and HP Con rod.
2018-01-25 | Fridge House | null | D | Aishwarya Ice & Cold Storage | Karnataka | KCX6 | 3394K634 | 2082082493 | 2017-12-19 | null | 2017-12-14 | abnormal noise | 2016-08-28 | 2016-11-18 | 4869 | null | null | 3 | Knocking sound from cylinder no. 1 & 4 due to cylinder liner & Piston rings worn-out . Also spurious filter observed. | null | closed | Replaced both liners & Piston ring set after approval from B.O.
2018-01-25 | Kalp Marketing | Gujrat | D | Satyam Marine Export Pvt Ltd | Gujrat | KCX51 | 3454K041 | 2075222455 | 2017-11-27 | 224 | 2017-11-23 | compressor seize | 2017-07-19 | 2017-08-28 | 955 | null | null | 1 | Liner kit and cylinder head gaskets wornout/broken. | null | closed | Erlier problem of compressor seize .Already replaced crankshaft customer wants to replace the liner & gasket.
2018-01-25 | Geekay Pneumatic Pvt Ltd | null | D | Gsk Business Associateds Pvl Ltd | Kerala | KCX51 | 3454K008 | 2086202509 | 2018-01-05 | 6012 | 2018-01-02 | dd flywheel retaining plate tap holes missing. | 2016-06-29 | 2018-01-02 | ZH | null | null | 18 | Flywheel not having holes for retaining plate assembly. | null | closed | Replaced Flywheel coupling.
2018-01-25 | Trade Links | Secunderabad | D | Abu Bakar Frozen Foods | Telangana | KCX42 | 3444K046 | 2087162519 | 2018-01-08 | 36 | 2017-12-30 | discharge filter spring & spacer ring missing. | 2017-03-01 | 2018-01-01 | ZH | null | null | 10 | Spring & Spacer missing in discharge filter. | null | closed | Replaced Spring & Spacer missing in discharge filter.
2018-01-25 | Kalp Marketing | Gujrat | D | Bhavani Industries | Gujrat | KCX6 | 3394K639 | 20181422487 | 2017-12-15 | 237 | 2017-11-23 | knocking / abnormal sound | 2016-09-19 | 2016-10-20 | 5125 | null | null | 1 | Knocking sound from cylinder no.2 due to piston touching to delivery valve . | null | closed | Replaced gasket & Suction ring
2018-01-25 | S M Refrigeraion Pvt Ltd | null | D | Bhole Baba Ice & Cold Storage Pvt Ltd | Uttar Pradesh | KCX4 | 3384K1547 | 2081462489 | 2017-12-15 | 3097 | 2017-11-09 | oil pressure not buildup | 2017-03-11 | 2017-05-05 | 1081 | null | null | 2 | Oil pressure not builtup due to pump elemnet broken. | null | closed | Oil pressure not builtup due to pump elemnet broken.
2018-01-25 | Kalp Marketing | Gujrat | D | Satyam Marine Export Pvt Ltd | Gujrat | KCX51 | 3454K041 | 20181022484 | 2017-12-14 | 105 | 2017-12-07 | oil pressure not buildup | 2017-07-19 | 2017-08-28 | 1076 | null | null | 1 | pump element broken. | null | closed | Replaced pump element
2018-01-25 | Parag Marketing Services | null | D | Sonali Ice Factory | Sangli | KCX2 | 3364K1416 | 2089442531 | 2018-01-15 | 2087 | 2017-12-22 | oil pump purging | 2017-11-28 | 2017-12-09 | 112(03) | null | null | 1 | During initial starting purging required for pump. | null | closed | Replaced pump assembly
2018-01-25 | Kalp Marketing | Gujrat | D | Runaq Ice & Cold Storage | Gujrat | KCX42 | 3444K075 | 2075162453 | 2017-11-27 | 223 | 2017-11-20 | panel board wiring wrong & pressure gauge not working | 2017-11-04 | 2017-11-16 | 80 | null | null | 1 | Panel wiring worng & Pressure gauge 25 Kg /cm2 not working | null | closed | Replaced pressure gauge & Wiring corrected.
2018-01-25 | Parag Marketing Services | null | D | Latur Zilha Sah Dudh Utpadak Sangh | Latur | PC2 | 331K2930 | 2088802528 | 2018-01-12 | 2094 | 2017-12-02 | shaft seal leakage | 2017-07-18 | 2017-09-01 | 380 | null | null | 2 | Scoring on shaft seal and dots marks on stationary seal. | null | closed | Replaced shaft seal assly.
2018-01-25 | Fridge House | null | D | Kolar-Cchikballapura Prods Scociety Union Ltd | Karnataka | KCX51 | 3454K009 | 2082042492 | 2017-12-19 | null | 2017-12-11 | solenoid valve not working | 2016-08-22 | 2017-12-18 | ZH | null | null | 16 | NC Solenoid valve manually not functioning due to plunger jammed. | null | closed | Replaced solenoid valve assly
2018-01-30 | Multivista Global Pvt Ltd | null | D | High Range | Tamil Nadu | KCX2 | 3364K1307 | 2090182354 | 2018-01-17 | null | 2017-12-21 | abnormal noise | 2017-04-29 | 2017-06-28 | 1349 | null | null | 2 | Connecting rod bolt loosened and oil hole blocked | null | closed | Replaced c.shaft, bearings
2018-01-30 | Kirloskar Pneumatic Co Ltd | Lucknow | D | Varun Beverage Limited | Uttar Pradesh | KC9 | 340K385 | 2085402506 | 2018-01-02 | 233 | 2017-09-25 | abnormal noise | 2017-03-04 | 2017-05-01 | 1206 | null | null | 2 | cylinser liner,piston and piston ring set worn out-3nos. | null | closed | liner,piston,piston ring set, SE & BE bearings 3 nos.
2018-01-30 | Trade Links | Secunderabad | D | Anannda Aqua Exports | Andhra Pradesh | KC51 | 345K980 | 2048502321 | 2017-09-07 | 11 | 2017-08-21 | abnormal noise and low oil pressure | 2016-03-26 | 2016-04-14 | 7705 | null | null | 1 | Abnormal sound and low oil pressure | null | closed | piston,gudgeon pin,piston ring set,HP con rod
2018-01-30 | Morgan | null | E | Hassan Hajratex Ice Plant | Karachi, Pakistan | KC6 | 339K3419 | null | 2017-10-13 | null | 2017-10-11 | high oil consumption | 2017-03-20 | 2017-06-05 | NA | null | null | 3 | 7-8 Lit oil consumption in 24 Hrs due to piston rings were worn-out | null | closed | Replaced all piston rings
2018-01-30 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX31 | 3434K039 | 20811222494 | 2017-12-19 | null | 2017-12-14 | kcx oil pressure not develop | 2017-04-23 | 2017-09-16 | 60 | null | null | 4 | Oil pump element tang broken | null | closed | Oil pump element replaced.
2018-01-30 | Kalp Marketing | Gujrat | D | Aftab Exports | null | KCX72 | 3474K105 | 2081402486 | 2017-12-08 | 107 | 2017-12-08 | knocking / abnormal sound | 2017-07-25 | 2017-10-02 | 658 | null | null | 2 | Delivery valve leakage | null | closed | Delivery valve kit
2018-01-30 | Parag Marketing Services | null | D | Tumasare Milk Products | Madhya Pradesh | KCX1 | 3354K011 | 2045602294 | 2017-08-29 | 106 | 2017-07-10 | oil carry over | 2016-06-24 | 2016-12-26 | 3215 | null | null | 6 | piston ring close gap increased | null | closed | Piston ring set and ORV replaced
2018-01-30 | Cool Comfort Private Limited | West Bengal | D | Maa Durga Baraf | Kalcutta | KCX1 | 3354K005 | Mail | 2017-12-06 | null | 2017-12-06 | oil carry over | 2016-04-01 | 2016-12-06 | 1800 | null | null | 8 | High oil carryover | null | closed | Compressor rectification done at KPCL
2018-01-30 | Cool Comfort Private Limited | West Bengal | D | Bharat Ice Plant | Malancha, West Bengal | KCX1 | 3354K004 | Mail | 2017-12-06 | null | 2017-12-06 | oil carry over | 2016-02-01 | 2016-04-01 | 1800 | null | null | 2 | High oil carryover | null | closed | Compressor rectification done at KPCL
2018-02-25 | Trade Links | null | D | Abu Bakar Frozen Foods | Hydrabad | KCX72 | 3474K054 | email | 2018-02-20 | null | 2018-02-20 | abnormal noise | 2017-01-10 | 2017-12-13 | null | null | null | 11 | Top clearance got reduced due to shrinkage of Liner gasket. Replace with a New type gasket and it is under observation. | null | null | null
2018-02-25 | Trade Links | null | D | Abu Bakar Frozen Foods | Hydrabad | KCX72 | 3474K091 | email | 2018-02-20 | null | 2018-02-20 | abnormal noise | 2017-05-29 | 2017-12-13 | null | null | null | 7 | On abnormal sound cylinder Liner opened and observed that there is no lubrication in the cylinder. Due to which piston got seized.( HP Piston) | null | null | null
2018-02-25 | Kalp Marketing | Gujrat | D | Aftab Exports | null | KCX72 | 3474K105 | 2092302545 | 2018-01-25 | 139 | 2018-01-16 | abnormal noise | 2017-07-25 | 2017-10-02 | 1010 | null | null | 2 | Burr found in compressor delivery side | null | closed | Cylinder liner,Piston,piston ring set
2018-02-25 | Trade Links | null | D | Svr Laboratories P Ltd | Yadadri Dist | KCX21 | 3424 K 050 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | null | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | Svr Laboratories P Ltd | Yadadri Dist | KCX21 | 3424 K 051 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2017-09-16 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | K K Agro Cold Storage | Hydrabad | KCX42 | 3444 K 050 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2017-09-16 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | K K Agro Cold Storage | Hydrabad | KCX31 | 3434K0044 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2017-09-18 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX42 | 3444 K 048 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2017-11-30 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX42 | 3444 K 049 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | null | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX31 | 3434K0039 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2018-01-12 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX3 | 3374K1411 | email | 2018-02-20 | null | 2018-02-20 | control pannel box wrong oil pressure connection | null | 2018-01-13 | null | null | null | null | Control pannel box - Wrong oil pressure connection | null | closed | null
2018-02-25 | Trade Links | Secunderabad | D | Munaga Chennai Cold Storage | null | KCX3 | 3374K1609 | 2090722560 | 2018-02-10 | null | 2018-01-03 | hp cutout not working | 2017-12-08 | 2018-01-05 | ZH | null | null | 1 | HP cutout not wotking | null | closed | HP cutout
2018-02-25 | Parag Marketing Services | null | D | Godavvari Khore Dudh Sangh | null | KC4 | 338K5628 | 2086662513 | 2018-01-05 | 1922 | 2017-12-20 | k5 valve leakage | 2017-10-29 | 2018-02-18 | ZH | null | null | 3 | K5 valve leakage due to threading damaged | null | closed | K5 valve
2018-02-25 | Parag Marketing Services | null | D | Mehata Dairy | null | KCX3 | 3374K1440 | 2092562547 | 2018-01-29 | 2098 | 2018-01-17 | oil carry over | 2017-05-15 | 2017-05-27 | 4204 | null | null | 1 | ORV plates misplaced | null | closed | ORV
2018-02-25 | S M Refrigeration | null | D | Imtiyaj Ice Factory | Haryana | KCX2 | 3364K1400 | 2099222566 | 2018-02-17 | 108 | 2018-01-22 | op cutout and wiring burn out | 2017-10-07 | 2018-01-24 | ZH | null | null | 1 | Found OP cutout and control wiring burst during commissioning | null | closed | Control box
2018-02-25 | Trade Links | null | D | Abu Bakar Frozen Foods | Hydrabad | KCX72 | 3474K096 | email | 2018-02-20 | null | 2018-02-20 | over heating | 2017-06-24 | 2017-12-13 | null | null | null | 6 | Discharge valve ring got stuck in the stroke limitor due to machining burr. | null | null | null
2018-03-24 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hikal LimitedBharuch | Gujrat | KC84 | 330K48 | 2108482606 | 2018-03-19 | 119 | 2018-03-14 | low oil pressure | 2017-10-11 | 2018-01-29 | 1245 | null | null | 2 | Low oil pressure, scoring on c.shaft | null | closed | Replace c.shaft,bearings,oil pump assly
2018-03-24 | Trade Links | null | D | Abu Bakar Frozen Foods | Telangana | KCX42 | 3344K044 | 2085842508 | 2018-01-03 | null | 2017-12-11 | pressure gauge glass broken | 2017-02-18 | 2017-12-16 | 2 | null | null | 10 | Pressure gauge glass broken | null | closed | Pressure gauge 16 kg/cm2
2018-03-24 | Model Pneumatic Co | Punjab | D | Ssb Fresh Foods | Punjab | KCX2 | 3364K1054 | 2103322580 | 2018-03-03 | 52 | 2018-02-27 | shaft seal leakage | 2016-03-29 | 2016-10-03 | 1435 | null | null | 6 | Shaft seal assly leak | null | closed | Replace shaft seal assly and cover
2018-03-27 | Parag Marketing Services | null | D | Push Engineering | Pune | KCX3 | 3374K1757 | Mail | 2018-03-27 | null | 2018-03-27 | no paint at base frame bottom | 2018-03-13 | 2018-03-25 | ZH | null | null | 1 | Improper painting and No paint at base frame bottom | null | closed | Replaced base frame
2018-03-28 | Trade Links | null | D | Abu Bakar Frozen Foods | Telangana | KCX72 | 3474K096 | 2097102559 | 2018-02-08 | 46 | 2018-02-07 | abnormal noise | 2017-06-24 | 2017-12-18 | 96 | null | null | 6 | Delivery valve leakage | null | closed | Delivery valve
2018-03-28 | Geekay Pneumatic Pvt Ltd | null | D | Premier Exports | Kerala | KC31 | 343K1506 | 2090982578 | 2018-03-01 | 6059 | 2018-01-19 | discharge filter housing leak . | 2017-08-09 | 2017-10-10 | 600 | null | null | 2 | Discharge filter housing leak due to pipe crack at ferule side | null | closed | Replaced filter housing top
2018-03-28 | Tal Sales | null | E | Mollah Cold Storage | Bangladesh | KCX6 | 3394K940 & 941 | Email | 2018-03-26 | null | 2018-03-26 | kcx oil pump not working | 2017-12-19 | null | ZH | null | null | 3 | KCX oil pump bush wornout | null | closed | Replace oil pump
2018-03-28 | Parag Marketing Services | null | D | Paithan Mega Food Park Pvt Ltd | Paithan | PC2 | 331K2866 | 2096262556 | 2018-02-05 | 1940 | 2018-01-28 | pc2 oil pump tang broken | 2016-08-29 | 2018-01-29 | null | null | null | 17 | Replaced gear kit | null | closed | Gear kit
2018-03-29 | S M Refrigeration | null | D | Jagdamba Cold Storage | null | KCX6 | 3394K764 | null | null | 116 | 2018-02-22 | kcx oil pressure not develop | 2017-03-08 | 2017-05-05 | 36 | null | null | 2 | KCX oil pump element tang broken | null | closed | Replace pump element
2018-03-29 | S M Refrigeration | null | D | Parmeshwar Industries Limited | null | KCX6 | 3394K956 | null | null | 4206 | 2018-03-17 | kcx oil pressure not develop | 2017-12-25 | 2018-02-28 | 30 | null | null | 2 | KCX oil pump element tang broken | null | closed | Replace pump element
2018-03-29 | S M Refrigeration | null | D | Kiran Agro | Haryana | KCX4 | 3384K1433 | null | null | 122 | 2018-03-13 | oil pressure not buildup | 2017-01-15 | 2017-03-24 | 3143 | null | null | 2 | Oil pressure not developed due to pump element broken | null | closed | Replaced pump element
2018-03-29 | Cool Comfort Private Limited | West Bengal | D | Hsb Agro | null | KCX4 | 3384K1538 | null | null | 1143 | 2018-02-25 | shaft seal leakage | 2018-03-07 | 2017-04-29 | 1700 | null | null | 1 | Shaft seal leakge. | null | closed | Replace Shaft seal assly
2018-03-31 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX42 | 3444K049 | 2104362585 | 2018-03-06 | null | 2018-03-04 | abnormal noise | 2017-04-23 | 2017-09-16 | 1327 | null | null | 5 | Cylinder liner and piston rings worn out | null | closed | Cylinder liner
2018-03-31 | Kirloskar Pneumatic Co Ltd | null | D | Trm Hofler Ac PlantKpcl | Hadapsar | PC2 | 331K2926 | Email | 2018-03-20 | null | 2018-03-20 | heavy vibrations and leakage at discharge housing | 2017-06-22 | 2018-01-11 | ZH | null | null | 5 | Heavy vibrations and leakage from Discahrge filter housing | null | closed | null
2018-03-31 | Trade Links | Secunderabad | D | Pearl Beverages | null | KCX6 | 3394K004 | 2127402632 | 2018-03-28 | null | 2018-03-13 | hour meter not working | 2017-11-28 | 2018-03-16 | ZH | null | null | 3 | Hour meter not working | null | closed | Hour meter
2018-03-31 | Parag Marketing Services | null | D | Finolex Industries | null | KCX4 | 3384K1597 | 2102662587 | 2018-03-07 | 2187 | 2018-02-24 | kcx oil pump purging | 2017-04-21 | 2018-03-01 | ZH | null | null | 11 | KCX oil pump purging | null | closed | KCX oil pump
2018-03-31 | Morgan | null | E | Umer Daraz Cold Store | null | KCX6 | 3394K823 | null | 2018-03-23 | 596 | 2018-03-23 | kcx oil pump tang broken | 2017-07-01 | 2018-03-17 | ZH | null | null | 8 | Oil pump outer rotor tang broken | null | closed | Pump Elelment
2018-04-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | M/S Nufarm Foods | New Delhi | KC9 | 340K397 | 2129962640 | 2018-04-04 | 212996 | 2018-04-01 | abnormal noise from motor pulley | 2017-12-27 | 2018-03-20 | ZH | null | null | 3 | Abnormal Sound from motor pulley | null | closed | null
2018-04-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Upl Limited Unit5 | Baroda,Gujarat | KCX9 | KCX9AV200100001 | 2131702654 | 2018-04-09 | 213170 | 2018-03-29 | shaft seal leakage | 2017-06-04 | 2017-11-06 | 989 | null | null | 5 | Shaft seal leakage | null | closed | null
2018-04-22 | Trade Links | Secunderabad | D | The Krishna District Milk Producers Mutually Aided CoOperative Union Ltd | null | KCX9 | 3404K079 | 2135902667 | 2018-04-17 | 213590 | 2018-04-14 | tah8 valve adaptor broken in transit | 2017-11-24 | null | ZH | null | null | 5 | TAH8 Valve adaptor broken in transit | null | closed | null
2018-04-25 | Trade Links | null | D | Abu Bakar Frozen Foods | Telangana | KCX72 | 3474K096 | 2111882629 | 2018-03-27 | 211188 | 2018-03-25 | abnormal noise | 2017-06-24 | 2017-12-16 | 694 | null | null | 6 | Pistoon abnormal wearing due to insufficient wearing | null | closed | piston,liner,piston ring set
2018-04-25 | Cool Comfort Private Limited | West Bengal | D | Santima Cold Storage (P) Ltd | Bankura,West Bengal | KCX6 | 3394K947 | 2135902667 | 2018-04-17 | 213590 | 2018-04-08 | abnormal noise from compressor head. | 2017-12-20 | 2018-03-12 | 308 | null | null | 3 | Delivery valve leak | null | closed | null
2018-04-25 | Kalp Marketing | Gujrat | D | Sk Cold Storage | null | KC3 | 337K4643 | 2130742648 | 2018-04-06 | 213074 | 2016-09-15 | abnormal noise in cylinder 1 and low oil pressure | 2016-05-18 | 2016-09-15 | 2425 | null | null | 4 | ABNORMAL SOUND IN CYLINDER 1 AND LOW OIL PRESSURE | null | closed | null
2018-04-25 | Trade Links | null | D | Aziz Enterprises | Telangana | KCX42 | 3444K049 | 2130042642 | 2018-04-05 | null | 2018-03-31 | delivery valve leakage | 2017-04-23 | 2017-09-16 | 1495 | null | null | 5 | Delivery valve leak back | null | closed | Del valve assly
2018-04-25 | Kalp Marketing | Gujrat | D | Gautam Sheet Gruh | Madhya Pradesh | KCX3 | 3374K1288 | 2136122669 | 2018-04-17 | 261 | 2018-02-07 | discharge valve leakage | 2017-02-03 | 2017-03-03 | 2371 | null | null | 1 | Piston touches to delivery valve,replaced delivery vlave,liner, piston, piston ring set, bearing | null | closed | null
2018-04-25 | Kalp Marketing | Gujrat | D | Raunak Ice & Cold Storage | Gujrat | KCX42 | 3444K075 | 2130702647 | 2018-04-06 | 163 | 2018-02-19 | high oil consumption | 2017-11-04 | 2017-11-16 | 21434 | null | null | 1 | High oil consumption 5.6 ltr in 3 days | null | closed | piston ring sets
2018-04-25 | Hss Solution Pvt Ltd | null | D | Santosh Kumar Enterprises | Rajastan | KCX1 | 3354K053 | 2109702613 | 2018-03-20 | 83 | 2018-03-18 | hour meter not working | 2017-12-13 | 2018-03-19 | ZH | null | null | 3 | Hour meter not working | null | closed | Hour meter
2018-04-25 | S M Refrigeraion Pvt Ltd | null | D | M/S Narendra Cold Storage | Haryana | KCX2 | 3364K1375 | 2132902659 | 2018-04-11 | 213290 | 2018-03-07 | hour meter not working | 2017-09-24 | 2018-03-07 | ZH | null | null | 6 | Hour meter not working | null | closed | Hour meter
2018-04-25 | Trade Links | Secunderabad | D | Sai Marine Exports Pvt LtdNollore | Andhra Pradesh | KCX4 | 3384K1813 | 2127742644 | 2018-04-05 | 212774 | 2018-03-24 | k5 valve leakage | 2018-01-21 | 2018-03-24 | ZH | null | null | 2 | K5 Valve leak | null | closed | K5 valve
2018-04-25 | Kalp Marketing | Gujrat | D | Sun Exports | Gujrat | KCX42 | 3444K073 | 2129842639 | 2018-04-04 | 212984 | 2018-02-18 | oil pressure not buildup | 2017-10-07 | 2017-10-25 | 1545 | null | null | 1 | Business promotion -- Cut outs setting done wrong - Pl refer received FRR and FSR , We also not to call such components at KPCL for further analysis (As remark by previous approval authority for to call back ) . | null | closed | oil pump element
2018-04-25 | Trade Links | Secunderabad | D | Sree Harsha Cold Storage | Telangana | KCX2 | 3364K1463 | 2131022650 | 2018-04-07 | null | 2018-04-05 | oil pressure not buildup | 2017-12-29 | 2018-03-03 | 60 | null | null | 3 | Oil pump element tang broken | null | closed | Pump element
2018-04-25 | Kalp Marketing | Gujrat | D | Jankeshwar Cold Storage | null | KCX4 | 3384K1928 | 2131162653 | 2018-04-07 | 213116 | 2018-03-28 | oil pressure not buildup | 2018-03-24 | 2018-03-28 | 24 | null | null | 1 | Business promotion -- Cut outs setting wrong i.e 0.5 and 0.7kg/cm2 - Pl refer received FRR and FSR , We also not to call such components at KPCL for further analysis (As remark by previous approval authority for to call back ) . | null | closed | oil pump element
2018-04-25 | Cool Comfort Private Limited | West Bengal | D | Baba Biswakarma Multipurpose Cold Storage (P) Ltd | null | KCX6 | 3394K1028 | 2138742676 | 2018-04-19 | 213874 | 2018-04-02 | oil pressure not buildup | 2018-02-27 | 2018-03-17 | 330 | null | null | 1 | Business promotion- Discussed with Mr.Sujit Mitra. Liquid entry found. -Refer mail from Gubyad Vinayak R. on dated 21 Apr18 | null | closed | oil pump element
2018-04-25 | Kalp Marketing | Gujrat | D | Aman Enterprises | New Delhi | KCX4 | 3384K1763 | 2128382646 | 2018-04-06 | 212838 | 2018-03-20 | oil pressure not buildup | 2017-12-16 | 2018-01-26 | 345 | null | null | 1 | Business promotion --Discussed with Mr. Mithil gandhi . Sudden power failure , may be comp dry run.--Refer mail from Gubyad Vinayak on dated 10 April18. | null | closed | oil pump element
2018-04-25 | Cool Comfort Private Limited | West Bengal | D | Sreenagar Cold Storage (P) Ltd | null | KCX4 | 3384K1833 | 2136122669 | 2018-04-17 | 213612 | 2018-04-04 | oil pressure not developing & loading, unloading problem | 2018-02-02 | 2018-04-02 | 7 | null | null | 2 | Business promotion -- Seems compressor dry run or filter not changed after 5hrs | null | closed | oil pump element
2018-04-25 | Model Pneumatic Co | null | D | Ssb Fresh Foods | null | KCX2 | 3364K1054 | 2095062551 | null | 39 | 2017-12-24 | shaft seal leakage | 2016-03-29 | 2016-10-03 | 1334 | null | null | 6 | Shaft seal assly leak | null | closed | Shaft seal assly
2018-05-25 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Agra Mai Sadabad Hatgras | Uttar Pradesh | KCX6 | 3394K963 | 2111462633 | 2018-03-30 | 53 | 2018-03-12 | abnormal noise | 2017-12-31 | 2018-02-22 | ZH | null | null | 2 | Abnormal noise from cylinder due to delivery valve leakage. Claned discharge valve. | null | closed | Replaced piston & piston ring set
2018-05-25 | Trade Links | Secunderabad | D | Abu Bakar Frozen Foods | Telangana | KCX72 | 3474K054 | 2145862711 | 2018-05-07 | null | 2018-05-03 | abnormal noise | 2017-01-10 | 2017-12-14 | 112 | null | null | 11 | Abnormal wearing on one side to one liner and piston ring set. | null | closed | Replaced liner & Ring set
2018-05-25 | Kalp Marketing | Gujrat | D | Mount Everest Breweries Limited | Madhya Pradesh | KCX4 | 3384K1400 | 2149842738 | 2018-05-19 | 145 | 2018-05-15 | breakdown of compressor | 2016-12-24 | 2017-05-19 | 1100 | null | null | 5 | Flywheel wobbled. Compressor was installed by OEM amd not fitted centre bolt during the commissioning it was dennie to re open for check of coupling fitment. | null | closed | Replaced Flywheel , Crankshaft , Oil pump element & Bearings
2018-05-25 | Kalp Marketing | Gujrat | D | Virat Cold Storage | Gujrat | KCX3 | 3374K1721 | 2142882698 | 2018-04-30 | 301 | 2018-04-10 | commissioning for kcx3 | 2018-02-20 | 2018-04-11 | ZH | null | null | 2 | Everything is ok As per FSR No.301 dtd 10-04-18. But in FRR mentioned one OP cut out requirement. | null | closed | OP Cut out
2018-05-25 | Hss Solution Pvt Ltd | null | D | Maa Pitambara Cold Storage | Rajastan | KCX6 | 3394K1008 | 2135422665 | 2018-04-16 | 96 | 2018-04-12 | high oil consumption | 2018-02-12 | 2018-03-04 | 595 | null | null | 1 | Replaced piston ring sets 3 nos. Root cause not found | null | closed | Replaced 3 Piston ring set
2018-05-25 | Kalp Marketing | Gujrat | D | Ambika Ice Factory | Gujrat | KCX2 | 3364K1403 | 2147502718 | 2018-05-11 | 324 | 2018-05-08 | high oil consumption | 2017-10-13 | 2018-01-01 | 818 | null | null | 3 | Replaced piston ring sets and compressor under observation. | null | closed | Replaced piston ring set
2018-05-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX4 | 3384K1267 | 2140482679 | 2018-04-21 | 214048 | 2018-04-10 | housing manifold leakage from plug | 2016-08-27 | 2017-04-28 | 500 | null | null | 8 | Oil spread from plug. | null | closed | Replaced manifold & Plug 1/2
2018-05-25 | Cool Comfort Private Limited | West Bengal | D | Prakash Poddar Himghar Pvt Ltd | West Bengal | KCX4 | 3384K1842 | 2142262692 | 2018-04-27 | 1530 | 2018-04-23 | loading unloading and oil pressure not develop | 2018-02-07 | 2018-03-12 | 516 | null | null | 1 | Oil pump small gear bush wornout with cover shaft causes driving tang broken. | null | closed | Pump element replaced
2018-05-25 | Cool Comfort Private Limited | West Bengal | D | DG Cold Storage | West Bengal | KCX4 | 3384K1864 | 2141482687 | 2018-04-25 | 1951 | 2018-04-21 | oil pressure not buildup | 2018-02-19 | 2018-03-11 | 163 | null | null | 1 | Oil pump small gear bush wornout with cover shaft causes driving tang broken. | null | closed | Replaced pump element
2018-05-25 | Cool Comfort Private Limited | West Bengal | D | Alicha Cold Storage | West Bengal | KCX4 | 3384K1838 | 2140942682 | 2018-04-24 | 1098 | 2018-04-21 | oil pressure not buildup | 2018-02-05 | 2018-03-16 | 745 | null | null | 1 | Oil pump small gear bush wornout with cover shaft causes driving tang broken. | null | closed | Replaced pump element
2018-05-25 | Trade Links | Secunderabad | D | Aiswarya Impex | Andhra Pradesh | KCX93 | 3485K003 | 2141762689 | 2018-04-26 | null | 2018-04-06 | plunger is not free in solenoid valve | 2017-03-13 | 2018-04-27 | ZH | null | null | 12 | Cyl no. 4,1,3,6,7&11 not unload due to solenoid valve plunger not free | null | closed | Replaced solenoid valve 3 nos
2018-05-25 | Model Pneumatic Co | null | D | Godrej Consumer Product Ltd | J&K | PC2 | 331K2912 | 2143962701 | 2018-05-02 | 70 | 2018-03-25 | shaft seal leakage | 2017-05-16 | 2017-10-14 | 94 | null | null | 5 | Shaft seal leakage | null | closed | Replaced shaft seal assly
2018-05-25 | Kalp Marketing | Gujrat | D | Shakti Polyweave Pvt Ltd | Gujrat | KCX2 | 3364K1328 | 2142962699 | 2018-04-30 | 190 | 2018-04-03 | shaft seal leakage | 2017-05-20 | 2018-02-13 | ZH | null | null | 9 | Seal leakage due to jammed . | null | closed | Rectified and replaced Oring kit
2018-05-25 | Multivista Global Pvt Ltd | null | D | Abt Industries Ltd | Tamil Nadu | KCX4 | 3384K1618 | 2142862695 | 2018-04-30 | null | 2018-04-26 | suct pr gauge & op cutout not working | 2017-05-21 | 2018-04-27 | ZH | null | null | 11 | Suction pressure gauge error & OP cut out not working. | null | closed | Replaced Suct Pr Gauge & OP Cut out.
2018-05-25 | Fridge House | null | D | Food And Bio Tech Engineerings Pvt Ltd | Karnataka | KCX4 | 3384K1567 | 2141962691 | 2018-04-26 | null | 2018-04-21 | td solenoid valve not working | 2017-03-21 | 2017-11-22 | ZH | null | null | 7 | NO Solenoid valve not working due to there is problem in magnet within 10 Hrs. | null | closed | Replaced solenoid valve
2018-05-30 | Cool Comfort Private Limited | West Bengal | D | Radha Krishna & Pillack Ice Factory | null | KCX2 | 3364K1385 | 2143102700 | 2018-04-30 | 1501 | 2018-04-20 | tah8 valve adaptor broken in transit | 2017-09-12 | 2018-04-21 | ZH | null | null | 6 | TAH8 Valve adaptor broken in transit | null | closed | null
2018-06-11 | Kalp Marketing | Gujrat | D | Megent Electric | Veraval, Gujarat | KCX51 | 3454K069 | Mail | 2018-06-11 | null | 2018-06-11 | suction str welding leakage | 2018-04-20 | 2018-06-11 | ZH | null | null | 2 | During pressure test at site pin hole in the welding on the joint at suction strainer is detected. | null | closed | null
2018-06-16 | Model Pneumatic Co | Punjab | D | Shl Agro Foods | Punjab | KCX51 | 3454K038 | 2144222704 | 2018-05-02 | 83 | 2018-04-26 | abnormal noise | 2017-06-26 | 2017-12-06 | 284 | null | null | 6 | Abnormal sound from HP Cylinder , Piston had deep scrach marks and big gap between piston and liner. | null | closed | Replaced Piston , Gudgeon pin and Bearing bush.
2018-06-16 | Kalp Marketing | Gujrat | D | Krishna Ice Plant | Gujrat | KCX4 | 3384K1626 | 2144042702 | 2018-05-02 | 295 | 2018-04-21 | cylinder overheating | 2017-06-11 | 2017-08-03 | 5180 | null | null | 2 | 01 no. Cylinder overheating due to delivery valve leakage. | null | closed | Replaced delivery valve assembly 01 no.
2018-06-16 | S M Refrigeraion Pvt Ltd | null | D | Gautam Cold Storage & Ice Factory | Uttar Pradesh | KCX4 | 3384K1847 | 2141402685 | 2018-04-25 | null | 2018-03-29 | cylinder overheating due to delivery valve leakage. | 2018-02-10 | 2018-03-23 | ZH | null | null | 1 | Within 22 hours , Cylinder overheating due to delivery valve leakage . | null | closed | Replaced liner , Piston , Piston ring set , delivery valve assly , spring and ORV . 02 Nos each
2018-06-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Srf Ltd Bharuch | Gujrat | KCX6 | 3394K820 | 2148622729 | 2018-05-16 | 199 | 2018-05-01 | delivery valve leakage | 2017-07-23 | 2018-04-26 | ZH | null | null | 9 | Delivery valve leakage within 4 hours. | null | closed | Replaced valve kit.
2018-06-16 | Trade Links | Secunderabad | D | Ss Industries | Andhra Pradesh | KCX4 | 3384K1894 | 2150202766 | 2018-05-30 | null | 2018-05-07 | gas leakage | 2018-03-03 | 2018-05-09 | ZH | null | null | 2 | Within 8 hours , gas leakage from pressure gauge adaptor. | null | closed | Replaced feamale run tee
2018-06-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Km Fisheries | Kerala | KCX72 | 3474K104 | 2146602713 | 2018-05-08 | 6065 | 2018-05-04 | kcx pump air purging | 2017-06-21 | 2017-09-15 | 1200 | null | null | 3 | Purging problem at initial starting of compressor. Replaced all Orings & Gasket but problem not resolved. | null | closed | Replaced pump assembly LC 07 17 287
2018-06-16 | S M Refrigeraion Pvt Ltd | null | D | Shri Mahaveer Clod Storage & Agro Industries | Uttar Pradesh | KCX4 | 3384K1879 | 2150462743 | 2018-05-22 | null | 2018-05-12 | oil pressure not buildup | 2018-02-27 | 2018-04-11 | 44 | null | null | 2 | Oil pump element tang broken | null | closed | Replaced pump element
2018-06-16 | S M Refrigeraion Pvt Ltd | null | D | Sterling Agro Industries Ltd | Haryana | KCX6 | 3394K1009 | 2152042757 | 2018-05-28 | 8131 | 2018-05-19 | oil pressure not buildup | 2018-02-13 | 2018-04-06 | 871 | null | null | 2 | Oil pump element tang broken | null | closed | Replaced pump element
2018-06-16 | Cool Comfort Private Limited | West Bengal | D | Dooars Infra Projects (P) Ltd | West Bengal | KCX6 | 3394K921 | 2157562783 | 2018-06-11 | 1618 | 2018-06-10 | oil pressure not buildup | 2017-11-25 | 2018-03-12 | 564 | null | null | 4 | Oil pump inner rotor bush seized in the cover due to driving gear shaft broken. | null | closed | Replaced pump element
2018-06-16 | Cool Comfort Private Limited | West Bengal | D | D K Ice & Cold Storage | Bihar | KCX6 | 3394K1014 | 2157622784 | 2018-06-11 | 1537 | 2018-06-05 | oil pressure not buildup | 2018-02-16 | 2018-05-02 | 106 | null | null | 3 | Oil pump inner rotor bush seized in the cover due to driving gear shaft broken. | null | closed | Replaced pump element
2018-06-16 | Cool Comfort Private Limited | West Bengal | D | Dollon'S Food Products (P) Ltd | West Bengal | KCX6 | 3394K765 | 2148942730 | 2018-05-16 | 1676 | 2018-05-10 | oil pressure not buildup | 2017-03-10 | 2018-04-23 | 120 | null | null | 1 | Oil pump inner rotor bush seized in the cover due to driving gear shaft broken. | null | closed | Replaced pump element
2018-06-16 | Trade Links | Secunderabad | D | Vamsi Ice Factory | Andhra Pradesh | KCX4 | 3384K1962 | 2147222715 | 2018-05-10 | 85 | 2018-05-06 | oil pressure not buildup | 2018-05-07 | 2018-05-09 | ZH | null | null | 0 | Within 3 hours , oil pressure not develop/drop due to element shaft broken | null | closed | Replaced Pump element
2018-06-16 | S M Refrigeraion Pvt Ltd | null | D | Shri Radha Ballabh Cold Storage | Uttar Pradesh | KCX6 | 3394K961 | 2141262684 | 2018-04-25 | 4048 | 2018-03-09 | oil pressure not buildup | 2017-12-29 | 2018-02-23 | ZH | null | null | 2 | Within 19 hours , oil pressure not builtup due to element shaft broken. | null | closed | Replaced pump element
2018-06-16 | S M Refrigeraion Pvt Ltd | null | D | Udai Cold Storage | Uttar Pradesh | KCX4 | 3384K1825 | 2152082755 | 2018-05-28 | null | 2018-04-18 | oil pressure not buildup | 2018-01-30 | 2018-04-13 | 594 | null | null | 3 | Oil not develop due to lement broken | null | closed | Replaced pump element
2018-06-16 | Multivista Global Pvt Ltd | null | D | Nila Sea Foods Exports | Tamil Nadu | KCX3 | 3374K1747 | 2151662752 | 2018-05-25 | null | 2018-05-08 | solenoid valve not working | 2018-03-05 | 2018-05-10 | ZH | null | null | 2 | Within 10 hours , Piston no.1 solenoid valve not working , spring damaged. | null | closed | Replaced solenoid valve
2018-06-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Accelerated Freeze Drying Co Ltd | Kerala | KCX4 | 3384K1635 | 2151862754 | 2018-05-26 | 6165 | 2018-05-19 | suction pressure gauge error | 2017-06-18 | 2018-05-19 | ZH | null | null | 11 | Within 12 houres , Pressure gauge error /out by 1.5Kg/cm2. | null | closed | Replaced suction pressure gauge
2018-06-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ruchi Food Llb | Vadodara , Gujarat | KCX21 | 3424K046 | 2147862728 | 2018-05-16 | 8 | 2018-04-26 | suction pressure gauge error | 2017-08-29 | 2018-04-27 | ZH | null | null | 8 | Suction pressure gauge error of 1 Kg/cm2 observed before comm. | null | closed | Replaced Pr. Gauge 16.00Kg/cm2.
2018-06-16 | Cool Comfort Private Limited | West Bengal | D | Kosi Dugdh Utpadak Sahakari Sangh Ltd | Bihar | KCX6 | 3394K707 | 2142942696 | 2018-04-30 | 1322 | 2018-04-18 | th8 valve adaptor broken | 2017-01-11 | 2018-04-18 | ZH | null | null | 14 | Observed TAH8 Valve adaptor broken . Compressor under commissioning | null | closed | Replaced adaptor & TAH8 Valve
2018-06-17 | Model Pneumatic Co | Punjab | D | Shl Agro Foods | Punjab | KCX51 | 3454K038 | 2095002552 | 2018-02-02 | 44 | 2018-01-22 | delivery valve leakage | 2017-06-26 | 2017-12-06 | ZH | null | null | 6 | Delivery valave leakage. | null | closed | Replaced Delivery valave leakage.
2018-06-17 | Cool Comfort Private Limited | West Bengal | D | B-One Buisness House Pvt Ltd | Bhubaneswar Orissa | KCX72 | 3474K144 | Email | 2018-05-30 | null | null | hp cylinder orv plug missing | 2018-01-08 | 2018-05-22 | ZH | null | null | 2 | HP Cylinder ORV plug misssing-2nos. | null | closed | null
2018-06-17 | Model Pneumatic Co | Punjab | D | Shahpur Cold Storage | Punjab | KC4 | 338K5580 | 2158622795 | 2018-06-15 | 92 | 2018-05-15 | oil lifting | 2017-01-20 | 2017-03-04 | 3815 | null | null | 2 | Piston rings worn-out , after replacement there was no oil carry over. | null | closed | Replaced 4 set of piston ring set
2018-06-17 | S M Refrigeraion Pvt Ltd | null | D | Parmeshwar Industries Pvt Ltd | Uttar Pradesh | KCX6 | 3394K956 | 2154522773 | 2018-06-04 | null | 2018-05-28 | oil pressure not buildup | 2017-12-25 | 2016-02-28 | 302 | null | null | 2 | Pump element broken | null | closed | Replaced pump element
2018-06-17 | Model Pneumatic Co | Punjab | D | Mansa Cold Storage | Punjab | KCX3 | 3374K1652 | 2107882604 | 2018-03-16 | 59 | 2018-03-09 | oil pressure not buildup | 2018-01-07 | 2018-02-23 | 60 | null | null | 1 | No oil pressure due to drive gear broken. | null | closed | Replaced pump element.
2018-06-17 | S M Refrigeraion Pvt Ltd | null | D | Patanjali Food & Herbals Haridwar | Uttarakhand | KCX4 | 3384K1529 | 2149862740 | 2018-05-19 | 8123 | 2018-05-07 | op cut out not working | 2017-02-28 | 2018-04-25 | ZH | null | null | 14 | OP cut-out not working observed while load testing | null | closed | Replaced OP Cutout
2018-06-23 | Parag Marketing Services | Pune | D | Rich Graviss Products PvtLtd | Pune | KC63 | 346K248 | 2159382808 | 2018-06-20 | 2357 | 2018-04-03 | low oil pressure | 2017-03-01 | 2017-07-27 | 497 | null | null | 4 | Due to lubrication failure compressor crank shaft and bearing damaged. | null | closed | Replaced Crankshaft , all bearings and pump element.
2018-07-08 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Uday Cold Storage | Uttar Pradesh | KCX9 | 3404K086 | 2158042792 | 2018-06-14 | null | 2018-05-29 | abnormal noise | 2018-01-16 | 2018-03-08 | 858 | null | null | 2 | Delivery valve leakage | null | closed | Replace cylinder liner, del. Valve,piston ring set
2018-07-08 | S M Refrigeraion Pvt Ltd | null | D | Shri Mahashay Bhikam Singh Cold Storage | Uttar Pradesh | KCX6 | 3394K969 | 2162702835 | 2018-06-30 | null | null | cylinder overheating | 2018-01-06 | 2018-02-24 | 5118 | null | null | 1 | Delivery valve leakage | null | closed | replace del. Valve
2018-07-08 | Fridge House | null | D | B P Uchil & Sons | Mangalore, Karnataka | KCX4 | 3384K1779 | 2159122802 | 2018-06-18 | null | 2018-06-05 | high oil consumption | 2017-12-25 | 2018-03-06 | 1662 | null | null | 3 | Visited by Mr. VRG , replaced liner,piston,piston ring set, valve kit, bush connecting rod | null | closed | Replaced liner,piston,piston ring set, valve kit, bush connecting rod
2018-07-08 | Gargi Engineering Enterprices Pvt Ltd | null | D | Val Organics | Valsad | KCX63 | 3464K006 | 2158982798 | 2018-06-16 | 24 | 2018-06-11 | pressure gauge out | 2017-08-07 | 2018-06-12 | 4 | null | null | 10 | Suction pressure gauge replaced | null | closed | Suction Pressure gauge
2018-07-08 | Parag Marketing Services | Pune | D | Shukla Dugdhalay | Dhule | KCX2 | 3364K1368 | 2159262803 | 2018-06-19 | 2321 | 2018-05-08 | solenoid valve coil not working | 2017-07-26 | 2018-04-14 | ZH | null | null | 9 | Replaced sol. Valve coil | null | closed | Replaced coil
2018-07-20 | Trade Links | Secunderabad | D | Svr Laboratorie | Telangana | KCX21 | 3424K051 | 2149922809 | 2018-06-20 | null | 2018-05-14 | abnormal noise | 2017-11-05 | 2018-01-12 | 500 | null | null | 2 | Replaced crank shaft,conrod,bearings | null | closed | Replaced crank shaft,conrod,bearings
2018-07-20 | Trade Links | Secunderabad | D | Devi Sea Foods | null | KCX3 | 3374K1646 | 2148322725 | 2018-05-11 | null | 2018-05-07 | abnormal noise | 2018-01-03 | 2018-01-22 | 1480 | null | null | 1 | delivery valve leak back | null | closed | Piston piston ring set, cyl. Liner,buffer spring, bearing bush
2018-07-20 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KC63 | 346K262 | 2137602671 | 2018-04-19 | null | 2018-04-16 | abnormal noise | 2017-10-04 | 2018-03-10 | ZH | null | null | 5 | HP Cylinder delevery valve leakage due to valve ring was stuckup and hence cylinder seize within 15 Hrs. | null | closed | Replaced Piston , liner , piston rings and delivery valve kit.
2018-07-20 | Trade Links | Secunderabad | D | Raghava Constructions | Telangana | KCX4 | 3384K1510 | 2148402726 | 2018-05-14 | null | 2018-05-06 | abnormal noise and oil consumption | 2017-02-21 | 2018-02-12 | 125 | null | null | 12 | Piston and liner wearout | null | closed | piston and cylinder liner
2018-07-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Chenitan Colour Chem | Chembur | KCX3 | 3374K1428 | 2165782841 | 2018-07-06 | 193 | 2018-06-08 | cylinder overheating | 2017-05-05 | 2018-01-27 | 2500 | null | null | 8 | Replaced delivery valve kit | null | closed | Delivery valve kit
2018-07-20 | Fridge House | null | D | B P Uchil & Sons | Mangalore, Karnataka | KCX4 | 3384K1779 | 2147462759 | 2018-05-29 | null | 2018-05-01 | high oil consumption | 2017-12-25 | 2018-03-06 | 1035 | null | null | 1035 | Found piston liner & piston rings worn out | null | closed | Replaced piston, piston, ring and liner
2018-07-20 | Multivista Global Pvt Ltd | null | D | Apm Terminal India Pvt Ltd | Tamil Nadu | KC63 | 3394K3438 | 2154882774 | 2018-06-04 | null | 2018-05-31 | kc63 compressor loading unloading problem | 2017-10-14 | 2018-04-26 | 20 | null | null | 6 | Sol. Vlave not working | null | closed | null
2018-07-20 | S M Refrigeration | null | D | New Dashmesh Ice Factory | Uttar Pradesh | KCX3 | 3374K1770 | 2160602815 | 2018-06-25 | 4285 | 2018-06-05 | kcx pump air purging | 2018-03-19 | 2018-05-21 | 385 | null | null | 2 | oil pressure problem /Purging | null | closed | Replaced oil pump assly
2018-07-20 | Trade Links | Secunderabad | D | Raghava Constructions | Telangana | KCX4 | 3384K1579 | 2152882763 | 2018-05-30 | null | 2018-05-06 | oil consumption | 2017-03-29 | 2018-02-12 | 100 | null | null | 10 | piston seized, abnormal wearing of liner | null | closed | replaced piston, liner,Gudgeon pin, piston ring set
2018-07-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Blue Circle Organic Pvt Ltd | Thane | KCX3 | 3374K1271 | 2147302716 | 2018-05-11 | 21 | 2018-05-07 | oil carry over | 2017-01-28 | 2017-09-15 | 3000 | null | null | 7 | replaced piston piston ring set and VLD orings | null | closed | Replaced piston1no,piston ring 3nos.,VLD orings
2018-07-20 | S M Refrigeration | null | D | Swadesh Milk Products Pvt Ltd | null | KCX4 | 3384K1876 | 2164602837 | 2018-07-04 | 4287 | 2018-06-09 | oil pressure not buildup | 2018-02-27 | 2018-05-29 | 4287 | null | null | 3 | Replaced KCX pump element | null | closed | KCX oil pump element
2018-07-20 | S M Refrigeration | null | D | Parmeshwar Industries Pvt Ltd | Uttar Pradesh | KCX6 | 3394K956 | 2162202829 | 2018-06-29 | 4296 | 2018-06-23 | oil pressure not buildup | 2017-12-25 | 2018-02-28 | 514 | null | null | 2 | Oil pump element tang broken | null | closed | Replaced Oil pump element
2018-07-20 | Trade Links | Secunderabad | D | Munaga Chennaih Cold Storage | Andhra Pradesh | KCX3 | 3374K1609 | 2148382732 | 2018-05-17 | null | 2018-04-30 | oil pressure not buildup | 2017-12-08 | 2018-01-05 | 877 | null | null | 1 | oil pump elelment wear out and OPR ball stuckup | null | closed | Replaced KCX oil pump assly
2018-07-20 | Trade Links | Secunderabad | D | Venkata Krishna Cold Storage | Andhra Pradesh | KCX2 | 3364K1534 | 2149722765 | 2018-05-30 | null | 2018-05-06 | pressure gauge error | 2018-03-17 | 2018-07-10 | 4 | null | null | 4 | Pressure gauge shows vaccume | null | closed | Replaced Pr. Gauge 16.00Kg/cm2.
2018-07-20 | Trade Links | Secunderabad | D | Sri Padmpujitha Ice Factory | Andhra Pradesh | KCX6 | 3394K1040 | 2146162712 | 2018-05-07 | 82 | 2018-04-27 | shaft seal leakage | 2018-03-09 | 2018-03-30 | 611 | null | null | 1 | FW side main bearing werout | null | closed | Replaced bearing
2018-07-20 | Multivista Global Pvt Ltd | null | D | Vedam Milk Products | Tamil Nadu | KCX2 | 3364K1308 | 2141022683 | 2018-04-24 | null | 2018-02-07 | shaft seal leakage | 2017-04-30 | 2017-07-07 | 665 | null | null | 15 | Shaft seal assembly leakage | null | closed | Shaft seal assly replaced
2018-07-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Jay Narayan Cold Strorage | Gujrat | KCX4 | 3384K1780 | 2170422867 | 2018-07-17 | 197 | 2018-07-09 | solenoid valve not working | 2017-12-26 | 2018-02-19 | 395 | null | null | 2 | TDV valve not working properly | null | closed | Replaced Sol.Valve
2018-07-30 | Fridge House | null | D | Hikal Ltd | Karnataka | KCX84 | 3305K001 | 2148542758 | 2018-05-29 | null | 2018-05-15 | cyl overheating due to dv leakage | 2017-12-02 | 2018-04-17 | 38 | null | null | 4 | Cyl no.3 overheat due to DV leakage. | null | closed | Replaced DV assembly
2018-07-30 | Trade Links | Secunderabad | D | Anand Enterprises Pvt Ltd | Andhra Pradesh | KCX93 | 3485K015 | 2157502794 | 2018-06-15 | null | 2018-06-01 | cyl overheating due to dv leakage | 2018-01-21 | 2018-06-08 | 8 | null | null | 5 | Cyl. No. 4 HP overheating due to delivery valve assembly leakage. Found abnormal sound from cylinder and damage of piston , piston rings , buffer spring , valave kit. | null | closed | Replaced piston , piston rings , buffer spring , valave k
2018-07-30 | Cool Comfort Private Limited | West Bengal | D | Zakariya Agro Pvt Ltd | Bihar | KCX4 | 3384K1624 | 2166542847 | 2018-07-07 | 1546 | 2018-06-28 | high oil consumption | 2017-05-31 | 2017-11-07 | 1646 | null | null | 6 | Damage of one cylinder cylinder & delivery valve leakage | null | closed | Replaced liner , piston , piston ring set gudgeon pin , bearing bushes
2018-07-30 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KC84 | 330K46 | Email | 2018-07-04 | null | 2018-07-04 | incorrect piping sequence | 2018-03-04 | 2018-07-06 | ZH | null | null | 4 | Piping sequence is as per KC93 instead of KC84 | null | closed | Replaced piping
2018-07-30 | Kalp Marketing | Gujrat | D | Vardhan Cold Storage | Madhya Pradesh | KCX4 | 3384K1382 | 2161962822 | 2018-06-28 | 707 | 2018-06-19 | knocking sound due to piston touches to dv | 2016-12-17 | 2017-02-18 | 1431 | null | null | 2 | Piston touches to delivery valve also liner tap bolts broken. | null | closed | Replaced liner assly spares
2018-07-30 | Kirloskar South East Asia Co Ltd | Thailand | E | Tharathip | Thailand | KCX9 | 3404K048 | Email | 2018-07-10 | null | 2018-07-10 | paint peel off | 2017-01-01 | 2018-07-01 | ZH | null | null | 19 | Paint peel off at cylinder head covers | null | closed | Replaced cylinder head covers
2018-07-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Giriraj Ice Factory | Gujrat | KCX4 | 3384K1958 | 2165862843 | 2018-07-06 | 194 | 2018-07-06 | pump element broken | 2018-04-28 | 2018-05-01 | 82 | null | null | 1 | Oil pressure issue due to element broken | null | closed | Replaced Oil pump element
2018-07-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX4 | 3484K1267 | 2165762842 | 2018-07-06 | 216576 | 2018-06-18 | shaft seal leakage | 2016-08-27 | 2017-04-28 | 6500 | null | null | 8 | Shaft seal leakage , Replaced | null | closed | Shaft seal assly replaced
2018-08-01 | Parag Marketing Services | null | D | Sarda Dairy And Food Products | Raipur, Chhatisgarh | KCX2 | 3364K1536 | Email | 2018-08-06 | null | 2018-08-06 | crank case weld leak at discharge pipe | 2018-03-17 | 2018-06-06 | PC | null | null | 3 | leak from dischrge pipe welding run | null | closed | null
2018-08-01 | Gargi Engineering Enterprices Pvt Ltd | null | D | HN Indigoes PvtLtdNavsari | Gujrat | KCX3 | 3374K1791 | Email | 2018-07-01 | null | 2018-08-11 | wrong sequence to lp cutout wiring done 5,4,2 instead of 4,5,2 | 2018-04-10 | 2018-06-29 | ZH | null | null | 2 | Wiring sequence wrong | null | closed | null
2018-08-12 | Parag Marketing Services | null | D | Lupin Limited | Ankleshwar Gujarat | KC84 | 330K45 | Email | 2018-08-08 | null | 2018-08-08 | incorrect piping sequence | null | null | ZH | null | null | null | Piping sequence is as per KC93 instead of KC84 | null | closed | null
2018-08-19 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX72 | 3474K156 | Email | 2018-08-16 | null | 2018-08-16 | 1.crankcase heater fouling to support of intermediate bearing housing 2. connecting rod and cap sr. no. not in same side 3.flywheel bore oversize. | 2018-01-30 | 2018-08-14 | ZH | null | null | 7 | 1.Crankcase heater fouling to support of intermediate bearing housing 2. connecting rod and cap sr. no. not in same side 3.Flywheel bore oversize. | null | closed | Flywheel
2018-08-19 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX51 | 3454K060 | Email | 2018-08-16 | null | 2018-08-16 | crankcase heater fouling to stiffning plate | 2018-02-19 | 2018-08-14 | ZH | null | null | 6 | Stiffning plate position shifted towards bottom hence fouling heater | null | closed | null
2018-08-19 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX51 | 3454K058 | Email | 2018-02-18 | null | 2018-08-16 | crankcase heater fouling to stiffning plate | 2018-02-18 | 2018-08-14 | ZH | null | null | 6 | Stiffning plate position shifted towards bottom hence fouling heater | null | closed | null
2018-08-21 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2870 | 2018-07-18 | 217068 | 2018-07-16 | abnormal noise | 2017-04-23 | 2017-09-18 | 3371 | null | null | 5 | Delivery valve leak, needle roller bearing free at one side | null | closed | null
2018-08-21 | Kalp Marketing | Gujrat | D | Om Cold Storage | Gujrat | KCX3 | 3374K1714 | 2875 | 2018-07-21 | 217198 | 2018-07-07 | kcx oil pump element tang broken | 2018-02-18 | 2018-07-03 | PC | null | null | 5 | pump element tang broken-replaced element | null | closed | null
2018-08-21 | Parag Marketing Services | null | D | Jain Farma Fresh Foods Ltd | Jalgaon | KCX21 | 3424K043 | 2879 | 2018-07-24 | 217250 | 2018-06-09 | knocking / abnormal sound | 2017-07-31 | 2018-05-26 | PC | null | null | 10 | piston siezed del. Valve leak, buffer spring height shrunk | null | closed | null
2018-08-21 | Kalp Marketing | Gujrat | D | Milky Milk Processes | Gujrat | KCX3 | 3374K1341 | 2863 | 2018-07-16 | 217002 | 2018-07-10 | low oil pressure | 2017-02-27 | 2018-07-06 | PC | null | null | 17 | Oil pressure regulator in jam condition | null | closed | null
2018-08-21 | Parag Marketing Services | null | D | Modern Agro | Wagholi | KCX31 | 3434K0054 | 2877 | 2018-07-23 | 217214 | 2018-07-17 | overheating of cylinder | 2017-07-28 | 2017-10-04 | 1499 | null | null | 3 | delivery valve leakage | null | closed | null
2018-08-21 | Trade Links | null | D | Sai Ice Factory | Andhra Pradesh | KCX4 | 3384K1940 | 2908 | 2018-08-07 | 21774 | 2018-08-01 | overheating of cylinder | 2018-03-30 | 2018-05-22 | 1475 | null | null | 2 | piston siezed del. Valve leak | null | closed | null
2018-08-21 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Ambika Sheetgrah Pvt Ltd | Uttar Pradesh | KCX6 | 3394K946 | 2854 | 2018-07-12 | 216818 | 2018-07-02 | shaft seal leakage | 2017-12-30 | 2018-03-01 | 499 | null | null | 3 | replaced shaft seal assly | null | closed | null
2018-08-21 | Trade Links | null | D | Covalent Laboratories Pvt Ltd | Telangana | KC84 | 330K46 | 2892 | 2018-07-28 | 217398 | 2018-07-05 | solenoid valve not working/ discharge valve assly | 2017-08-28 | 2018-08-18 | 10 | null | null | 12 | Replaced sol. Valve, del. Valve & suction stroke limitor | null | closed | null
2018-08-21 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KC84 | 330K47 | 2891 | 2018-07-28 | 217416 | 2018-07-06 | solenoid valve not working/ valve ring not freely seating in del. stroke limitor | 2017-08-28 | 2018-08-18 | PC | null | null | 12 | Replaced sol. Valve and del. Stroke limitor | null | closed | null
2018-08-21 | S M Refrigeration | null | D | Shrim Industries Pvt Ltd | Uttarakhand | KCX4 | 3384K1634 | 2859 | 2018-07-14 | 216932 | 2018-06-06 | tah8 valve adaptor broken | 2017-06-16 | 2018-06-08 | ZH | null | null | 12 | Replaced TAH8 valve adaptor | null | closed | TAH8 valve
2018-08-21 | Kalp Marketing | Gujrat | D | Nilesh Sea Foods | Gujrat | KCX72 | 3474K106 | 2862 | 2018-07-16 | 216994 | 2018-07-11 | tah8 valve adaptor broken | 2017-07-25 | 2018-07-12 | ZH | null | null | 12 | Replaced Adaptor | null | closed | Adaptor
2018-08-26 | Trade Links | null | D | Sanghani Agencies | Goa | KCX3 | 3374K1856 | 2909 | 2018-08-07 | 217776 | 2018-07-11 | panel board wiring burnt | 2018-07-06 | 2018-08-07 | ZH | null | null | 1 | Panel board wiring short circuit | null | closed | Panel board
2018-08-28 | Parag Marketing Services | null | D | Sonali Ice Factory | Sangli | KCX2 | 3364K1416 | 2762 | 2018-05-30 | 215310 | 2018-04-21 | high oil consumption | 2017-11-28 | 2017-12-09 | 2107 | null | null | 1 | replaced piston ring sets and ORV | null | closed | null
2018-08-28 | S M Refrigeration | null | D | S P Cold Storage | null | KC4 | 338K5616 | 2860 | 2018-07-14 | 216934 | 2018-04-20 | overheating of cylinder | 2017-04-10 | 2018-03-05 | 109 | null | null | 11 | Delivery valve leakage and buffer spring shrunk | null | closed | Delivery valve and buffer spring shrunk
2018-08-31 | Morgan | null | E | Haji Sadique Chashma Goth Ice Plant | Karachi, Pakistan | KCX6 | 3394K1059 | null | 2018-07-17 | 31 | 2018-07-07 | low oil pressure | 2018-03-07 | 2018-07-06 | ZH | null | null | 4 | KCX oil pump Low oil pressure | null | closed | Replace oil pump
2018-09-21 | Trade Links | Goa | D | KIIce Plant Goa | null | KCX3 | 3374K1512 | 2177722907 | 2018-08-07 | 217772 | 2018-07-12 | abnormal noise | 2017-09-05 | 2017-09-23 | 4383 | null | null | 1 | Cylinder no.1 Piston had crack. | null | closed | Replaced piston
2018-09-21 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2179222919 | 2018-08-11 | 217922 | 2018-08-09 | abnormal noise | 2017-04-23 | 2017-09-18 | 3517 | null | null | 5 | Both HP Cylinder liners & Piston rings wornout. | null | closed | Replaced liner & Piston rings.
2018-09-21 | Multivista Global Pvt Ltd | null | D | Apm Terminal India Pvt Ltd | Tamil Nadu | KCX6 | 339K3440 | 2184722966 | 2018-08-27 | 218472 | 2018-08-20 | abnormal noise from piston no 1 | 2017-10-14 | 2018-06-10 | 48 | null | null | 10 | Piston , Piston rings , Cylinder liner wornout and delivery valve leakage. | null | closed | Replaced Liner , Piston , Piston ring set , Buffer spring, Kit delivery valve, gudgeon pin & Bush con rod.
2018-09-21 | Parag Marketing Services | null | D | Jeelani Marine Products | Ratnagiri | KCX42 | 3444K081 | 2172822885 | 2018-07-25 | 217282 | 2018-05-30 | delivery valve leakage | 2018-01-05 | 2018-06-07 | ZH | null | null | 5 | Delivery valve leakage and jammed in cylinder liner. | null | closed | Replaced delivery valve assembly
2018-09-21 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Food Export Pvt Ltd | Uttar Pradesh | KCX72 | 3474K191 | 2174982896 | 2018-07-30 | 217498 | 2018-07-20 | flywheel groove oversize | 2018-06-18 | 2018-07-21 | ZH | null | null | 1 | Flywheel groove no.2 from shaft seal side was oversized. | null | closed | Replaced Flywheel (1012)
2018-09-21 | Multivista Global Pvt Ltd | null | D | Ninnas Pvt Ltd | Tamil Nadu | KCX3 | 3374K1629 | 2184422963 | 2018-08-27 | 218442 | 2018-08-22 | high oil consumption | 2017-12-18 | 2018-06-22 | 1080 | null | null | 6 | Piston 1& 3 crack on top side and piston no. 2 top side having scoring marks. | null | closed | Replaced Piston 3 , Piston ring set3, Filter wire , Bearings & DV1
2018-09-21 | Kalp Marketing | Gujrat | D | Zenith Exports | Gujrat | KCX51 | 3454K071 | 2193063007 | 2018-09-11 | 219306 | 2018-09-08 | knocking / abnormal sound | 2018-05-13 | 2018-10-23 | 3 | null | null | 5 | Knocking sound in HP cylinder due to delivery valve leakage and piston rings damaged due to foregin particle entry. No manufacturing defect | null | closed | Replaced valve kit and Piston ring set
2018-09-21 | S M Refrigeraion Pvt Ltd | null | D | M/S Shri NK Ice & Cold Storage | Madhya Pradesh | KCX4 | 3384K1750 | 2181962952 | 2018-08-18 | 218196 | 2018-07-15 | oil lifting | 2017-12-10 | 2018-02-07 | 1313 | null | null | 2 | Found leakage in ORV due to oil lifting of 3 liters within 24 hrs. | null | closed | Replaced ORV1 No.
2018-09-21 | S M Refrigeraion Pvt Ltd | null | D | M/S Kasturi Bai Gopi Babu Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1002 | 2178842916 | 2018-08-10 | 217884 | 2018-07-29 | oil pressure not buildup | 2018-02-07 | 2018-03-05 | 1095.7 | null | null | 1 | Due to increase in gap between driven gear bush and its pin , Pump element outer rotor shaft broken. | null | closed | Replaced pump element
2018-09-21 | Multivista Global Pvt Ltd | null | D | Abt Industries Ltd | Tamil Nadu | KCX4 | 3384K1618 | 2198463029 | 2018-09-25 | 219846 | 2018-09-13 | oil pump damage | 2017-05-21 | 2018-10-23 | 1046 | null | null | 17 | To removed the oil pump assembly pump element gear shaft was broken. Replaced with existing KCX63 compressor pump. | null | closed | Replaced pump assembly.
2018-09-21 | Fridge House | null | D | Rpm Engineering India Ltd | Karnataka | KCX4 | 3384K1268 | 2166502846 | 2018-07-07 | 216650 | 2018-07-03 | oil pump tang broken | 2016-08-31 | 2017-08-17 | 3807 | null | null | 12 | Tang broken and scoring marks to pump body hence oil pressure was not built. | null | closed | Replaced pump assembly (LubricareLC 08 16 306)
2018-09-21 | Kalp Marketing | Gujrat | D | Om Cold Storage | Gujrat | KCX3 | 3374K1714 | 2193003005 | 2018-09-11 | 219300 | 2018-09-07 | shaft seal leakage | 2018-02-18 | null | 203 | null | null | null | Dismentled shaft seal assembly found both stationary and rotory in damaged condition. | null | closed | Replaced shaft seal assy
2018-09-21 | Fridge House | null | D | M/SDivine Spirit Ice And Cold Storage | Karnataka | KCX6 | 3394K1067 | 2192923001 | 2018-09-10 | 219292 | 2018-08-30 | transit damage oil pump body | 2018-04-09 | null | 4 | null | null | null | As mentioned in FRR Oil pump body has cracked during transit time. | null | closed | Replaced pump assembly
2018-09-22 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX72 | 3474K156 | 2188063010 | 2018-09-12 | 218806 | 2018-08-14 | 1.crankcase heater fouling to support of intermediate bearing housing 2. connecting rod and cap sr. no. not in same side | 2018-01-30 | 2018-08-14 | ZH | null | null | 7 | 1.Crankcase heater fouling to support of intermediate bearing housing 2. connecting rod and cap sr. no. not in same side | null | closed | null
2018-09-22 | Multivista Global Pvt Ltd | null | D | Kvs Ice Plant | Tamil Nadu | KCX3 | 3374K1579 | 2179062917 | 2018-08-10 | 217906 | 2018-06-29 | abnormal noise | 2017-11-22 | 2018-05-23 | 1416 | null | null | 6 | Replaced Orings & 1 K5 Valve | null | closed | Replaced Orings & 1 K5 Valve
2018-09-22 | Kalp Marketing | Gujrat | D | Megent Electric | Veraval, Gujarat | KCX72 | 3474K100 | Email | 2018-09-19 | null | 2018-09-19 | c.case weld leak at discharge | 2017-06-28 | null | 150 | null | null | null | null | null | null | null
2018-09-22 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX51 | 3454K065 | 2183262960 | 2018-08-23 | 218326 | 2018-08-14 | flywheel bore oversize. | 2018-03-06 | 2018-08-14 | ZH | null | null | 5 | Gap between shaft and flywheel 0.18mm | null | closed | Replaced Flywheel
2018-09-22 | Trade Links | Secunderabad | D | Sri Venkateshwara Cold Storage | null | KCX2 | 3364K1566 | 2191422990 | 2018-09-06 | 219142 | 2018-08-26 | kcx oil pump element tang broken | 2018-04-28 | 2018-08-26 | 180 | null | null | 4 | Driven gear bush damaged & resulted to shearing of the driving tang | null | null | Replaced pump elemnet
2018-09-22 | Parag Marketing Services | null | D | Jeelani Marine Products | Ratnagiri | KCX72 | 3374K148 | 2191342989 | 2018-09-06 | 219134 | 2018-09-03 | knocking / abnormal sound | 2018-01-27 | 2018-06-01 | 126 | null | null | 7 | Knocking sound from cylinder no.4 due to liner piston seized & delivery valve leakage. | null | null | Replaced cylinder liner , Piston , Piston ring set & delivery valve assembly
2018-09-22 | S M Refrigeration | null | D | Prabhat Ware House & Cold Storage | null | KCX6 | 3394K966 | 2181982996 | 2018-09-07 | 218198 | 2018-08-05 | oil carry over | 2018-01-05 | 2018-03-07 | 1823 | null | null | 2 | ORV leakage | null | null | ORV Replaced
2018-09-22 | S M Refrigeraion Pvt Ltd | null | D | Radha Krishna Ice & Cold Storage | Uttar Pradesh | KCX3 | 3374K1683 | 2169182858 | 2018-07-13 | 216918 | 2018-07-11 | overheating of cylinder | 2018-01-29 | 2018-03-13 | 2140 | null | null | 2 | Delivery valve leakage & Piston rings wornout - 01 no. | null | closed | Replaced delivery valve assly & Piston ring set.
2018-09-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Saf Yest Company Ltd | Uttar Pradesh | KCX6 | 3394K1109 | 2188722986 | 2018-09-05 | 218872 | 2018-08-17 | pressure gauge & switch not working | 2018-06-29 | 2018-08-18 | ZH | null | null | 2 | During comm pressure gauge error and MP55A not working. | null | closed | Replacde Pr gauge & MP55A
2018-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vanita Ice (P) Ltd | Palghar | KCX3 | 3374K1616 | 2188202982 | 2018-09-04 | 218820 | 2018-08-30 | pump element tang broken | 2017-12-10 | 2018-10-23 | 1000 | null | null | 10 | Element broken due to jamming of bearings and seal was leaking. | null | null | Replaced element and Shaft seal oring kit.
2018-09-22 | Kalp Marketing | Gujrat | D | Megent Electric | Veraval, Gujarat | KCX51 | 3454K069 | mail | null | null | null | suction str welding leakage | 2018-04-20 | 2018-06-11 | ZH | null | null | 2 | During pressure test at site pin hole in the welding on the joint at suction strainer is detected. | null | null | null
2018-10-19 | Parag Marketing Services | null | D | Western Superfresh Stores | Mumbai | KCX72 | 3474K122 | 2198783032 | 2018-09-26 | 219878 | 2018-08-12 | abnormal noise in hp cylinder | 2017-09-22 | 2018-08-07 | 35 | null | null | 11 | Water entered in cylinder from system | null | null | Replaced piston, liner & Del. Valve
2018-10-19 | Hss Solution Pvt Ltd | null | D | Vrindavan Dairies | Rajastan | KCX4 | 3384K1330 | 2195723027 | 2018-09-24 | 219572 | 2018-09-11 | driving plate replaced | 2016-11-13 | 2017-04-05 | 2210 | null | null | 5 | Driving plate replaced | null | null | Driving plate
2018-10-19 | Parag Marketing Services | null | D | Amrut Dairy & Beverages | null | KCX1 | 3354K052 | 2197503025 | 2018-09-22 | 219750 | 2018-09-20 | knocking / abnormal sound | 2017-12-11 | 2018-05-14 | 136 | null | null | 5 | System weld particles entered in system | null | null | Replaced Del Valve
2018-10-19 | Parag Marketing Services | null | D | Natural Sugar & Alied Induztries | null | KCX4 | 3384K1884 | 2182922958 | 2018-08-23 | 218292 | 2017-07-27 | knocking / abnormal sound | 2018-02-28 | 2018-06-02 | 122 | null | null | 6 | Delivery valve leakage & Buffer spring length short | null | null | Delivery valve leakage & Buffer spring length short
2018-10-20 | S M Refrigeration | null | D | Varun Beverage Limited | Uttar Pradesh | KCX6 | 339K3363 | 2185702969 | 2018-08-29 | 218570 | 2018-08-14 | extra sound | 2016-12-11 | 2017-04-15 | 2964 | null | null | 4 | Extra Sound problem due to del valve leakage | null | closed | Replaced del. Valve,liner,piston, piston ring set
2018-10-20 | S M Refrigeration | null | D | Shri Mahashay Bhikam Singh Cold Storage | Uttar Pradesh | KCX6 | 3394K969 | 2206323079 | 2018-10-13 | 220632 | 2018-09-03 | heating piston | 2018-01-06 | 2018-02-24 | 1794 | null | null | 1 | Heating Piston No. 4 | null | closed | replaced Discharge valve Assembly
2018-10-20 | S M Refrigeration | null | D | Jai Managla Cold Storage | Uttar Pradesh | KC4 | 338K5611 | 2194883016 | 2018-09-17 | 219488 | 2018-04-30 | knocking / abnormal sound | 2017-03-24 | 2018-04-01 | 593 | null | null | 13 | Knocking sound Problem | null | closed | del valve assly,buffer spring
2018-10-20 | S M Refrigeration | null | D | Sahu Khan Chand CS | Uttar Pradesh | KCX6 | 3394K3474 | 2204783065 | 2018-10-11 | 220478 | 2018-07-07 | knocking / abnormal sound | 2018-01-19 | 2018-03-17 | 152 | null | null | 2 | Premature failure | null | null | Replaced Piston ring set
2018-10-20 | S M Refrigeration | null | D | Lala Navel Kishore Cold Storage Bareilly | Uttar Pradesh | KCX2 | 3364K1424 | 2177902918 | 2018-08-11 | 217790 | 2018-07-27 | oil carry over | 2017-11-11 | 2018-02-26 | 608 | null | null | 3 | Oil carryover 2 ltr/day | null | closed | Piston ring set
2018-10-20 | S M Refrigeration | null | D | Shrim Industries Pvt Ltd | Uttarakhand | KCX4 | 3384K1634 | 2205863075 | 2018-10-13 | 220586 | 2018-09-07 | oil carry over | 2017-06-16 | 2018-06-08 | 890 | null | null | 12 | Oil carryover 3 ltr/day | null | closed | Replaced Piston ring set
2018-10-20 | S M Refrigeration | null | D | Sahu Khan Chand CS | Uttar Pradesh | KCX6 | 339K3474 | 2202283068 | 2018-10-12 | 220228 | 2018-09-23 | oil carry over | 2018-01-19 | 2018-03-17 | 572 | null | null | 2 | Premature failure | null | closed | Replaced Piston ring set
2018-10-20 | Kalp Marketing | Gujrat | D | Jay Shree Gayatri Food Products Pvt Ltd | Sehore, Madhya Pradesh | KCX6 | 3394K1025 | 2205403069 | 2018-10-12 | 220540 | 2018-10-10 | oil carry over | 2018-02-26 | 2018-05-24 | 2404 | null | null | 3 | Knocking sound cylinder no.1and higher Oil consumption. | null | closed | Replaced Piston Ring Set and Gasket replaced
2018-10-20 | Model Pneumatic Co | Punjab | D | Sri Guru Ram Das Cold Storage | null | KC4 | 338K5567 | 2167102850 | 2018-07-09 | 216710 | 2018-06-19 | oil carry over | 2017-01-09 | 2017-02-21 | 1390 | null | null | 1 | Oil carryover 2 ltr/day | null | null | Replaced Piston ring set
2018-10-20 | S M Refrigeration | null | D | Swadesh Milk Products Pvt Ltd | null | KCX4 | 3384K1876 | 2176562910 | 2018-08-07 | 217656 | 2018-08-01 | oil carry over | 2018-02-27 | 2018-05-29 | 682 | null | null | 3 | Replaced piston ring set & Piston | null | null | Replaced piston ring set & Piston
2018-10-20 | S M Refrigeration | null | D | Kumar Ice & Cold Storage | Mathura,Uttar Pradesh | KCX4 | 3384K1554 | 2205303072 | 2018-10-12 | 220530 | 2018-06-20 | oil pressure not buildup | 2017-03-14 | 2018-03-11 | 5120 | null | null | 12 | Oil pump element tang broken | null | closed | Oil pump Element.
2018-10-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vkm Foods Pvt Ltd | Taloja, Mh | KCX72 | 3474K128 | 2193143008 | 2018-09-11 | 219314 | 2018-09-07 | oil pressure not buildup | 2017-10-14 | 2018-06-13 | 27 | null | null | 8 | Tang broken | null | null | Replaced Pump Element
2018-10-20 | S M Refrigeration | null | D | Maa Gayatri Cold Storage | null | KCX4 | 3384K1854 | 2192063015 | 2018-09-15 | 219206 | 2018-08-20 | oil pressure not buildup | 2018-02-13 | 2018-03-09 | 541 | null | null | 1 | Tang broken | null | null | Replaced pump element
2018-10-20 | Kalp Marketing | Gujrat | D | Hind Ice &Cold Storage | Gujrat | KCX3 | 3374K1908 | 2200283040 | 2018-09-29 | 220028 | 2018-09-24 | oil pressure not buildup | 2018-09-03 | 2018-09-20 | ZH1 | null | null | null | Oil pump element tang broken | null | closed | Replaced Oil pump Element.
2018-10-20 | Kalp Marketing | Gujrat | D | Mayur Fish Suppliers | Gujrat | KCX21 | 3424K068 | 2205843074 | 2018-10-13 | 220584 | 2018-10-10 | oil pressure not buildup | 2018-08-24 | 2018-10-12 | ZH2 | null | null | 2 | Regulator Fault | null | closed | Replaced Regulator
2018-10-20 | S M Refrigeration | null | D | Jai Jabdambey Ice Factory & Milk | Uttar Pradesh | KCX3 | 3374K1727 | 2179902923 | 2018-08-13 | 217990 | 2018-08-11 | shaft seal leakage | 2018-02-23 | 2018-04-20 | 1062 | null | null | 2 | Shaft seal leak | null | closed | shaft seal assly
2018-10-20 | Kalp Marketing | Gujrat | D | Dytint Specialities Pvt Ltd | Gujrat | KCX6 | 3394K873 | 2200163039 | 2018-09-29 | 220016 | 2018-09-16 | shaft seal leakage | 2017-09-29 | 2018-07-13 | ZH1 | null | null | 10 | Shaft seal leak | null | closed | Replaced shaft seal assly
2018-10-20 | Kalp Marketing | Gujrat | D | Excel Cropcare Ltd | Bhuj Gujarat | KCX6 | 3394K1110 | 2205563070 | 2018-10-12 | 220556 | 2018-10-10 | shaft seal leakage | 2018-06-29 | 2018-09-26 | 28 | null | null | 3 | Shaft seal leak | null | closed | Replaced shaft seal assly
2018-10-20 | S M Refrigeration | null | D | Jaharveer Maharaj Agro Ltd Hathras | Uttar Pradesh | KCX3 | 3374K1599 | 2203923060 | 2018-10-10 | 220392 | 2018-08-14 | solenoid valve not working | 2017-12-01 | 2018-02-28 | 614 | null | null | 2 | solenoid valve not working | null | closed | solenoid valve
2018-10-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K1912 | 2206403081 | 2018-01-14 | 220640 | 2018-09-27 | lp pressure switch / cutout not working | 2018-09-11 | 2018-09-18 | 2 | null | null | 1 | Pressure switch not working | null | closed | Replaced pressure switch
2018-11-18 | Cool Comfort Private Limited | West Bengal | D | Megaa Moda P Ltd | null | KCX6 | 3394K691 | 2205643071 | 2018-10-12 | 220564 | 2018-10-01 | abnormal noise | 2017-01-04 | 2017-06-23 | 4465 | null | null | 5 | Abnormal sound | null | closed | Delivery valve ,piston , liner
2018-11-18 | Trade Links | Secunderabad | D | Amrut Dairy & Beverages | null | KCX1 | 3354K052 | 2205883076 | 2018-10-13 | 220588 | 2018-10-11 | abnormal noise | 2017-12-11 | 2018-05-14 | 506 | null | null | 17 | Abnormal sound | null | closed | piston and cyl liner
2018-11-18 | Gargi Engineering Enterprices Pvt Ltd | null | D | Western Chemicals | Mumbai | KCX3 | 3374K1685 | Email Dt. 17/11/18 | null | null | null | crank case leak near foot and shell joint due to crack | 2018-01-01 | 2018-04-26 | 1500 | null | null | 3 | Crack developed near shell and foot joint | null | closed | Compressor
2018-11-18 | Fridge House | null | D | M/SDivine Spirit Ice And Cold Storage | Karnataka | KCX6 | 3394K1067 | Email dt.30.10.2018 | null | null | null | crank case leak near foot and shell joint due to crack | 2018-04-09 | 2018-09-01 | 700 | null | null | 5 | Crack developed near shell and foot joint | null | closed | Compressor
2018-11-18 | Hss Solution Pvt Ltd | null | D | Krishna Chilling Center | Rajastan | KCX2 | 3364K1530 | 2192983003 | 2018-09-11 | 219298 | 2018-09-04 | oil carry over | 2018-03-12 | 2018-04-15 | 2145 | null | null | 1 | oil carryover | null | closed | Piston ring sets
2018-11-18 | S M Refrigeration | null | D | Sushila Cold Storage | Uttar Pradesh | KCX6 | 3394K1024 | 2167562852 | 2018-07-10 | 216756 | 2018-07-07 | oil lifting | 2018-02-26 | 2018-05-22 | 352 | null | null | 3 | oil carryover | null | closed | Replaced liner,piston piston rings
2018-11-25 | Trade Links | Secunderabad | D | Royal Imports & Exports | Andhra Pradesh | KCX51 | 3454K033 | 2198903077 | 2018-10-13 | 219880 | 2018-09-18 | abnormal noise | 2017-05-09 | 2018-06-12 | 930 | null | null | 13 | Delivery valve leakge | null | closed | Delivery valve , piston liner replaced 3nos.
2018-11-25 | Trade Links | Secunderabad | D | Satya Sea Foods P Ltd | Andhra Pradesh | KC93 | 348K148 | 2205963078 | 2018-10-13 | 220596 | 2018-08-24 | low oil pressure | 2017-02-18 | 2017-06-05 | 1485 | null | null | 4 | Replaced oil KC pump assly , gear bush , cover ok | null | closed | Replaced oil KC pump assly.
2018-11-25 | Trade Links | Secunderabad | D | Aiswarya Impex | Andhra Pradesh | KCX72 | 3474K072 | 2206943090 | 2018-10-15 | 220694 | 2018-09-17 | oil lifting | 2017-03-21 | 2018-04-06 | 1206 | null | null | 13 | Heavy oil throw from cylinders | null | closed | Piston ring set 05 nos.
2018-11-25 | Trade Links | Secunderabad | D | Munaga Chennahai | Andhra Pradesh | KCX3 | 3374K1609 | 2198043028 | 2018-09-24 | 219804 | 2018-09-17 | shaft seal leakage | 2017-12-08 | 2018-01-05 | 1753 | null | null | 1 | Replaced shaft seal assly | null | closed | Shaft seal assly
2018-11-25 | Kalp Marketing | Gujrat | D | Shree Sorath Chilling Plant Junagadh | Gujrat | KCX6 | 3394K773 | 2210603100 | 2018-10-26 | 221060 | 2018-10-12 | shaft seal leakage | 2017-03-27 | 2018-05-30 | ZH | null | null | 14 | O ring kit replaced | null | closed | O ring kit
2018-12-16 | Fridge House | null | D | Coastal Refrigeration And Fabricators | Karnataka | KCX6 | 3394K1053 | 2203303059 | 2018-11-10 | 220330 | 2018-09-28 | abnormal noise | 2018-03-20 | 2018-08-17 | 617 | null | null | 5 | Knocking sound from 1,4 & 5 due to damage/seize liner & Piston. | null | closed | Replaced Piston3 , Piston ring4 set , del valve assly1 & liner 1 replaced.
2018-12-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Bharat Sea Foods | Kerala | KC21 | 342K898 | 2205823073 | 2018-10-13 | 220582 | 2018-10-11 | abnormal noise | 2017-04-14 | 2017-11-07 | 4000 | null | null | 7 | Abnormal soun due to buffer spring shrink in HP cylinder. | null | closed | Replaced buffer spring
2018-12-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Siddhart Colorchem Pvt Ltd | Mahad | KCX4 | 3384K1861 | 2202163051 | 2018-10-05 | 220216 | 2018-10-02 | abnormal noise | 2018-02-18 | 2018-06-01 | 1567 | null | null | 4 | Replaced piston , piston ring set , del valve assly, bush con rod | null | closed | Replaced piston , piston ring set , del valve assly, bush con rod
2018-12-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Aarti Drugs Limited | Tarapur | KCX6 | 3394K1060 | 2212343181 | 2018-12-08 | 221234 | 2018-10-31 | abnormal noise | 2018-03-28 | 2018-09-18 | 169 | null | null | 6 | Replaced cylinder liner, piston, del valve | null | closed | Replaced cylinder liner, piston, del valve
2018-12-16 | Parag Marketing Services | Pune | D | Izhan Ice Plant | Ratnagiri | KCX3 | 3374K1336 | 2207043089 | 2018-10-15 | 220704 | 2018-09-17 | ccsv problem | 2017-02-25 | 2017-09-08 | 2682 | null | null | 7 | CCSV No. 1 problem due to coil burned also not working manually. | null | closed | Replaced solenoid valve assembly NO type 01 no.
2018-12-16 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KC42 | 344K1108 | 2220343157 | 2018-11-28 | 222034 | 2018-11-26 | delivery valve leakage | 2017-09-29 | 2018-11-28 | ZH | null | null | 2 | During commissoning of compressor HP cylinder pressure was not building up more than 7.0 Kg/cm2. | null | closed | Replaced del valve
2018-12-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Lupin Limited | Ankleshwar Gujarat | KC84 | 330K45 | 2212723141 | 2018-11-21 | 221272 | 2018-10-21 | high pressure | 2017-08-13 | 2018-10-04 | 372 | null | null | 14 | Cylinder no. 1 & 11 tap bolt broken & Cyl 1 big end bearing worn out due to high pressure. | null | closed | Replaced tap bolt 4 nos & Big end bearing 1 no.
2018-12-16 | Parag Marketing Services | Pune | D | United Agro Frozen Food | Kopargaon | KCX42 | 3444K074 | 2213763164 | 2018-11-29 | 221376 | 2018-11-02 | knocking sound problem | 2017-10-31 | 2018-03-12 | 570 | null | null | 5 | Abnormal sound from cylinder no.4 due to piston seized . | null | closed | Replaced discharge valve , liner , piston , pisoton ring set & gudgeon pin.
2018-12-16 | Trade Links | Goa | D | Quality Foods Goa | null | KC72 | 347K969 | 2207023088 | 2018-10-15 | 220702 | 2018-10-13 | low oil pressure | 2017-05-31 | 2017-08-16 | 2201 | null | null | 3 | Low oil pressure problem due to gear kit wornout. | null | closed | Replaced gear kit
2018-12-16 | Parag Marketing Services | Pune | D | Shree Warna Dudh Sangh Pvt Ltd | Kolhapur | KCX3 | 3374K1279 | 2217203134 | 2018-11-19 | 221720 | 2018-11-16 | oil carry over | 2017-01-29 | 2017-07-03 | 2019 | null | null | 6 | Replaced Piston ring sets & ORV | null | closed | Replaced Piston ring sets & ORV
2018-12-16 | Parag Marketing Services | Pune | D | Shramik Milk Products | Ahmed Nagar | KCX2 | 3364K1301 | 2217763137 | 2018-11-20 | 221776 | 2018-11-19 | oil carry over | 2017-04-25 | 2017-08-19 | 4163 | null | null | 4 | Replaced both cylinder piston ring sets | null | closed | Replaced both cylinder piston ring sets
2018-12-16 | Parag Marketing Services | Pune | D | Ganesh Sah Dudh V Yasaik Sanstha Maryadit | Pune | KCX2 | 3364K1361 | 2237103180 | 2018-12-07 | 222370 | 2018-12-05 | oil carry over | 2017-07-15 | 2018-01-31 | 515 | null | null | 6 | Replaced cyl liner and piston ring set-2nos. | null | closed | Replaced cyl liner and piston ring set2nos.
2018-12-16 | Trade Links | Goa | D | Sagar Feeds & Food Processing Industries | Goa | KCX72 | 3474K206 | 2203743058 | 2018-10-09 | 220374 | 2018-10-02 | oil pressure not buildup | 2018-07-18 | 2018-09-03 | 778 | null | null | 2 | Low oil pressure due to both OPR Circlip not found and malfunctioning. | null | closed | Replaced both OPR
2018-12-16 | Multivista Global Pvt Ltd | null | D | Apm Terminal India Pvt Ltd | Tamil Nadu | KC6 | 339K3441 | 225403193 | 2018-12-12 | 222540 | 2018-12-01 | op overflow connection thread damaged | 2017-10-14 | 2018-04-26 | 303 | null | null | 6 | Compressor crankcase and oil pump overflow line ferrule and nut & Crankcase niple thread damaged. | null | closed | Replace Nipple M22 & Union nut
2018-12-16 | S M Refrigeraion Pvt Ltd | null | D | Stellar Gold Chain Inc | Uttarakhand | KCX4 | 3384K2000 | 2223003175 | 2018-12-06 | 222300 | 2018-12-04 | suction pressure gauge not working | 2018-07-01 | 2018-12-06 | 2 | null | null | 5 | Suction pressure gauge not working | null | closed | Replaced Pr. Gauge 16.00Kg/cm2.
2018-12-28 | Kalp Marketing | Gujrat | D | Sun Exports | Gujrat | KCX72 | 3474K180 | 2230603222 | 2018-12-27 | 223060 | 2018-12-26 | abnormal noise | 2018-04-30 | 2018-08-02 | 1992 | null | null | 4 | Two Piston crack . One piston found touch to delivery valve where crankpin wornout. We will do the analysis at our end. doubt of liquid entry in this case. For this we are giving advantage to customers. Detail mail recd from Mr. Shendge. compressor will witnessed by Vishal Barot before start of machine | null | closed | Replaced Piston, piston ring set , Crankshaft & Bearings
2018-12-31 | Kalp Marketing | Gujrat | D | Aksharchem India Ltd | Kadi, Gujrat | KCX9 | 3404K075 | 2213823120 | 2018-11-03 | 221382 | 2018-11-02 | high oil consumption | 2017-09-27 | 2018-04-18 | 3679 | null | null | 7 | ORV 6 Nos and VLD Orings changed. | null | closed | Replaced ORV 6 Nos and VLD Orings.
2018-12-31 | Kalp Marketing | Gujrat | D | Anmol Frozen Pvt Ltd | Rajkot, Gujrat | KCX3 | 3374K1464 | 2227943212 | 2018-12-24 | 222794 | 2018-12-18 | high oil consumption | 2017-06-19 | 2018-02-21 | 133 | null | null | 8 | Change piston ring set 03 .02 N R V | null | closed | Replaced piston ring set 3 & ORV 2 nos.
2018-12-31 | Kalp Marketing | Gujrat | D | Raunak Ice & Cold Storage | Gujrat | KCX51 | 3454K075 | 2216783128 | 2018-11-26 | 221678 | 2018-11-15 | high oil consumption | 2018-06-10 | 2018-08-06 | 986 | null | null | 2 | Change v.ld oring inner and outer 6 nos found 1 n.r.v found in crankcase body so reffitting it also 2 nrv found leackage condition so replace it | null | closed | Replaced VLD Oring & ORV
2018-12-31 | Kalp Marketing | Gujrat | D | Kiri Industries Limited | Ahmedabad | KCX3 | 3374K043 | 2223883176 | 2018-12-06 | 222388 | 2018-12-06 | oil pressure problem | 2017-04-25 | 2018-06-14 | 750 | null | null | 14 | Open up oil pump found element broken condition relpace element check both filter found ok then full load trail ok | null | closed | Replaced pump element
2018-12-31 | Trade Links | Secunderabad | D | Satya Ice | Kakinada | KCX4 | 3384K1929 | 2220263167 | 2018-11-30 | 222026 | 2018-11-26 | overheating & abnormal sound | 2018-03-24 | 2018-07-10 | 1930 | null | null | 4 | customer had told over heating of no1 cylinder visited site and observed same opened head cover and checked all observed dv assly back leakage due to piston liner sized removed all damaged spare parts and replaced from customer stock liner piston piston rings set dv assly buffer spring suction valve ring suction valve springs and etc changed oil and paper filter taken trail run of compressor oil pressure developed up to 2kgcm square loading and un loading fond ok put back the machine | null | closed | Delivery valve, Liner & Piston ring set
2018-12-31 | Kalp Marketing | Gujrat | D | Sadguru Cold Storage | Mahuva,Gujrat | KCX3 | 3374K1600 | 2225003218 | 2018-12-26 | 222500 | 2018-12-11 | shaft seal leakage | 2017-11-29 | 2018-03-27 | 556 | null | null | 16 | Shaft seal found oring warn out condition so replace new oring kit then refitting all and take full load trail ok | null | closed | Replaced Oring kit
2019-01-23 | S M Refrigeration | null | D | Sahu Khan Chand CS | Uttar Pradesh | KC4 | 338K5632 | 2204943067 | 2018-10-12 | 220494 | 2018-07-10 | abnormal noise | 2017-11-10 | 2018-03-05 | 401 | null | null | 4 | Replaced cylinder liner, piston, piston ring set | null | closed | Replaced cylinder liner, piston, piston ring set
2019-01-23 | S M Refrigeration | null | D | Sahu Khan Chand CS | Uttar Pradesh | KC4 | 338K5632 | 2204903066 | 2018-10-11 | 220490 | 2018-05-15 | abnormal noise | 2017-11-10 | 2018-03-05 | 391 | null | null | 4 | Replaced cylinder liner, piston, piston ring set | null | closed | Replaced cylinder liner, piston, piston ring set
2019-01-23 | S M Refrigeration | null | D | Nature Welness Food Products | Uttarakhand | KCX3 | 3374K1436 | 2197463026 | 2018-09-22 | 219746 | 2018-09-04 | abnormal noise | 2017-05-10 | 2017-12-15 | 767 | null | null | 7 | Foreign particles entered , piston, liner,and oil pump components wearout. | null | closed | Replaced Cylinder liner, piston, oil pump.
2019-01-23 | Geekay Pneumatic Pvt Ltd | null | D | Southern Ice And Cold Storage | null | KCX3 | 3374K1447 | 2212843138 | 2018-11-21 | 221284 | 2018-11-01 | abnormal noise | 2017-08-14 | 2018-02-05 | 1909 | null | null | 5 | cylinder liner,piston ring set worn out | null | closed | null
2019-01-23 | Fridge House | null | D | The Mandya Dist Co Operative Products Societies Union Ltd | null | KCX6 | 3394K995 | 2217683165 | 2018-11-29 | 221768 | 2018-11-19 | abnormal noise | 2018-01-31 | 2018-06-08 | 2387 | null | null | 5 | cylinder liner,piston ring set damged delivery valve leakage | null | closed | null
2019-01-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Arati Drugs | null | KCX6 | 3394K845 | 2219863174 | 2018-12-05 | 221986 | 2018-11-24 | abnormal noise | 2017-08-14 | 2018-02-05 | 1909 | null | null | 5 | Delivery valve ring & spring broken | null | closed | null
2019-01-23 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2228783209 | 2018-12-21 | 222878 | 2018-12-21 | abnormal noise | 2017-04-23 | 2017-09-18 | 4866 | null | null | 5 | liner worn out at one side | null | closed | null
2019-01-23 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2234023249 | 2019-01-05 | 223402 | 2019-01-04 | abnormal noise | 2017-04-23 | 2017-09-18 | 4964 | null | null | 5 | Wearings of rings and springs | null | closed | null
2019-01-23 | Trade Links | Secunderabad | D | Devi Sea Foods | null | KCX4 | 3384K1789 | 2258523210 | 2018-12-22 | 222852 | 2018-12-20 | abnormal noise | 2018-01-01 | 2018-02-07 | 606 | null | null | 2 | Discharge stroke limitor damaged | null | closed | Del stroke limitor & Valve kit
2019-01-23 | Trade Links | Secunderabad | D | Nirmala Metal Industries | null | KCX3 | 3374K1810 | 2232583248 | 2019-01-04 | 223258 | 2019-01-02 | cylinder overheating | 2018-05-09 | 2018-08-07 | 2812 | null | null | 3 | Delivery stroke limitor lugs worn out | null | closed | Replace delivery valve assly1
2019-01-23 | Geekay Pneumatic Pvt Ltd | null | D | Abad Fisheries | Secunderabad | KC72 | 347K985 | 2230683225 | 2018-12-28 | 223068 | 2018-12-27 | high oil carryover | 2018-09-15 | 2018-12-18 | 32 | null | null | 3 | oil splashing thru pistons | null | closed | null
2019-01-23 | Cool Comfort Private Limited | West Bengal | D | Shimpo Export | null | KCX51 | 3454K053 | 2161062817 | 2018-06-26 | 216106 | 2018-05-31 | high oil consumption | 2018-01-12 | 2018-02-24 | 605 | null | null | 1 | Replaced piston ring set | null | closed | null
2019-01-23 | Fridge House | null | D | Coronet Fish Products | null | KCX3 | 3374K1485 | 2221563171 | 2018-12-05 | 222156 | 2018-11-29 | high oil consumption | 2017-07-24 | 2017-08-10 | 8655 | null | null | 1 | Piston ring set and ORV replaced | null | closed | null
2019-01-23 | Fridge House | null | D | Shimigha Davangere Co Ltd | null | KCX2 | 3364K1619 | 2226723269 | 2019-01-18 | 222672 | 2018-12-15 | kcx oil pressure not develop | 2018-08-27 | 2019-01-18 | ZH | null | null | 5 | oil presure not develops | null | closed | null
2019-01-23 | Cool Comfort Private Limited | West Bengal | D | The Capital Freezing | null | KCX21 | 3424K047 | 2162522838 | 2018-06-30 | 216252 | 2018-06-26 | kcx oil pressure not develops | 2017-09-25 | 2017-11-20 | 1620 | null | null | 2 | Replace pump element | null | closed | null
2019-01-23 | S M Refrigeration | null | D | Shrim Industries Pvt Ltd | Uttarakhand | KCX4 | 3384K1633 | 2204563061 | 2018-01-11 | 220456 | 2018-09-11 | oil carry over | 2017-06-16 | 2018-06-07 | 1320 | null | null | 12 | oil carryover 2.5 L in 24 HRS | null | closed | Piston ring set
2019-01-23 | S M Refrigeration | null | D | Gupta Agro Products | Uttarakhand | KCX6 | 3394K811 | 2235303264 | 2019-01-14 | 223530 | 2019-01-18 | oil carry over | 2017-06-22 | 2018-01-14 | 662 | null | null | 7 | Piston ring sets worn out | null | closed | null
2019-01-23 | S M Refrigeration | null | D | Gupta Agro Products | Uttarakhand | KCX6 | 3394K810 | 2235283263 | 2019-01-14 | 223528 | 2019-01-18 | oil carry over | 2017-06-22 | 2018-01-14 | 560 | null | null | 7 | Cylinder no 04 & 05 piston and liner replaced | null | closed | null
2019-01-23 | S M Refrigeration | null | D | Kishori Kirpa Cold Storage | Uttar Pradesh | KCX6 | 3394K903 | 2181842950 | 2018-08-18 | 218184 | 2018-07-16 | oil lifting | 2017-10-30 | 2018-03-20 | 1689 | null | null | 5 | oil consumption 2 litre / 24 Hrs observed ORV leakage | null | closed | ORV 4 nos.
2019-01-23 | S M Refrigeration | null | D | D K Agarwal Cold Storage | Uttar Pradesh | KC4 | 338K5629 | 2202083062 | 2018-10-11 | 220208 | 2018-08-30 | oil lifting | 2017-10-28 | 2018-02-24 | 2000 | null | null | 4 | ORV leakage | null | closed | ORV Replaced
2019-01-23 | S M Refrigeration | null | D | Patanjali Food & Herbals Haridwar | Uttarakhand | KCX4 | 3384K1529 | 2206503082 | 2018-10-14 | 220650 | 2018-10-17 | oil lifting | 2017-02-28 | 2018-04-25 | 160 | null | null | 2 | Piston ring set worn out | null | closed | Piston ring set
2019-01-23 | Cool Comfort Private Limited | West Bengal | D | Dollon'S Food Products (P) Ltd | West Bengal | KCX6 | 3394K765 | 2219263146 | 2018-11-24 | 221926 | 2018-11-22 | oil pressure not buildup | 2017-03-10 | 2018-04-23 | 1440 | null | null | 1 | KCX oil pump element tang broken | null | closed | null
2019-01-23 | Trade Links | Secunderabad | D | Gangotri Ice House | null | KCX4 | 3384K1971 | 2226043194 | 2018-12-15 | 222604 | 2018-12-13 | overheating of cylinder | 2018-05-29 | 2018-08-30 | 1933 | null | null | 3 | Delivery valve leakage | null | closed | null
2019-01-23 | Parag Marketing Services | null | D | Gadre Marine Export Pvt Ltd | null | KCX72 | 3474K208 | null | null | null | 2019-01-18 | paint peel off | 2018-07-25 | null | ZH | null | null | null | null | null | closed | null
2019-01-23 | Parag Marketing Services | null | D | Gadre Marine Export Pvt Ltd | null | KCX63 | 3464K019 | null | null | null | 2019-01-18 | paint peel off | 2018-06-18 | null | ZH | null | null | null | null | null | closed | null
2019-01-23 | Parag Marketing Services | null | D | Gadre Marine Export Pvt Ltd | null | KCX9 | 3404K099 | null | null | null | 2019-01-18 | paint peel off | 2018-06-12 | null | ZH | null | null | null | null | null | closed | null
2019-01-23 | Kalp Marketing | Gujrat | D | Advance Techno System | null | KCX4 | null | null | null | null | 2019-01-18 | paint peel off | 2018-08-10 | 2018-01-20 | ZH | null | null | 5 | null | null | closed | null
2019-01-23 | Cool Comfort Private Limited | West Bengal | D | Sundarphukhuri CoOperative Society | null | PC2 | 331K3014 | 2226183195 | 2018-12-16 | 22618 | 2018-12-14 | pc2 oil pump seazed | 2018-09-30 | 2018-12-16 | ZH | null | null | 3 | Gear seased into gearbush | null | closed | null
2019-01-23 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Agarwal Frozen Foods | null | KCX72 | 3474K202 | 2231103224 | 2018-12-28 | 223110 | 2018-12-28 | pressure gauge out | 2018-07-12 | 2018-12-21 | ZH | null | null | 5 | Pressure gauge out 16.0 Kg/Cm2 | null | closed | null
2019-01-23 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Agarwal Frozen Foods | null | KCX93 | 3485K039 | 2231063226 | 2018-12-28 | 223106 | 2018-12-28 | pressure gauge out | 2018-09-04 | 2018-12-21 | ZH | null | null | 3 | Replaced pressure gauge 16.0 kg/cm2 | null | closed | null
2019-01-23 | Fridge House | null | D | Chamarajangara Dist Co Operative Milk Products | null | KCX21 | 3424K042 | 2218183154 | 2018-11-27 | 221818 | 2018-01-20 | pressure gauge out | 2017-06-23 | 2018-11-27 | ZH | null | null | 5 | Replaced pressure gauge 16.0 kg/cm2 | null | closed | null
2019-01-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sai Krishna Ice Factory | Andhra Pradesh | KCX4 | 3384K1992 | 2215443158 | 2018-11-29 | 221544 | 2018-11-12 | shaft seal leakage | 2018-06-30 | 2018-11-22 | ZH | null | null | 5 | Replaced shaft seal Orings | null | closed | null
2019-01-23 | Trade Links | Secunderabad | D | Vasavi Ice Industries | null | KCX6 | 3394K1007 | 2211423103 | 2018-10-29 | 221142 | 2018-10-14 | shaft seal leakage | 2018-02-11 | 2018-05-16 | 2554 | null | null | 3 | Replaced shaft seal assly | null | closed | null
2019-02-12 | S M Refrigeration | null | D | Nufarm Frpzen Pvt Ltd | Uttar Pradesh | KC42 | 344K114 | 2218083142 | 2018-11-22 | 221808 | 2018-12-09 | abnormal noise | 2017-12-27 | 2018-03-19 | 2210 | null | null | 3 | Cylinder liner 01&04 wearout/liner cut mark | null | closed | Replaced Cylinder liner,piston,bigend bearings at cylinder no.01&04
2019-02-12 | Geekay Pneumatic Pvt Ltd | null | D | Himalaya Cold Storage | Kerala | KCX3 | 3374K1839 | 2241563288 | 2019-01-29 | 224156 | 2019-01-19 | high oil carryover | 2018-06-12 | 2018-09-14 | 2016 | null | null | 3 | Piston crack | null | open | Piston & piston ring set
2019-02-12 | Cool Comfort Private Limited | West Bengal | D | Pristin Mega Food Park Pvt Ltd | Bihar | KCX4 | 3384K1903 | 2229943223 | 2018-12-28 | 222994 | 2018-12-28 | shaft seal leakage | 2018-03-10 | 2018-12-14 | 26 | null | null | 9 | Shaftseal assly replaced | null | closed | Shaft seal assly
2019-02-19 | Trade Links | Secunderabad | D | Sri Vyashnavi Foods | Telangana | KCX3 | 3374K1511 | 2219023155 | 2018-11-28 | 221902 | 2018-12-01 | abnormal noise | 2017-09-04 | 2018-03-08 | 3263 | null | null | 6 | Replaced cylinder liner & piston ring set | null | closed | Replaced cylinder liner & piston ring set
2019-02-19 | Trade Links | Secunderabad | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2237263280 | 2019-01-23 | 223726 | 2019-01-28 | abnormal noise | 2017-04-23 | 2017-09-18 | 5002 | null | null | 5 | Replaced cylinder liner,delivery valve, piston assly | null | closed | null
2019-02-19 | Trade Links | Secunderabad | D | Sri Sai Rama Industries | null | KCX6 | 3394K1048 | 2236623260 | 2019-01-11 | 223662 | 2019-01-12 | abnormal noise | 2018-03-19 | 2018-08-29 | 1549 | null | null | 5 | Replaced delivery valve ,piston assly | null | closed | null
2019-02-19 | Kalp Marketing | Gujrat | D | Saraf Foods Ltd | Gujrat | KC63 | 346K279 | Email | 2019-02-11 | null | 2019-02-11 | crankcase weld leak at discharge pipe | 2018-06-01 | 2019-02-19 | ZH | null | null | 8 | Welding rectification done | null | closed | null
2019-02-19 | Parag Marketing Services | null | D | Dattaprasad Assosiates | null | KCX3 | 3374K1763 | 2235483283 | 2019-01-24 | 223548 | 2019-01-24 | cylinder overheating | 2018-03-13 | 2018-05-26 | 2425 | null | null | 2 | Replaced delivery valve assly | null | closed | Replaced del valve assly
2019-02-19 | Parag Marketing Services | null | D | Bansi Diary Pvt Ltd | Bhandara | KCX3 | 3374K1793 | 2241123297 | 2019-02-04 | 224112 | 2019-02-04 | cylinder overheating | 2018-04-15 | 2018-06-12 | 1780 | null | null | 2 | Replaced cylinder liner , piston assly | null | closed | null
2019-02-19 | Trade Links | Secunderabad | D | Sri Sai Rama Industries | null | KCX6 | 3394K1048 | 2231143232 | 2018-12-31 | 223114 | 2019-01-01 | cylinder overheating | 2018-03-19 | 2018-08-29 | 1311 | null | null | 5 | Replaced Cylinder liner,piston,del valve ,bearings | null | closed | null
2019-02-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amoli Organics Pvt Ltd | null | KCX4 | 3384K1848 | 2245383314 | 2019-02-09 | 224538 | 2019-02-08 | kcx oil pump tang broken | 2018-02-10 | 2019-02-08 | ZH | null | null | 12 | Replaced oil pump assly | null | closed | null
2019-02-19 | Parag Marketing Services | null | D | Shubham Milk & Milk Products | null | KCX1 | 3354K086 | 2235243262 | 2019-01-14 | 223524 | 2019-01-13 | kcx oil pump tang broken | 2018-08-19 | 2019-01-13 | ZH | null | null | 4 | Replaced oil pump asly | null | closed | null
2019-02-19 | Parag Marketing Services | null | D | Dce Refrifgeration | Pune | KCX4 | 3384K | Email | 2019-02-12 | null | 2019-02-12 | motorpulley keway distance undersize by 0.3 to 0.7 mm | 2019-01-30 | 2019-01-31 | ZH | null | null | 1 | Replaced motor pulley | null | closed | null
2019-02-19 | Parag Marketing Services | null | D | Somnath Milk And Milk Products | Baramati | KCX2 | 3364K1521 | 2225283204 | 2018-12-20 | 222528 | 2018-12-19 | oil carry over | 2018-03-09 | 2018-05-22 | 676 | null | null | 2 | Replaced cylinder liner and piston ring set | null | closed | cylinder liner and piston ring set
2019-02-19 | Trade Links | Secunderabad | D | The Telangana State Dairy | Telangana | KCX2 | 3364K1398 | 2238303268 | 2019-01-17 | 223830 | 2019-01-21 | oil carry over | 2017-09-23 | 2018-02-13 | 982 | null | null | 5 | Replaced piston ring set | null | closed | null
2019-02-19 | Trade Links | Secunderabad | D | Krishna Ice Factory | Andhra Pradesh | KCX3 | 3374K1458 | 2199523037 | 2018-09-28 | 219952 | 2017-06-10 | oil lifting | 2017-06-10 | 2017-09-27 | 4162 | null | null | 3 | Replaced piston ring set | null | closed | Replaced piston ring set
2019-02-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sarna Chemicals Pvt LtdVapi | Gujrat | KCX6 | 3394K1019 | 2227103240 | 2019-01-03 | 222710 | 2019-01-21 | shaft seal leakage | 2018-02-24 | 2018-08-19 | 1051 | null | null | 6 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2019-02-19 | Parag Marketing Services | null | D | Finolex Cabale Limited | Urse, Pune | KCX6 | 3394K808 | 2211943108 | 2018-10-30 | 221194 | 2018-10-30 | shaft seal leakage | 2017-07-14 | 2017-09-28 | 6645 | null | null | 2 | Replaced Shaft seal assly | null | closed | null
2019-02-19 | Parag Marketing Services | null | D | Shukla Dugdhalay | Dhule | KCX2 | 3364K1367 | 2229663215 | 2018-12-25 | 222966 | 2018-12-25 | shaft seal leakage | 2017-07-26 | 2018-04-15 | 2675 | null | null | 9 | Replaced shat seal assly | null | closed | Replaced shaft seal assly
2019-02-19 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Haldiram Frozen Foods | Bhandara | KCX51 | 3454K077 | Email | 2019-02-10 | null | 2019-02-10 | solenoid valve not working | 2018-06-01 | 2019-02-10 | ZH | null | null | 8 | Replaced KCX NO sol valve | null | closed | null
2019-02-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Saraf Foods Ltd | Gujrat | KC6 | 339K3497 | null | null | 223574 | 2019-01-31 | intermediate housing bolts loose. | 2018-04-29 | 2019-01-31 | ZH | null | null | 8 | Intermediate Housisng bolts loose. | null | closed | null
2019-02-24 | Trade Links | null | D | Padmavati Ice And Cold Storage | null | KCX4 | 3384K1919 | 2238943279 | 2019-01-22 | 223894 | 2019-01-22 | abnormal noise | 2018-03-19 | 2018-07-27 | 4200 | null | null | 4 | Ring springs wear out & Discharge valve failure | null | closed | null
2019-02-24 | Morgan | null | E | Hamdan Cold Storage | null | KC63 | 346K258 | null | 2018-12-05 | null | 2018-12-19 | high oil consumption | null | 2018-03-17 | null | null | null | null | oil consumption 5-6 liters/day | null | closed | Piston ring sets
2019-02-24 | Morgan | null | E | Morgan | Pakistan | KC63 | 346K275 | Email | 2018-09-28 | null | 2018-09-28 | paint peel off and colour change at discharge side | null | null | null | null | null | null | null | null | closed | null
2019-02-24 | Parag Marketing Services | null | D | Lupin Limited | Ankleshwar Gujarat | KC84 | 330K45 | 3080 | 2018-10-14 | 220634 | 2018-10-04 | solenoid valve malfuctioning | 2017-08-13 | 2018-10-04 | 24 | null | null | 14 | Replaced sol valves | null | closed | Solenoid valve
2019-02-26 | S M Refrigeration | null | D | Aziz Enterprises | Telangana | KCX42 | 3444K048 | 2237263280 | 2019-01-23 | 223726 | 2019-01-28 | abnormal noise | 2017-04-23 | 2017-09-18 | 5002 | null | null | 5 | Cylinder no. 4 & 5 abnormal sound due to seized. | null | closed | Replaced Liner , Piston , Piston ring set , connecting rod & discharge valve assly .
2019-02-26 | Trade Links | Secunderabad | D | Sri Sai Rama Industries | Andhra Pradesh | KCX6 | 3394K1048 | 2231143232 | 2018-12-31 | 223114 | 2019-01-01 | cylinder overheating | 2018-03-19 | 2018-08-29 | 1311 | null | null | 5 | Cylinder no.2 seized. | null | closed | Replaced Liner , Piston , Piston ring , Buffer spring & kit delivery valve etc.
2019-02-26 | S M Refrigeration | null | D | Kanpur Plastik Ltd | Uttar Pradesh | KCX6 | 3394K1035 | 2248763316 | 2019-02-12 | 224876 | 2019-02-12 | cylinder overheating | 2018-03-06 | 2018-08-25 | 1392 | null | null | 5 | Discharge valve ring spring broken , delivery valve seat damaged. Piston and piston ring set wornout. | null | closed | Replaced Piston , Piston ring set & discharge valve assly.
2019-02-26 | Parag Marketing Services | Pune | D | Bansi Diary Pvt Ltd | Bhandara | KCX3 | 3374K1793 | 2241123297 | 2019-02-04 | 224112 | 2019-02-04 | cylinder overheating | 2018-04-15 | 2018-06-12 | 1780 | null | null | 2 | Piston , piston ring set & liner seized. Delivery valve leakage. | null | closed | Replaced Piston , piston ring set, discharge valve assembly & bearings replaced.
2019-02-26 | Kalp Marketing | Gujrat | D | Sudam Dairy | Gujrat | KCX4 | 3384K1917 | 2244023299 | 2019-02-04 | 224402 | 2019-02-02 | shaft seal leakage | 2018-03-16 | 2018-05-19 | 811 | null | null | 2 | Rotory & staionary seal not match | null | closed | Replaced shaft seal
2019-02-27 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Ambika Sheetgrah Pvt Ltd | Uttar Pradesh | KCX6 | 3394K946 | 2252023333 | 2019-02-20 | 225202 | 2019-02-20 | stop valve tal 100 leakage | 2017-12-30 | 2018-03-01 | 1661 | null | null | 1 | Stop valve leakage | null | closed | Replaced stop valve Tal 100
2019-03-22 | Trade Links | null | D | Vasista Marine | Andhra Pradesh | KCX93 | 3485K045 | 2254363347 | null | 225436 | 2019-02-28 | delivery valve leakage | 2018-11-20 | null | ZH | null | null | 3 | Replaced delivery valve | null | closed | Delivery valve replaced
2019-03-22 | Parag Marketing Services | null | D | Bloom Agrotech | Pune | KCX3 | 3374K1910 | 2251263334 | 2019-02-21 | 225126 | 2019-02-21 | delivery valve leakage | 2018-09-30 | 2018-11-03 | 1486 | null | null | 2 | Replaced delivery valve | null | closed | Delivery valve replaced
2019-03-22 | Trade Links | null | D | Covalent Laboratories Pvt Ltd | Telangana | KCX72 | 3474K135 | 2249423328 | 2019-02-18 | 224942 | 2019-02-18 | delivery valve stuck in liner | 2017-12-26 | 2019-02-18 | ZH | null | null | 14 | Replaced delivery valve & liner | null | closed | Delivery valve replaced
2019-03-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sarna Chemicals Pvt Ltd | Gujrat | KCX6 | 3394K1019 | 2245263313 | 2019-02-09 | 224526 | 2019-02-06 | shaft seal leakage | 2019-02-24 | 2018-08-19 | 1583 | null | null | 6 | Replaced Shaft Seal assly | null | closed | Replaced shaft seal assly
2019-03-23 | Trade Links | null | D | Sri Vyshanvi Foods P Ltd | Telangana | KCX3 | 3374K1511 | 2267403363 | 2019-03-07 | 226740 | 2019-03-07 | abnormal noise | 2017-09-04 | 2018-03-08 | 4265 | null | null | 6 | Cylinder wornout and abnormal noise | null | closed | Replaced Cylinder liner , Piston ring set, Gudgeon pin , Con rod bush & Bearing bush.
2019-03-23 | Trade Links | null | D | Sri Venkateshwara Ice Factory | Andhra Pradesh | KCX6 | 3394K1115 | 2268963371 | 2019-03-11 | 226896 | 2019-03-11 | abnormal noise | 2018-07-06 | 2018-12-04 | 1575 | null | null | 5 | Cylinder no.1 & 3 buffer spring shrink by 16mm & delivery valve back leakage. | null | closed | Replaced Buffer spring , Kit delivery valve.
2019-03-23 | Kalp Marketing | Gujrat | D | Indradhanush Ice & Cold Storage | Gujrat | KCX4 | 3384K1987 | 229383327 | 2019-02-18 | 224938 | 2019-02-16 | delivery valve leakage | 2018-06-16 | 2018-10-11 | 275 | null | null | 4 | Discharge valve leakage two times by replacing kit. | null | closed | Delivery valve replaced
2019-03-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Transpek Industries Limited | Gujrat | KCX2 | 3364K1425 | 2251763331 | 2019-02-19 | 225176 | 2019-02-20 | knocking sound & overheating | 2017-11-17 | 2018-10-10 | 1540 | null | null | 11 | Cylinder no. 2 seized due to DV leakage. | null | closed | Replaced Piston , Brg bush , Piston ring set & Kit delivery valve .
2019-03-23 | Parag Marketing Services | null | D | Tasty Bytes Bhandgaon | Pune | KCX72 | 3474K251 | null | null | null | 2019-03-18 | paint peel off | 2018-12-10 | 2019-03-10 | ZH | null | null | 3 | null | null | null | null
2019-03-27 | Geekay Pneumatic Pvt Ltd | Kerala | D | Nas Fisheries Pvt Ltd | Kerala | KC72 | 347K982 | 2253803352 | 2019-03-02 | 225380 | 2019-03-01 | fitting leakage | 2018-01-06 | 2019-03-01 | 3 | null | null | 2 | Blank FSR | null | closed | Replaced gauge board female tee
2019-03-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sajjan India Limited | Gujrat | KCX93 | 3485K012 | 2246583306 | 2019-02-07 | 224658 | 2018-08-03 | hp cylinder no. 4 seized | 2017-12-11 | 2018-08-03 | 4 | null | null | 8 | Blank FSR | null | closed | Replaced cylinder assembly
2019-03-27 | Cool Comfort Private Limited | West Bengal | D | Maa Nalini Cold Storage | West Bengal | KCX4 | 3384K2159 | 2273503391 | 2019-03-19 | 227350 | 2019-03-19 | kcx pump element broken | 2019-01-11 | 2019-03-08 | 80 | null | null | 2 | Pump element was broken due to small gear seized. | null | closed | Replaced pump element
2019-03-27 | Fridge House | null | D | Divine Spirit Ice & Cold Storage | Karnataka | KCX6 | 3394K1067 | 2270443375 | 2019-03-14 | 227044 | 2019-03-14 | oil carry over | 2018-04-09 | 2018-09-01 | 2484 | null | null | 5 | Piston & Piston ring set damaged and wornout . | null | closed | Replaced Piston 2 nos & Piston ring set 03 nos.
2019-03-27 | Trade Links | Secunderabad | D | Siri Cold Storage | Andhra Pradesh | KCX3 | 3374K1663 | 2268903366 | 2019-03-09 | 226890 | 2019-03-09 | oil leakage from filter manifold. | 2018-01-10 | 2018-02-12 | 1107 | null | null | 1 | Oil leakage | null | closed | Replaced manifold
2019-03-27 | Trade Links | Secunderabad | D | Siri Cold Storage | Andhra Pradesh | KCX2 | 3364K1476 | 2268883369 | 2019-03-11 | 226888 | 2019-03-11 | oil leakage from filter manifold. | 2018-01-10 | 2018-02-14 | 1270 | null | null | 1 | Oil leakage from manifold due to threading spoil.( Excess tightning) | null | closed | Replaced manifold
2019-03-27 | Cool Comfort Private Limited | West Bengal | D | Maa Nalini Cold Storage | West Bengal | KCX6 | 3394K1253 | 2273963390 | 2019-03-19 | 227396 | 2019-03-19 | oil pressure not buildup | 2019-01-11 | 2019-03-08 | 46 | null | null | 2 | Pump element was broken due to small gear seized. | null | closed | Replaced pump element
2019-03-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Saraf Foods Ltd | Gujrat | KC9 | 340K404 | 2267923374 | 2019-03-12 | 226792 | 2019-03-07 | shaft seal leakage | 2018-05-20 | 2019-01-31 | 159 | null | null | 8 | FSR Blank & Compressor alignment value not given | null | closed | Replaced shaft seal
2019-03-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ganraaj Cold Storage | Gujrat | KCX3 | 3374K1977 | 2269383372 | 2019-03-11 | 226938 | 2019-03-12 | shaft seal leakage | 2018-12-15 | 2019-02-13 | 9 | null | null | 2 | Shaft seal worn out & Oring expanded. | null | closed | Replaced shaft seal assly
2019-03-27 | Parag Marketing Services | Pune | D | Jain Farma Fresh Foods Ltd | Jalgaon | KCX21 | 3424K045 | 2217983312 | 2019-02-08 | 221798 | 2019-02-08 | shaft seal leakage | 2017-08-07 | 2018-05-26 | 1525 | null | null | 9 | Failure due to operational problem. | null | closed | Replaced all spares except crankcase
2019-03-27 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Haldiram Foods International Pvt Ltd | Nagpur | KCX51 | 3454K078 | 2245123339 | 2019-02-25 | 224512 | 2019-02-15 | solenoid valve not working. in visit of branch engineer no problem of solenoid valve | 2018-06-23 | 2019-02-15 | 3 | null | null | 8 | Replaced NO solenoid valve but observed ok in inhouse analysis. | null | closed | Replaced NO Solenoid valve
2019-04-26 | Multivista Global Pvt Ltd | Tamil Nadu | D | Aavin Milk Chilling Center | Tamil Nadu | KCX2 | 3364K1550 | 2266803364 | 2019-03-08 | 226680 | 2019-03-06 | abnormal noise | 2018-04-09 | 2018-07-01 | 2497 | null | null | 3 | Direct cylinder piston crack | null | closed | Replaced Piston & Piston ring set.
2019-04-26 | Trade Links | Secunderabad | D | Sri Sai Rama Industries | Telangana | KCX6 | 3394K1048 | 2284243424 | 2019-04-08 | 228424 | 2019-04-05 | abnormal noise | 2018-03-19 | 2018-08-29 | 1286 | null | null | 5 | Buffer spring , Piston , Discharge valve ring spring broken & Liner damaged. | null | closed | Replaced Cylinder liner , Piston , Piston rings , Gudgeon pin , Discharge valve buffer spring & bushing .
2019-04-26 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hari Orgochem | Savli, Vadodara | KCX72 | 3474K210 | Mail | 2019-04-23 | null | 2019-04-23 | additional intermediate housing bolt found in crankcase. | 2018-07-01 | 2019-04-23 | ZH | null | null | 9 | One additional intermediate bolt observed in crankcase as a loose condition. | null | closed | null
2019-04-26 | S M Refrigeration | null | D | Janta Cold Storage | Uttar Pradesh | KCX2 | 3364K1615 | 2282563414 | 2019-04-01 | 228256 | 2019-04-01 | kcx pump element broken | 2018-08-22 | 2019-03-12 | 113 | null | null | 7 | Pump element broken | null | closed | Replaced Pump element
2019-04-26 | Cool Comfort Private Limited | West Bengal | D | Malda Samaby Himghar Ltd | West Bengal | KCX4 | 3384K2198 | 2285783426 | 2019-04-09 | 228578 | 2019-04-09 | kcx pump element broken | 2019-02-10 | 2019-03-11 | 419 | null | null | 1 | Pump element broken | null | closed | Replaced Pump element
2019-04-26 | S M Refrigeration | null | D | Raja Shree Cold Storage | Uttar Pradesh | KCX3 | 3374K2004 | 2281523423 | 2019-04-05 | 228152 | 2019-04-06 | kcx pump element broken | 2019-01-15 | 2019-02-18 | 368 | null | null | 1 | Pump element broken | null | closed | Replaced Pump element
2019-04-26 | S M Refrigeration | null | D | Jay Govinda Cold Storage | Uttar Pradesh | KC6 | 339K3489 | 2285303427 | 2019-04-09 | 228530 | 2019-04-17 | low oil pressure | 2018-02-12 | 2019-04-17 | ZH | null | null | 14 | Oil pressure not increase more than 1 Kg/cm2 & Scoring at cover & gears within 4 Hrs. | null | closed | Replaced pump assembly
2019-04-26 | Parag Marketing Services | Pune | D | Jain Farma Fresh Foods Ltd | Jalgaon | KCX21 | 3424K045 | 2254243348 | 2019-02-28 | 225424 | 2019-02-28 | oil carry over | 2017-08-07 | 2018-05-26 | 1822 | null | null | 9 | Only 1 piston ring set replaced. | null | closed | 1 piston ring set replaced.
2019-04-26 | Trade Links | Secunderabad | D | Al-Kabeer Exports Pvt Ltd | Telangana | KCX9 | 3404K103 | 2284583425 | 2019-04-09 | 228458 | 2019-04-18 | oil lifting | 2018-08-27 | 2018-11-22 | 2946 | null | null | 3 | Discharge valve failure , Piston & piston rings were wornout abnormally for 2 pistons. Piston no.2 seized & Piston 4 Cracked. | null | closed | Replaced Piston , Piston rings , Bush connecting rod,Gudgeon pin Discharge valve , Buffer spring , ORV & connecting rod assembly.
2019-04-26 | Kirloskar Pneumatic Co Ltd | Uttar Pradesh | D | Himalaya Cold Storage | Uttar Pradesh | KCX3 | 3374K1726 | 2289863444 | 2019-04-17 | 228986 | 2019-04-17 | oil pressure not buildup | 2018-02-23 | 2018-07-06 | 321 | null | null | 5 | Pump element broken | null | closed | Replaced pump element
2019-04-26 | Trade Links | Secunderabad | D | Sri Veda Cold Storage | Andhra Pradesh | KCX2 | 3364K1729 | 2288823437 | 2019-04-15 | 228882 | 2019-04-20 | op cut out malfunctoning. | 2019-02-08 | 2019-04-04 | 358 | null | null | 2 | OP Cut out malfunctoning. | null | closed | Replaced OP Cut out
2019-04-26 | Kalp Marketing | Gujrat | D | Sudam Dairy | Gujrat | KCX4 | 3384K1917 | 2274243398 | 2019-04-25 | 227424 | 2019-03-23 | shaft seal leakage | 2018-03-16 | 2018-05-19 | 250 | null | null | 2 | Shaft seal leakage due to Oring damaged | null | closed | Oring kit
2019-04-26 | Kalp Marketing | Gujrat | D | Akshar Cold Storage | Gujrat | KCX3 | 3374K1543 | 2253303378 | 2019-03-14 | 225330 | 2019-03-13 | shaft seal leakage | 2017-10-17 | 2017-12-30 | 1138 | null | null | 2 | Shaft seal leakage due to Oring damaged. | null | closed | Oring kit
2019-04-26 | Trade Links | Secunderabad | D | Sanghi Polymers Pvt Ltd | Telangana | KCX2 | 3364K1707 | 228703438 | 2019-04-15 | 228780 | 2019-04-23 | wrong cut out fitted in gauge panel board | 2019-01-23 | 2019-04-23 | ZH | null | null | 3 | 2 nos LP Cut outs fitted instead of 1HP cut out & 1 LP Cutout. | null | closed | Replaced LP Cut out with HP Cut out
2019-05-12 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX6 | 3394K958 | 2251583417 | 2019-04-03 | 225158 | 2019-04-16 | delivery valve leakage & solenoid coil failure | 2017-12-27 | 2019-04-16 | ZH | null | null | 16 | Delivery valve back leaking and Solenoid valve coil failure. | null | closed | Replaced delivery valve & coil
2019-05-17 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ambika Ice Factory | Gujrat | KCX6 | 3394K1264 | 2287083430 | 2019-04-10 | 228708 | 2019-04-13 | abnormal noise | 2019-01-23 | 2019-02-04 | 1209 | null | null | 1 | Abnormal sound from cylinder no.5 , Delivery valve leakage & Piston liner seized. | null | closed | Replaced DV , Piston , Piston rings , Gudgeon pin , Liner , Bushing.
2019-05-17 | Trade Links | Secunderabad | D | Sri Rama Krishna Ice Factory | Andhra Pradesh | KCX3 | 3374K1630 | 2286223429 | 2019-04-10 | 228622 | 2019-04-09 | cylinder overheating | 2017-12-18 | 2018-05-11 | 4497 | null | null | 5 | Cylinder No.1 overheat due to delivery valve leak back resulting into cylinder seized. This is 3rd time problem. | null | closed | Replaced cylinder assembly.
2019-05-17 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX72 | 3474K186 | 2285943454 | 2019-04-24 | 228594 | 2019-04-24 | delivery valve leakage | 2018-05-30 | 2019-03-20 | 40 | null | null | 10 | Cylinder no.4 Delivery valve leakage. | null | closed | Replaced delivery valve
2019-05-17 | Trade Links | Secunderabad | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1951 | 2286963435 | 2019-04-12 | 228696 | 2019-04-12 | oil carry over | 2018-04-16 | 2018-08-24 | 1258 | null | null | 4 | Total 6 pistons had crack. | null | closed | Replaced piston & piston rings
2019-05-17 | Kirloskar Pneumatic Co Ltd | New Delhi | D | R K Frozen Foods | Uttarakhand | KCX72 | 3474K226 | 2294583457 | 2019-04-25 | 229458 | 2019-04-25 | oil pressure not buildup | 2018-10-03 | 2019-01-28 | 801 | null | null | 3 | Purging problem at initial starting of compressor. | null | closed | Replaced KCX Pump assembly
2019-05-17 | Parag Marketing Services | Pune | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX72 | 3474K173 | 2288363436 | 2019-04-14 | 228836 | 2019-04-14 | oil pressure not buildup | 2018-03-19 | 2018-12-07 | 1942 | null | null | 9 | Air purging problem due to wearing of internal gaer & cover also clearances incresased. | null | closed | Replaced pump assembly.
2019-05-17 | S M Refrigeration | New Delhi | D | Kapoor Preservation Llp | Uttar Pradesh | KCX2 | 3364K1611 | 2286323431 | 2019-04-10 | 228632 | 2019-04-25 | oil pressure not buildup | 2018-08-18 | 2019-03-17 | 709 | null | null | 7 | Air purging problem. | null | closed | Replaced KCX Pump assembly
2019-05-17 | Shree Engineering Services | Chhattisgarh | D | Sandeep Cold Storage | Chhattisgarh | KCX3 | 3374K2031 | 2284183446 | 2019-04-18 | 228418 | 2019-04-20 | oil pressure not buildup | 2019-02-06 | 2019-03-01 | 359 | null | null | 1 | Pump element seized & broken | null | closed | Replaced pump element
2019-05-17 | Cool Comfort Private Limited | West Bengal | D | Kandurai Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K1212 | 2297643471 | 2019-05-06 | 229764 | 2019-05-13 | over heating | 2018-11-24 | 2019-03-10 | 784 | null | null | 4 | Delivery valve ring spring broken / Leakage | null | closed | Replaced Kit delivery valve , Piston , Piston rings , Gudgeon pin , Bush.
2019-05-17 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX63 | 3464K016 | 2291923455 | 2019-04-24 | 229292 | 2019-04-24 | over heating | 2018-05-30 | 2019-03-20 | 45 | null | null | 10 | Cylinder no.4 Delivery valve leakage. | null | closed | Replaced Delivery valve
2019-05-17 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Micas Organic Limited | Gujrat | KCX6 | 3394K1165 | 2287943440 | 2019-04-16 | 228794 | 2019-04-13 | overheating of body & head. | 2018-09-05 | 2018-09-26 | 1578 | null | null | 1 | Discharge valve leakage due to ring spring broken & one piston hair crack. | null | closed | Replaced DV , Piston , Piston rings & All head gaskets.
2019-05-17 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ahuja Ice Ambernathe Pvt Ltd | Thane | KC3 | 337K4762 | 2281803418 | 2019-04-03 | 228180 | 2019-04-01 | piston crack | 2018-06-08 | 2018-07-03 | 3741 | null | null | 1 | Piston crack & delivery valve leakage | null | closed | Replaced Piston , piston rigs , & Kit delivery valve.
2019-05-17 | Kalp Marketing | Gujrat | D | Akshar Cold Storage | Gujrat | KCX3 | 3374K1543 | 2248403335 | 2019-02-21 | 224840 | 2019-02-21 | shaft seal leakage | 2017-10-17 | 2017-12-30 | 1088 | null | null | 2 | Oring wornout | null | closed | Replaced Oring kit
2019-05-17 | Kalp Marketing | Gujrat | D | Rewell Cold Storage | Gujrat | KCX3 | 3374K1710 | 2254303370 | 2019-03-11 | 225430 | 2019-03-09 | shaft seal leakage | 2018-02-13 | 2018-04-09 | 286 | null | null | 2 | Shaft seal wornout | null | closed | Replaced new shaft seal
2019-05-17 | Trade Links | Goa | D | Jay Ice Bank | Goa | KCX3 | 3374K1541 | 2284443422 | 2019-04-05 | 228444 | 2019-04-05 | shaft seal leakage | 2017-10-14 | 2018-03-16 | 5588 | null | null | 5 | Shaft seal leakage due to dirty oil | null | closed | Replaced Oring kit
2019-05-22 | Trade Links | Secunderabad | D | Sri Venkteswara Cold Storage Ap | null | KCX2 | 3364K1566 | 2301363477 | 2019-05-10 | 230136 | 2019-05-10 | cylinder overheating | 2018-04-28 | 2018-08-05 | 3031 | null | null | 4 | Delivery valve ring/spring broken & stroke limitor wornout | null | closed | Repalaced Kit delivery valve & Delivery stroke limitor
2019-05-22 | Kalp Marketing | Gujrat | D | Rohra Plant & Packaging P Ltd | Gujrat | KCX51 | 3454K101 | 2279923405 | 2019-03-27 | 227992 | 2019-03-27 | cylinder overheating cyl 4 | 2019-02-12 | 2019-03-22 | ZH | null | null | 1 | Overheating due to delivery valve leakage | null | closed | Replaced DV
2019-05-22 | Kalp Marketing | Gujrat | D | Rohra Plant & Packaging P Ltd | Gujrat | KCX51 | 3454K101 | 2285903439 | 2019-04-16 | 228590 | 2019-04-16 | cylinder overheating cyl 5 | 2019-02-12 | 2019-03-22 | 60 | null | null | 1 | Overheating due to delivery valve leakage | null | closed | Replaced DV
2019-05-22 | Fridge House | null | D | Vijay Sharan Cold Storage Pvt Ltd | Karnataka | KCX3 | 3374K1979 | 2299863478 | 2019-05-10 | 229986 | 2019-05-10 | high oil consumption | 2018-12-17 | 2019-02-12 | 1066 | null | null | 2 | Cylinder no. 1 oil throw due to piston rings wornout & ORV Leakage. | null | closed | Cylinder no. 1 oil throw due to piston rings wornout & ORV Leakage.
2019-05-22 | Parag Marketing Services | null | D | Somnath Milk And Milk Products | Baramati | KCX2 | 3364K1521 | 2293523470 | 2019-05-06 | 229352 | 2019-05-06 | knocking / abnormal sound | 2018-03-09 | 2018-05-22 | 1199 | null | null | 2 | DV Ring spring kit broken & valve damaged, Liner step cut mark | null | closed | Replaced DV & Cylinder Liner
2019-05-22 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Lupin Limited | Tarapur | KCX9 | 3404K102 | 2289743466 | 2019-05-03 | 228974 | 2019-05-01 | loading & unloading problem | 2018-08-12 | 2018-12-05 | 2098 | null | null | 4 | Piston , Piston rings - 8(Crack) , Tap bolt & liner springs - 4 | null | closed | Replaced Piston , Piston rings 8(Crack) , Tap bolt & liner springs 4 etc
2019-05-22 | Trade Links | Secunderabad | D | Srinidhi Products | Andhra Pradesh | KCX2 | 3364K1684 | Email | 2019-05-27 | 229220 | 2019-04-24 | motor pulley bore oversize by 1mm | 2018-12-12 | null | ZH | null | null | 4 | Motor pulley bore oversize by 1mm | null | closed | Replaced motor pulley
2019-05-22 | S M Refrigeraion Pvt Ltd | null | D | Govardhan Sheetalaya Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1241 | 2287383501 | 2019-05-20 | 228738 | 2019-04-11 | oil lifting | 2018-12-30 | 2019-03-22 | 419 | null | null | 3 | Cylinder no. 2 , ORV Leakage. | null | closed | Replaced ORV
2019-05-22 | Kalp Marketing | Gujrat | D | Shree Nakoda Cold Storage | Madhya Pradesh | KCX3 | 3374K1666 | 2289103445 | 2019-04-18 | 228910 | 2019-04-18 | oil pressure not buildup | 2018-01-10 | 2018-03-20 | PC | null | null | 2 | Oil pump element broken | null | closed | Replaced Pump element
2019-05-22 | Kalp Marketing | Gujrat | D | Rspl Limited | Madhya Pradesh | KCX3 | 3374K1653 | 2293563459 | 2019-04-30 | 229356 | 2019-04-27 | oil pressure not buildup | 2018-01-08 | 2018-11-17 | 733 | null | null | 10 | Oil pressure not develop | null | closed | Replaced Pump Assembly
2019-05-22 | Fridge House | null | D | Mtc Cold Storage | Karnataka | KCX2 | 3364K1665 | 2273443442 | 2019-04-17 | 227344 | 2019-04-17 | oil pressure not buildup | 2018-11-12 | 2019-02-23 | 568 | null | null | 3 | Oil pressure not develop due to drive shaft broken. | null | closed | Replaced Pump element
2019-05-22 | Trade Links | Secunderabad | D | Masqati Dairy Products | Telangana | KCX51 | 3454K1092 | 2300943487 | 2019-05-16 | 230094 | 2019-05-16 | oil pressure not buildup | 2018-10-30 | 2018-11-24 | 1870 | null | null | 1 | Abnormal wear out of element | null | closed | Replaced Pump element
2019-05-22 | S M Refrigeraion Pvt Ltd | null | D | Stellar Gold Chain Inc | Uttarakhand | KCX4 | 3384K2000 | 2297623473 | 2019-05-07 | 229762 | 2019-05-03 | oil pressure not buildup | 2018-07-01 | 2018-12-06 | 685 | null | null | 5 | Blank FSR - Oil pump element failure | null | null | null
2019-05-22 | Hss Solution Pvt Ltd | null | D | Prem Kripa Udyog Pvt Ltd | Rajastan | KCX4 | 3384K2140 | 2302543479 | 2019-05-13 | 230254 | 2019-05-13 | shaft seal leakage | 2018-12-30 | 2019-02-07 | 795 | null | null | 2 | Shaft seal wornout | null | closed | Replaced Shaft seal assembly
2019-05-22 | Parag Marketing Services | null | D | Sonali Ice Factory | Sangli | KCX2 | 3364K1416 | 2297163476 | 2019-05-08 | 229716 | 2019-05-08 | shaft seal leakage | 2017-11-28 | 2017-12-09 | 4200 | null | null | 1 | Shaft seal wornout | null | closed | Replaced Shaft seal assembly
2019-05-29 | Trade Links | Secunderabad | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1950 | 2303983488 | 2019-05-16 | 230398 | 2019-05-22 | abnormal noise | 2018-04-16 | 2018-08-25 | 2926 | null | null | 4 | Cylinder no.1 piston seized crack & 2,3 Liner cut marks. Delivery valve leakage | null | closed | Replaced DV , Piston , Liner , Piston ring sets, Bufferspring etc.
2019-05-29 | Parag Marketing Services | null | D | Royal Food Stuffs Pvt Ltd | Karad | KCX72 | 3474K270 | 2305683514 | 2019-05-27 | 230568 | 2019-05-27 | air purging problem | 2019-03-09 | 2019-05-15 | 31 | null | null | 2 | Oil pressure not develop & SV leakage HP | null | closed | Replaced Oil pump assembly & Pump element.
2019-05-29 | Hss Solution Pvt Ltd | null | D | United Breweries Ltd | Rajastan | KCX9 | 3404K114 | 2303743498 | 2019-05-20 | 230374 | 2019-05-27 | coupling problem disk pack broken | 2018-10-22 | 2019-01-18 | 795 | null | null | 3 | Replaced Diskpack D640022214 | null | closed | Replaced Diskpack D640022214
2019-05-29 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2304563499 | 2019-05-20 | 230456 | 2019-05-16 | coupling problem disk pack broken | 2018-09-12 | 2019-02-08 | 33 | null | null | 5 | Replaced Diskpack D640022214 | null | closed | Replaced Diskpack D640022214
2019-05-29 | Multivista Global Pvt Ltd | Tamil Nadu | D | Ninnas Pvt Ltd | Tamil Nadu | KCX3 | 3374K1629 | 2289043450 | 2019-04-20 | 228904 | 2019-04-20 | knocking / abnormal sound | 2017-12-18 | 2018-06-22 | 3029 | null | null | 6 | Piston damage and customer not maintain correct soresponding suction pressure also suction line not insulated. | null | closed | Replaced Piston , Piston ring set , gudgeon pin , bush con rod & bearings.
2019-05-29 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sajjan India Limited | Gujrat | KCX93 | 3485K011 | 2296523465 | 2019-05-02 | 229652 | 2019-05-02 | oil carry over | 2017-12-11 | 2018-08-03 | 2688 | null | null | 8 | Cylinder no.1 Piston rings broken , piston and liner wornout. | null | closed | Replaced Liner , Piston , Piston ring set and Oil pump assembly was erlier replaced for low oil pressure problem.
2019-05-29 | S M Refrigeraion Pvt Ltd | null | D | Govardhan Sheetalaya Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1241 | 2303203500 | 2019-05-20 | 230320 | 2019-05-14 | oil lifting | 2018-12-30 | 2019-03-22 | 672 | null | null | 3 | FSR Blank - Replaced ORV | null | closed | Replaced ORV
2019-05-29 | Kalp Marketing | Gujrat | D | Gopinath Chem Tech Limited | Gujrat | KCX4 | 3384K2094 | 2299443492 | 2019-05-18 | 229944 | 2019-05-18 | overheating compressor | 2018-10-19 | 2019-03-09 | ZH | null | null | 5 | Safety vaalve teflon ring replaced within 12 hours due to overheating. | null | closed | Replaced safety valve teflon ring
2019-05-29 | S M Refrigeraion Pvt Ltd | null | D | Samrath Ice & Milk Chilling Centre | Uttar Pradesh | KCX2 | 3364K1609 | 2302943484 | 2019-05-15 | 230294 | 2019-05-15 | pump element broken | 2018-08-14 | 2019-05-15 | 3 | null | null | 9 | Liquid ammonia entered in compressor. | null | closed | Replaced pump element
2019-05-29 | Trade Links | Secunderabad | D | Aditya Industries | Andhra Pradesh | KCX6 | 3394K1259 | 2293083467 | 2019-05-03 | 229308 | 2019-05-03 | retainer plate bolt threading damaged | 2019-01-21 | 2019-05-03 | ZH | null | null | 4 | Retainer plate bolt threading damaged | null | closed | Replaced retainer plate assly
2019-05-29 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Lupin Limited | Tarapur | KCX9 | 3404K102 | 2305923497 | 2019-05-20 | 230592 | 2019-05-20 | tal valve & sfaety valve leakage | 2018-08-12 | 2018-12-05 | 2190 | null | null | 4 | Replaced Teflon for both tal valve & safety valve and Solenoid valve coil. | null | closed | Replaced Teflon for both tal valve & safety valve and Solenoid valve coil.
2019-06-07 | Geekay Pneumatic Pvt Ltd | Kerala | D | Busthan Al-Wathaniya Co Ltd | Kerala | KCX72 | 3474K121 | 2224903203 | 2018-12-19 | 222490 | 2018-12-19 | cylinder overheating | 2017-09-19 | 2018-12-19 | 2 | null | null | 3 | Piston & Piston ring set damaged | null | closed | Replaced Piston & Piston rings
2019-06-07 | S M Refrigeration | null | D | Tirupati Cold Storage | Uttar Pradesh | KCX6 | 3394K1171 | 2305463513 | 2019-05-26 | 230546 | 2019-05-30 | high oil consumption | 2018-09-14 | 2019-03-01 | 581 | null | null | 6 | Oil throw from cylinder no. 1&6 | null | closed | Replaced liner , Piston , Piston rings , Bearings , ORV & DV
2019-06-07 | Trade Links | Secunderabad | D | Sri Bhanu Ice Industries | Andhra Pradesh | KCX3 | 3374K1817 | 2303763494 | 2019-05-18 | 230376 | 2019-05-18 | high oil consumption | 2018-05-21 | 2018-07-07 | 5599 | null | null | 2 | Discharge valve leakage & ORV Leakage | null | closed | Replaced dishcharge valve & ORV
2019-06-07 | S M Refrigeration | null | D | Ss Tomer Sheetgrah Pvt Ltd | Uttar Pradesh | KC3 | 337K4755 | 2276543403 | 2019-03-26 | 227654 | 2019-03-26 | knocking / abnormal sound | 2018-01-23 | 2019-03-26 | 1 | null | null | 2 | Customer run compressor himself / mishandling . Knocking sound due to delivery valve leakage & Buffer spring shrink. | null | closed | Replaced discharge valve & Buffer spring
2019-06-07 | S M Refrigeration | null | D | Varun Beverage Limited | Uttar Pradesh | KCX6 | 3394K1245 | 2303543496 | 2019-05-20 | 230354 | 2019-05-14 | oil pressure not buildup | 2019-01-13 | 2019-04-05 | 565 | null | null | 3 | Blank FSR - Oil pump element failure | null | closed | Replaced pump element
2019-06-07 | S M Refrigeration | null | D | Rewa Preservation Ltd | Uttar Pradesh | KCX4 | 3384K2055 | 2303063516 | 2019-05-27 | 230306 | 2019-05-14 | oil pressure not buildup | 2018-08-31 | 2019-03-15 | 581 | null | null | 7 | Oil pump element broken | null | closed | Replaced pump element
2019-06-07 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | V S K Ice Maker | Gujrat | KCX3 | 3374K2100 | 2300903502 | 2019-05-21 | 230090 | 2019-05-18 | pump element broken | 2019-05-04 | 2019-05-18 | 4 | null | null | 1 | Within 3 hours , oil pressure not develop/drop due to element shaft broken.This failure due to suction cloth bag badly tornout , heavy dust entered in to pump. | null | closed | Replaced pump element.
2019-06-15 | Trade Links | Secunderabad | D | Tagoor Labaratories | null | KCX63 | 3464K036 | 2298943490 | 2019-05-17 | 229894 | 2019-05-06 | abnormal noise | 2018-12-28 | 2019-05-17 | ZH | null | null | 5 | checked all para meters are found ok taken trail run of compressor oil pressure developed up to 2kgcm square but taking direct load from lp calendar no5 so opened no5 cylinder checked all observed lines loading pins gone dwon then opened liner assly observed one tap bolt is broken tap bolt should be change for compressor running | null | closed | Replaced Tap Bolt Liner Assly & Piston & Piston Ring Set Discharge Valve Assly & Ring Suction Valve & Valve Spring Suction & Buffer Spring & Gudgeon Pin
2019-06-15 | Trade Links | Secunderabad | D | Sri Venkateswara Ice & Cold Storage | null | KCX4 | 3384K1784 | 2322843527 | 2019-06-01 | 232284 | 2019-06-01 | abnormal noise & oil lifting | 2017-12-29 | 2018-02-05 | 2524 | null | null | 2 | Abnormal Sound In Compressor While Running & Delivery Valve Leakage & Buffer Spring Hight Down & Oil Filter Damage | null | closed | Replaced Gudgeon Pin & Piston & Piston Ring Set & Descharge Valve Assly & Buffer Spring & Bearing Bush Big End Con Rod
2019-06-15 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX72 | 3474K186 | 2323303537 | 2019-06-06 | 232330 | 2019-06-05 | compressor over heating | 2018-05-30 | 2019-03-20 | 150 | null | null | 10 | Change Piston & Piston Ring Set | null | closed | Replaced Lock Plate Con Rod & Inter. HSG Bolt & Piston Ring Set & Piston.
2019-06-15 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2329363549 | 2019-06-11 | 232936 | 2019-06-11 | coupling problem | 2018-09-12 | 2019-02-08 | 0 | null | null | 5 | Blank FSR | null | closed | Replaced Diskpack D640022214
2019-06-15 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K108 | 2329603551 | 2019-06-11 | 232960 | 2019-06-11 | coupling problem | 2018-09-12 | 2019-02-08 | PC | null | null | 5 | Blank FSR | null | closed | Replaced Diskpack D640022214
2019-06-15 | Trade Links | Secunderabad | D | Godavari Ice & Cold Storage | Andhra Pradesh | KCX6 | 3394K939 | 2323583538 | 2019-06-07 | 232358 | 2019-06-08 | cylinder overheating | 2017-12-13 | 2018-05-07 | 6288 | null | null | 5 | Over Heating at Cylinder no. 02 | null | closed | Replaced Spring Curtain, Liner Assly & Bearing Bush Big End Con Rod & Valve Spring Suction & Gudgeon Pin & Bush Connecting Rod & Cyliner Liner & Piston & Piston Ring Set & Buffer Spring & Descharge Valve Assly
2019-06-15 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX72 | 3474K187 | 2305363510 | 2019-05-23 | 230536 | 2019-05-23 | delivery valve assembly leakage | 2018-05-30 | 2019-03-20 | 200 | null | null | 10 | Delivery Valve assly Leakage | null | closed | Replaced Delivery Valve Assly
2019-06-15 | Fridge House | null | D | Vijay Sharan Cold Storage Pvt Ltd | Karnataka | KCX3 | 3374K1979 | 2325123542 | 2019-06-08 | 232512 | 2019-06-06 | high oil consumption | 2018-12-17 | 2019-02-12 | 1180 | null | null | 2 | Found gap in Piston Ring was in Cyl. No. 01 0.05mm & 1.2mm in Compression Ring & Oil Scraper Ring | null | closed | Replaced Piston Ring Set
2019-06-15 | Trade Links | Secunderabad | D | Saraca Laboratories Limited | Andhra Pradesh | KCX84 | 3305K004 | 2318683515 | 2019-05-27 | 231868 | null | knocking / abnormal sound | 2018-12-30 | 2019-05-08 | 65 | null | null | 5 | Blank FSR - Delivery valve back leaking | null | closed | Replaced KIT Delivery Valve
2019-06-15 | Cool Comfort Private Limited | West Bengal | D | Dhirendra Narayan Cold Starage Pvt Ltd | West Bengal | KCX4 | 3384K2088 | 2325683536 | 2019-06-06 | 232568 | 2019-06-06 | oil carry over | 2018-11-03 | 2019-03-18 | 535 | null | null | 4 | Blank FSR | null | closed | Replaced Piston Ring Set & Cylinder Liner
2019-06-15 | S M Refrigeraion Pvt Ltd | null | D | Himalaya Food Co | New Delhi | KCX21 | 3424K081 | 2303103480 | 2019-05-14 | 230310 | 2019-05-24 | oil lifting | 2019-01-15 | 2019-02-07 | 1430 | null | null | 1 | Found high oil throw through piston no. 01&02 and piston rings worn out | null | closed | Replaced Piston Rings Set
2019-06-15 | S M Refrigeraion Pvt Ltd | null | D | Deviram Cold Storage Evam Ice Factory | Madhya Pradesh | KCX6 | 3394K899 | 2306443517 | 2019-05-27 | 230644 | 2019-05-21 | oil lifting | 2017-10-27 | 2018-02-19 | 2405 | null | null | 4 | Oil lifting problem due to ORV leakage | null | closed | Replaced ORV01 no.
2019-06-15 | S M Refrigeraion Pvt Ltd | null | D | Rura Cold Storage & Ice Factory | Uttar Pradesh | KCX4 | 3384K2068 | 2317783507 | 2019-05-22 | 231778 | 2019-06-01 | oil pressure not buildup | 2018-09-14 | 2019-02-23 | 514 | null | null | 5 | Found Broken Oil Pump Element | null | closed | Replaced Oil Pump Element
2019-06-15 | Fridge House | null | D | Shiva Milk Dairy Harugeri | Karnataka | KCX1 | 3354K118 | 2318123541 | 2019-06-08 | 231812 | 2019-06-08 | oil pressure problem | 2019-03-31 | 2019-05-10 | 215 | null | null | 2 | Oil Pressure is not developed & air Purging is observed. | null | closed | Replaced Oil Pump Assly
2019-06-15 | Hss Solution Pvt Ltd | null | D | Duratuff Yarns Private Limited | Rajastan | KCX2 | 3364K1658 | 2324263533 | 2019-06-04 | 232446 | 2019-06-04 | oil pressure trip | 2018-10-29 | 2019-04-20 | 171 | null | null | 6 | Air Purging when long time off compressor then start | null | closed | Replaced Oil Pump Assly
2019-06-15 | Trade Links | Secunderabad | D | Rdr Exports | Andhra Pradesh | KCX72 | 3474K253 | 2319003512 | 2019-05-25 | 231900 | 2019-05-28 | over heating | 2019-01-27 | 2019-03-30 | 813 | null | null | 2 | Abnormal Sound IN Cylinder No. 01 & 02, Found No. 01 Delivery valve Leakage, Liner Damage. | null | closed | Replaced Ring Suction Valve & Valve Spring Suction & Descharge Valve Assly & Gudgeon Pin & Needle Roller Bearing & Bearing Bush Big End Con Rod & Piston & Cylinder Liner & Piston Ring Set & Buffer Spring
2019-06-15 | Cool Comfort Private Limited | West Bengal | D | Aed Co Organics Pvt Ltd | West Bengal | KCX4 | 3384K2137 | 2322223539 | 2019-06-07 | 232222 | 2019-05-30 | shaft seal leakage | 2018-12-20 | 2019-03-16 | 915 | null | null | 3 | Blank FSR | null | closed | Shaft Seal Assly Replaced
2019-06-25 | Trade Links | null | D | Y R Ice Industries | Andhra Pradesh | KCX4 | 3384K2102 | 2321603524 | 2019-05-30 | 232160 | 2019-05-30 | k5 valve thread damaged | 2018-11-19 | 2019-05-30 | ZH | null | null | 6 | Threading damaged at site | null | closed | Replaced K5 valve
2019-06-25 | Kalp Marketing | Gujrat | D | VatvaAhmedabad | Gujrat | KCX4 | 3384K2103 | null | null | null | 2019-06-22 | low oil pressure problem | 2018-11-20 | 2019-06-19 | ZH | null | null | 8 | Paper filter fitted in suction oil stariner instead of discharge oil striner. Filter chocked. WITHIN 15 HRS | null | closed | null
2019-06-25 | Trade Links | null | D | Royal Food Goa | null | KCX3 | 3374K1936 | 2326883543 | 2019-06-10 | 232668 | 2019-06-09 | oil carry over | 2018-10-05 | 2019-01-02 | 3678 | null | null | 3 | ORV fail | null | closed | Replaced ORV
2019-06-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Anupam Colours Pvt Ltd | Vapi, Gujarat | KCX3 | 3374K1862 | 2323083562 | 2019-06-15 | 232308 | 2019-06-05 | oil carry over | 2019-06-18 | 2018-09-17 | 1499 | null | null | 8 | Piston crack, oil carryover 2 liters in 24 hrs | null | closed | Replaced piston piston ringsets
2019-06-25 | Multivista Global Pvt Ltd | null | D | Prakash Dairy | Tamil Nadu | PC2 | 331K2944 | 2299963305 | 2019-05-21 | 229996 | 2019-05-21 | spring missing from oil pressure regulatror | 2017-10-13 | 2019-05-21 | ZH | null | null | 19 | Spring missing from regulator | null | closed | Fitted OPR Spring and suction pressure gauge due to leakage
2019-06-25 | Trade Links | null | D | Jai Shanker Ice Plant | Eluru, Andhra Pradesh | KCX6 | 3394k1291 | null | null | null | 2019-06-22 | suction thermowell drill hole undersize | null | null | ZH | null | null | null | KRMS Suction temperature sensor fitment problem in thrmowell due to drill hole undersize. | null | closed | null
2019-06-26 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Food Export Pvt Ltd | null | KCX72 | 3474K205 | null | null | null | 2019-05-10 | abnormal noise | 2018-07-11 | 2018-09-14 | PC | null | null | 3 | HP Cylinder 4 - liner Liver spring was broken | null | closed | Replaced spring
2019-06-26 | S M Refrigeraion Pvt Ltd | null | D | Jpv Cold Store Pvt Ltd | null | KCX3 | 3374K2003 | null | null | null | 2019-05-16 | fitting leakage | 2019-01-02 | 2019-03-20 | PC | null | null | 2 | Fitting leakage from mearing cover Oring . Discharge oil pipe length oversize by 2mm | null | closed | Replaced pipe
2019-06-30 | Trade Links | Secunderabad | D | Nadhi Bio Products Pvt Ltd | Telangana | KCX93 | 3485K054 | 2319403555 | 2019-06-13 | 231940 | 2019-06-13 | delivery valve leakage | 2019-03-20 | 2019-06-13 | 50 | null | null | 3 | Storke limitor problem , Rings stucked. | null | closed | Replaced DV
2019-06-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | V S K Ice Maker | Gujrat | KCX3 | 3374K2100 | 2335243575 | 2019-06-22 | 233524 | 2019-06-22 | loading / unloading problem | 2019-05-04 | 2019-05-18 | 500 | null | null | 1 | Solenoid valve malfunctioning | null | closed | Replaced solenoid valve
2019-06-30 | Parag Marketing Services | Pune | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX93 | 3485K019 | 2333963566 | 2019-06-19 | 233396 | 2019-06-19 | oil carry over | 2018-03-19 | 2018-12-07 | 3298 | null | null | 9 | Oil throw found in cylinder no.2,3,5,6,10,11 , piston ring close gap 0.75mm also HP piston crack. | null | closed | Replaced Piston rings , Piston & Bearing bush.
2019-06-30 | Trade Links | Secunderabad | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1951 | 2303483585 | 2019-06-27 | 230348 | 2019-05-14 | oil carry over | 2018-04-16 | 2018-08-24 | 2484 | null | null | 4 | Modified ORV trial | null | closed | Modified ORV taken back for inspection
2019-06-30 | Trade Links | Secunderabad | D | Mohan Ice Fcatory | Andhra Pradesh | KCX3 | 3374K1707 | 2303003584 | 2019-06-27 | 230300 | 2019-05-13 | oil carry over | 2018-02-12 | 2018-05-25 | 7476 | null | null | 3 | Modified ORV trial | null | closed | Modified ORV taken back for inspection
2019-06-30 | Trade Links | Secunderabad | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1950 | 2326263548 | 2019-06-11 | 232626 | 2019-06-14 | shaft seal leakage | 2018-04-16 | 2018-08-25 | 2971 | null | null | 8 | Shaft seal leakage ???? & liner gasket down | null | closed | null
2019-06-30 | Trade Links | Secunderabad | D | Sri Sai Rama Industries | Telangana | KCX6 | 3394K1048 | 2304923495 | 2019-05-20 | 230492 | 2019-05-19 | shaft seal leakage | 2018-03-19 | 2018-08-29 | 3760 | null | null | 4 | Shaft seal leakage and wearing of cylinder | null | closed | Replaced cylinder assly & shaft seal asly
2019-07-01 | Multivista Global Pvt Ltd | Chennai | D | Sree Kannan Dairy Farm | Tamil Nadu | KCX4 | 3384K1924 | MailVRG | 2019-06-29 | null | 2019-06-29 | wrong wiring in control panel. | 2018-03-21 | 2019-07-01 | ZH | null | null | 16 | Wrong wiring : T2 : 7 No., S : 1 No Correct wiring : T2 : 1No., S : 7 No. | null | closed | Rectified at site
2019-07-01 | Trade Links | Secunderabad | D | Naga Hanuman Agro Oil Pvt Ltd | null | KCX2 | 3364K1703 | MailVRG | 2019-06-29 | null | 2019-06-29 | wrong wiring in control panel. | 2019-01-18 | 2019-07-29 | ZH | null | null | 6 | Direct supply was given to LP cut-out 8 No. wire. Actually its should be from HP cut-out 2 No. Terminal | null | closed | Rectified at site
2019-07-17 | Trade Links | Secunderabad | D | Devi Ice Factory | Andhra Pradesh | KCX6 | 3394K1293 | 2306823586 | 2019-06-27 | 230682 | 2019-05-24 | abnormal noise | 2019-03-10 | 2019-04-30 | 508 | null | null | 2 | Abnormal Sound And Over Heating | null | closed | Replaced Cylinder Liner, Piston, Piston Ring Set, bush Connecting Rod, Gudgeon Pin, Bearing Bush Big End Con Rod, Buffer Spring, Descharge valve assly, Connecting Rod With Bolt, Ring Suction Valve, Valve Spring Suction, Spring Curtain, Liner Assly
2019-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Phoenix Frozen Food | Gujrat | KCX93 | 3485K041 | 2333023564 | 2019-06-17 | 233302 | 2019-06-17 | cylinder overheating | 2018-09-11 | 2019-04-24 | 605 | null | null | 7 | Delivery valve passed cyl no 4 | null | closed | Replace Discharge valve assly
2019-07-17 | Kirloskar Pneumatic Co Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K011 | 2324543532 | 2019-06-04 | 2362454 | 2019-06-08 | discharge pressure to high | 2017-12-11 | 2018-08-03 | 3215 | null | null | 8 | Observe that compressor intermediate pressure to high, Found dish valve passed, Safety valve pass | null | closed | Replace Discharge valve assly , Teflon safety valve, set of gasket
2019-07-17 | Kalp Marketing | Gujrat | D | Aksharchem [India] Ltd | Gujrat | KCX9 | 3404K075 | 2324423556 | 2019-06-13 | 232442 | 2019-06-13 | high oil consumption | 2018-09-27 | null | 7999 | null | null | 7 | Piston Broken | null | closed | Replace Piston Ring Set, Piston ,Buffer Spring
2019-07-17 | Parag Marketing Services | Saswad | D | RSPL Limited | Madhya Pradesh | KCX3 | 3374K1653 | 2320463573 | 2019-06-20 | 232046 | 2019-06-20 | knocking / abnormal sound | 2018-01-08 | 2018-11-17 | 3500 | null | null | 10 | Kit Cylinder liner | null | closed | Replace Kit Cylinder liner
2019-07-17 | S M Refrigeraion Pvt Ltd | null | D | Hma Food Export Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1054 | 2335263576 | 2019-06-23 | 233536 | 2019-06-23 | knocking sound problem | 2018-03-21 | 2018-07-03 | 3968 | null | null | 4 | Knocking Sound | null | closed | Replace Cylinder liner, Piston, Piston Ring set, Safety Plate For Gudgion Pin
2019-07-17 | Trade Links | Secunderabad | D | Sanghi Polymers Pvt Ltd | Telangana | KCX2 | 3364K1707 | 2337603590 | 2019-06-28 | 233760 | 2019-07-03 | leakage problem | 2019-01-23 | 2019-04-23 | 84 | null | null | 3 | Shaft seal leakage, | null | closed | Replaced Shaft seal assly
2019-07-17 | S M Refrigeraion Pvt Ltd | null | D | Amara Breweries Pvt Ltd | Punjab | KCX4 | 3384K2064 | 2342903607 | 2019-07-09 | 234290 | 2019-07-09 | oil leakage | 2018-09-11 | 2019-04-21 | 199 | null | null | 7 | Found that discharge filter housing manifold threads which was damage | null | closed | Manifold oil filter housing KCX
2019-07-17 | Trade Links | Secunderabad | D | Surya Mitra Exim | Andhra Pradesh | KCX3 | 3374K2039 | 2337183587 | 2019-06-27 | 233718 | 2019-06-27 | oil lifting | 2019-02-15 | 2019-03-02 | 2024 | null | null | 1 | Blank FSR | null | closed | Replace Piston, Piston Ring Set, Cylinder Liner, spring Curtain, Liner Assly
2019-07-17 | Kalp Marketing | Gujrat | D | Ahemedabad Dist Co Oprative Milk Products | Gujrat | KCX2 | 3364K1650 | 2332503563 | 2019-06-17 | 233250 | 2019-06-17 | oil pressure not buildup | 2018-10-19 | 2019-01-02 | 976 | null | null | 3 | Pump Element Broken | null | closed | Pump Element Oil Pump KCX, Oil Return Valve, Gasket Set, ORing Set Flat End
2019-07-17 | Trade Links | Secunderabad | D | Sai Marine Export | null | KCX4 | 3384K1813 | 2320543534 | 2019-06-06 | 232054 | 2019-06-28 | over heating | 2018-01-21 | 2018-03-24 | 2075 | null | null | 3 | Dv back leakage roblem, Abnormal sound from cyl | null | closed | Replaced Piston, Cylinder Liner, Spring Curtain, Gudeon Pin, Bush Connecting Rod, Kit delivery Valve, buffer Spring, piston Ring Set
2019-07-17 | S M Refrigeraion Pvt Ltd | null | D | Sallarpur Cold Storage | Uttar Pradesh | KCX6 | 3394K1144 | 2342923608 | 2019-07-09 | 234292 | 2019-07-10 | shaft seal leakage | 2018-08-16 | 2019-02-09 | 799 | null | null | 6 | Found Oil Through Flywheel And Leakage Shaft Seal | null | closed | Shaft Seal Assly
2019-07-19 | Kalp Marketing | Gujrat | D | Zenith Exports | Gujrat | KCX51 | 3454K071 | 2326363554 | 2019-06-12 | 232636 | 2019-06-07 | abnormal noise | 2018-05-13 | 2018-08-10 | 750 | null | null | 3 | Spares worn out | null | closed | Replace Piston, Piston ring set, Gudgeon pin, Needle roller bearing
2019-07-19 | Cool Comfort Private Limited | West Bengal | D | Dhirendra Narayan Cold Starage Pvt Ltd | West Bengal | KCX4 | 3384K2088 | 2340062596 | 2019-07-03 | 234006 | 2019-07-18 | excessive oil lifting | 2018-11-03 | 2019-03-18 | 563 | null | null | 4 | Excessive oil lifting | null | closed | Replace Bearing bush flange, Bearing bush plain, Cylinder liner, Piston, Gudgeon pin, Bush connecting rod, Connecting rod with bol, Bearing bush big end con rod, Lock plate con rod, Gasket, Oring set flat end
2019-07-19 | Shree Engineering Services | Chhattisgarh | D | Ojaswi Cold Storage Pvt Ltd | null | KCX3 | 3374K1697 | 2344603627 | 2019-07-17 | 234460 | 2019-07-13 | leaking from the oil filter | 2018-02-07 | 2019-04-18 | 150 | null | null | 2 | Blank FSR | null | closed | Replace Solenoid Valve, Manifold Oil Filter Housing
2019-07-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Fine Organic Industries | Ambernath | KCX4 | 3384K2071 | 2342463612 | 2019-07-11 | 234246 | 2019-07-09 | oil prassure gauge faculty | 2018-09-14 | 2019-06-07 | 4 | null | null | 9 | Oil Pressure Gauge Found bulged and reading to br out | null | closed | Replace Pressure gauge ammonia
2019-07-19 | Kalp Marketing | Gujrat | D | Mother Dairy Fruits & Vegetables Pvt Ltd | Bihar | KCX4 | 3384K1975 | 2343303613 | 2019-07-11 | 234330 | 2019-07-12 | oil pressure not buildup | 2018-06-05 | 2019-01-02 | 1046 | null | null | 7 | Oil pump elements bearing damage and tiank broking. Liquid entry...ref mail YRP 16.07.19 | null | closed | Raplace pump element oil pump
2019-07-19 | S M Refrigeraion Pvt Ltd | null | D | Kurauli Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1149 | 2343583614 | 2019-07-11 | 234358 | 2019-07-12 | shaft seal leakage | 2018-08-18 | 2019-02-09 | 531 | null | null | 6 | Oil throw in flywheel side and Leakage shaft seal | null | closed | Replace Shaft Seal assly
2019-07-21 | Hss Solution Pvt Ltd | null | D | Gowardhan Villa | Udaipur,Rajastan | KCX6 | 3394K973 | 2287703443 | null | 228770 | 2019-04-17 | discharge stop valve leackage. | 2018-01-12 | 2019-04-17 | ZH | null | null | 13 | Fitting leakage from teflon | null | closed | TEFLON SEAT BOTTOM TAL 80/100 replaced.
2019-07-22 | Kirloskar South East Asia Co Ltd | Thailand | E | Suk See Ree | Thailand | KCX4 | 3384K2121 | Email | 2019-07-18 | null | 2019-07-18 | cylinder overheating | 2018-10-01 | null | null | null | null | null | one cylinder of KCX4 blown out and other cylinders overheating | null | open | null
2019-07-22 | S M Refrigeration | null | D | Goverdhan Shetalay Pvt Ltd | null | KCX6 | 3394K1241 | 2327003552 | 2019-06-11 | 232700 | 2019-06-11 | oil lifting | 2018-12-30 | 2019-03-22 | 840 | null | null | 3 | Piston ring sets replaced | null | closed | Piston ring sets
2019-07-22 | Cool Comfort Private Limited | West Bengal | D | Sahada Exports | null | KCX72 | 3474K252 | 234488 | 2019-07-15 | 234488 | 2019-07-16 | overheating of cylinders | 2019-01-23 | 2019-01-30 | 795 | null | null | 1 | Replaced HP piston assly | null | closed | HP piston assly
2019-07-24 | Fridge House | null | D | Gadre Marine Export Pvt Ltd | Karnataka | KCX63 | 3364K018 | 2337823624 | 2019-07-17 | 233782 | 2019-07-01 | cylinder overheating | 2018-06-22 | 2019-06-21 | ZH | null | null | 12 | Replaced cylinder liner,piston,piston ring sets, Brg bush conrod BE,Valve ring springs | null | closed | Replaced liner,piston, piston ring sets,valve ring springs
2019-07-24 | Fridge House | null | D | Mtc Cold Storage | Karnataka | KCX2 | 3364K1665 | 2238043625 | 2019-07-17 | 233804 | 2019-07-06 | high oil consumption | 2018-11-22 | 2019-02-22 | 1208 | null | null | 3 | Piston rings worn out and close gap increased | null | closed | piston ring sets and ORV
2019-07-24 | Fridge House | null | D | Jubilant Generics Ltd | Mysore | KCX6 | 3394K1141 | 2340563626 | 2019-07-17 | 234056 | 2019-07-05 | high oil consumption | 2018-08-13 | 2019-04-26 | 1102 | null | null | 8 | Piston rings worn out and close gap increased | null | closed | Piston ring set and liner
2019-07-24 | Kalp Marketing | Gujrat | D | Ambika Ice Factory | Gujrat | KCX2 | 3364K1403 | 2319483520 | 2019-05-28 | 231948 | 2019-05-27 | kcx oil pump low oil pressure | 2017-10-13 | 2018-01-01 | 4000 | null | null | 4 | oil pressure ok after replacement of oil pump | null | closed | Replaced oil pump
2019-07-24 | Multivista Global Pvt Ltd | null | D | Heritage Foods Ltd | Tamil Nadu | KCX2 | 3364K1587 | 2336083582 | 2019-06-26 | 233608 | 2019-06-25 | kcx oil pump tang broken | 2018-06-26 | 2019-04-26 | 474 | null | null | 10 | oil pump tang broken | null | closed | Replaced pump element
2019-07-24 | Multivista Global Pvt Ltd | null | D | Prakash Dairy | Tamil Nadu | PC2 | 331K2954 | 2238963604 | 2019-07-06 | 223896 | 2019-07-02 | shaft seal leakage | 2017-11-22 | 2019-05-09 | 29 | null | null | 18 | Scratch marks on sealing surface | null | closed | Replaced Shaft seal assly
2019-07-30 | Parag Marketing Services | null | D | Sawant Dairy Farm | Baramati | PC2 | 331K2953 | null | null | 235386 | 2019-07-23 | welding crack at discharge line | 2017-11-25 | 2018-05-21 | 2417 | null | null | 6 | Welding crack at discharge line | null | open | Compressor called back to KPCL for welding rectification.
2019-07-30 | Multivista Global Pvt Ltd | Chennai | D | Kader Investment & Trading CoPvt Ltd | Tamil Nadu | KCX31 | 3434K0103 | Mail Atul marwade | 2019-07-29 | null | 2019-07-29 | wrong serial number name plate punching. | 2019-05-31 | 2019-07-27 | ZH | null | null | 2 | Serial number punched on name plate 3434 K 103 Instaed of required 3434K0103. i.e. 0 missing. | null | open | null
2019-07-31 | Cool Comfort Private Limited | West Bengal | D | Contai Marine | Kalcutta | KCX51 | 3454K083 | Mail Amrish to GPV | 2019-07-31 | null | 2019-07-31 | crankcase heater fouling to stiffening plate. | 2018-07-15 | 2019-07-31 | ZH | null | null | 12 | Crankcase heater fouling to stiffening plate. | null | closed | null
2019-08-06 | Kalp Marketing | Gujrat | D | Nichem Industries | Gujrat | KCX6 | 3394K1006 | 2356463651 | 2019-08-02 | 235646 | 2019-08-02 | abnormal noise | 2018-02-11 | 2018-05-07 | 3200 | null | null | 3 | Piston crack | null | closed | Replace piston and piston ring set
2019-08-06 | Trade Links | null | D | Ind Union Foods Ltd | Andhra Pradesh | KCX6 | 3394K1117 | 2352843641 | 2019-07-25 | 235284 | 2019-07-25 | cylinder overheating | 2018-07-13 | 2019-06-14 | 498 | null | null | 11 | Delivery valve failure resulting into wearing of piston and liner | null | closed | piston,liner piston ring set
2019-08-06 | Parag Marketing Services | null | D | L V Dairy Patas | Duand ,Pune | KCX3 | 3374K1790 | 2344403616 | 2019-07-13 | 234440 | 2019-07-13 | kcx oil pump purging | 2018-03-31 | 2019-02-06 | 620 | null | null | 11 | oil pump replaced | null | closed | Replaced oil pump
2019-08-20 | Fridge House | null | D | Vijaya Sharan Cold Storage Pvt Ltd | Karnataka | KCX3 | 3374K1979 | 2354643659 | 2019-08-05 | 235464 | 2019-08-01 | high oil consumption | 2018-12-17 | 2019-02-12 | 4 | null | null | 2 | As per log book oil consumption found witin limit. No oil throw from cylinders. | null | closed | Replaced 2 buffer springs for length under size obs 109.
2019-08-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Forstar Frozen Foods Pvt Ltd | Mumbai | KCX6 | 3394K1089 | 2360563671 | 2019-08-09 | 236056 | 2019-08-09 | loading unloading problem | 2018-05-19 | 2018-10-15 | 1553 | null | null | 5 | Solenoid valve malfunctioning. Stuck in continous loading postion. | null | closed | Replaced solenoid valve
2019-08-20 | Parag Marketing Services | null | D | Agrani Foods & Agro Processing Pvt Ltd | Sangli | KCX3 | 3374K1967 | 2343363617 | 2019-07-14 | 234336 | 2019-07-14 | oil carry over | 2018-12-01 | 2019-05-27 | 190 | null | null | 5 | Oil consumption 2.5 Liter additional. Oil throw in cylinder no.3 due to close gap 1.2mm. | null | closed | Replaced piston ring set
2019-08-20 | S M Refrigeraion Pvt Ltd | null | D | Anand Dairy | Haryana | KCX3 | 3374K2032 | 2352463635 | 2019-07-23 | 235246 | 2019-07-23 | oil lifting | 2019-02-09 | 2019-05-05 | 903 | null | null | 3 | Piston rings wornout and close gap found 0.8mm. | null | closed | Replaced piston ring set
2019-08-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Shalom Marine Ice Plant | Kerala | KCX2 | 3364K1757 | 2353003637 | 2019-07-23 | 235300 | 2019-08-15 | op cutout malfunctioning | 2019-03-29 | 2019-08-15 | ZH | null | null | 5 | OP Cut out Coil getting heat but not trippling. | null | closed | Replaced OP Cut out
2019-08-20 | Trade Links | Secunderabad | D | Kumari Ice & Cold Storage | Andhra Pradesh | KCX6 | 3394K1013 | 2356203658 | 2019-08-05 | 235620 | 2019-08-02 | over heating | 2018-02-16 | 2018-05-14 | 9339 | null | null | 3 | Discharge valve leakage due to this other parts were damaged. Piston , liner seized. | null | closed | Replaced Liner , Piston , Piston ring set, Gudgeon pin , buffer spring & Discharge valve assly.
2019-08-20 | Parag Marketing Services | null | D | Rupal Chemicals | Khed, Maharashtra | KCX2 | 3364K1742 | 2352623670 | 2019-08-08 | 235262 | 2019-07-23 | shaft seal leakage | 2019-03-11 | 2019-06-18 | 1044 | null | null | 3 | Frequent shaft seal leakage problem . R22 Refrigerant gas application. | null | closed | Replaced Shaft seal
2019-08-20 | Trade Links | Secunderabad | D | The Krishna District Milk Producers Mutually Aided Co-Operative Union Ltd | Andhra Pradesh | KCX9 | 3404K079 | 2361883675 | 2019-08-10 | 236188 | 2019-08-10 | stop valve spindle damaged | 2017-11-24 | 2018-04-18 | 7337 | null | null | 6 | discharge stop valve passing problem , abnormal sound this is due to spindle & taflon damaged | null | closed | Replaced stop valve Tal 100
2019-08-31 | S M Refrigeration | null | D | Jamunar Ram Cold Storage | null | KCX4 | 3384K2147 | 2365183685 | 2019-08-19 | 236518 | 2019-08-19 | abnormal noise | 2018-12-30 | 2019-03-19 | 1518 | null | null | 3 | Blank FSR ... Approval remark - Delivery valve leakage , rings broken and hence damaged cylinder liner , piston & ring set. | null | closed | Replaced DV , Liner , Piston & Piston rings.
2019-08-31 | Kirloskar Pneumatic Co Ltd | Lucknow | D | Udya Cold Storage | Uttar Pradesh | KCX9 | 3404K086 | 2366763687 | 2019-08-21 | 236676 | 2019-08-21 | abnormal noise | 2018-01-16 | 2018-03-08 | 2716 | null | null | 3 | Blank fsr..As per FRR discharge valve leakage and damaged liner , piston , piston ring, gudgeon pin, bearings | null | closed | Replaced DV, liner , piston , piston ring, gudgeon pin, bearings
2019-08-31 | Trade Links | Secunderabad | D | Ind Union Foods Ltd | Andhra Pradesh | KCX6 | 3394K1117 | 2368423696 | 2019-08-24 | 236842 | 2019-08-24 | abnormal noise | 2018-07-13 | 2019-06-14 | 958 | null | null | 11 | Abnormal sound due to wearing of Liner, Piston , Piston rings , Bearings , Delivery valve etc. | null | closed | Replaced Liner, Piston , Piston rings , Bearings , Delivery valve , gudgeon pin, buffer spring.
2019-08-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sajjan India Limited | Gujrat | KCX93 | 3485K011 | 2324543532 | 2019-06-04 | 2362454 | 2019-06-08 | discharge pressure to high | 2017-12-11 | 2018-08-03 | 3215 | null | null | 8 | Observe that compressor intermediate pressure to high, Found dish valve passed, Safety valve pass | null | closed | Replace Discharge valve assly , Teflon safety valve, set of gasket
2019-08-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Lupin Limited | Ankleshwar Gujarat | KCX72 | 3474K287 | 2354283644 | 2019-07-26 | 235428 | 2019-07-26 | discharge valve leakage | 2019-05-22 | 2019-07-12 | 240 | null | null | 2 | Cylinder no.7 Delivery valve leakage | null | closed | Replaced delivery valve kit.
2019-08-31 | Kalp Marketing | Gujrat | D | Excel Cropcare Ltd | Bhuj Gujarat | KCX6 | 3394K1110 | 2343083650 | 2019-08-02 | 234308 | 2019-07-31 | gas leakage | 2018-07-29 | 2018-09-26 | 2022 | null | null | 3 | Gas leakage from manifold damaged threading & head cover fitment. | null | closed | Gas leakage from manifold damaged threading & head cover fitment.
2019-08-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Gumandev Chemicals Pvt Ltd | Gujrat | KCX1 | 3354K108 | 2350383638 | 2019-07-23 | 235038 | 2019-07-27 | knocking / abnormal sound | 2019-01-23 | 2019-07-27 | 2 | null | null | 6 | Compressor run by customer for 2 hrs without informed to Gargi. Knocking sound due to piston touches to delivery valve .Gudgeon pin , Con rod bush & half bearing bush damaged. | null | closed | Replaced Gudgeon pin , Con rod bush & half bearing bush
2019-08-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Akshar Cold Storage | Gujrat | KCX4 | 3384K2174 | 2336103579 | 2019-06-25 | 233610 | 2019-06-29 | loading & unloading problem | 2019-01-22 | 2019-03-14 | ZH | null | null | 2 | Within 24 hrs , Compressor direct solenoid valve is ok but other 2 NC valves automatically loading in 3sec... | null | closed | Replaced solenoid valve
2019-08-31 | Trade Links | Secunderabad | D | Vasista Marine | Andhra Pradesh | KCX93 | 3485K045 | 2364263679 | 2019-08-16 | 236426 | 2019-08-19 | oil lifting | 2018-11-20 | 2019-02-28 | 2714 | null | null | 3 | Oil throw from all 12 cylineders , due to wearing of rings also one liner & piston worn-out.. | null | closed | Replaced Piston ring set 12, Liner1 , Piston 1 & Bearings.
2019-08-31 | Trade Links | Secunderabad | D | Aditya Industries | Andhra Pradesh | KCX6 | 3394K1259 | 2368403695 | 2019-08-24 | 236840 | 2019-08-27 | oil lifting | 2019-01-21 | 2019-05-03 | 1762 | null | null | 5 | 5 Lit/day. Clinder no. 3 liner and cylinder no.6 Piston ring set wornout.. | null | closed | Replaced Cylinder liner , Piston rings set , Bearing bush & ORV.
2019-08-31 | Trade Links | Secunderabad | D | Illios Breweries Pvt Ltd | Andhra Pradesh | KCX9 | 3404K110 | 2366263686 | 2019-08-20 | 236626 | 2019-08-26 | over heating | 2018-08-28 | 2019-04-09 | 1339 | null | null | 8 | Cylinder no. 4 overheating due to delivery valve leakage, Liner piston rings damaged. | null | closed | Replaced DV & All cylinder assly except con rod.
2019-08-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Shivangi Ice Factory | Gujrat | KCX6 | 3394K1301 | 2352963640 | 2019-07-24 | 235296 | 2019-07-24 | overheating of compressor | 2019-03-28 | 2019-05-25 | 1033 | null | null | 2 | Safety valve passing & cylinder no.3 delivery valve leakage. | null | closed | Replaced Teflon rings safety valve ,Kit delivery valve & solenoid valve
2019-08-31 | Cool Comfort Private Limited | West Bengal | D | Contai Marine | West Bengal | KCX51 | 3454K105 | YRP Mail | 2019-08-02 | null | 2019-08-02 | panel guage board toggle got current | null | null | ZH | null | null | null | toggle switch glands (03 nos switches) in one panel got current . | null | closed | Toggle / Panel board
2019-08-31 | Parag Marketing Services | null | D | M/S Royal Food Stuffs Pvt Ltd | Satara | KCX42 | 3444K146 | YRP Mail | 2019-08-02 | null | 2019-08-02 | panel guage board toggle got current | 2019-03-09 | 2019-07-31 | ZH | null | null | 4 | OP gauge not working and also due to loos supply in TDV togal switch getting shock from panel board | null | closed | Toggle / Panel board
2019-08-31 | Multivista Global Pvt Ltd | Chennai | D | Kumaresh Cold Storage | Tamil Nadu | KCX2 | 3364K1808 | 2367823697 | 2019-08-24 | 236782 | 2019-08-24 | suction & discharge temp error in the controller krms panel. | 2019-06-27 | 2019-07-28 | 379 | null | null | 1 | Suction & Discharge Temp error in the controller - KRMS Panel. Sensor found ok. | null | closed | Replaced controller
2019-08-31 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Andhra Pradesh | KCX1 | 3354K130 | 2365103693 | 2019-08-23 | 236510 | 2019-08-23 | suction strainer missing | 2019-07-31 | 2019-08-23 | ZH | null | null | 1 | Suction strainer missing | null | closed | null
2019-08-31 | Fridge House | null | D | Mrf Industries | null | KCX6 | 3394K1147 | 2361823691 | 2019-08-23 | 236182 | 2019-08-13 | tdv solenoid valve malfunctioning | 2018-08-17 | 2019-08-13 | ZH | null | null | 1 | TDV Solenoid valve malfunctioning | null | closed | Replaced TDV
2019-08-31 | Multivista Global Pvt Ltd | Chennai | D | Cap Seafood Pvt Ltd Ernakulum | Kerala | KCX2 | 3364K1819 | Mail Marwade | 2019-08-30 | null | 2019-08-30 | wrong pressure name plate fitted | 2019-07-20 | 2019-08-30 | ZH | null | null | 1 | Suction pressure name plate fitted at both suction & discharge K5 Valve. | null | closed | null
2019-09-21 | Cool Comfort Private Limited | West Bengal | D | Jana Brothers Sea Food Llp | West Bengal | KCX72 | 3474K177 | 2373183737 | 2019-09-07 | 237318 | 2019-09-07 | abnormal noise | 2018-04-13 | 2018-08-02 | 2526 | null | null | 4 | Piston crack | null | closed | piston, piston ring set, gudgeon pin
2019-09-21 | Cool Comfort Private Limited | West Bengal | D | Friends Industries | West Bengal | KCX3 | 3374K1821 | 2374763743 | 2019-09-12 | 237476 | 2019-09-17 | abnormal noise | 2018-05-23 | 2019-06-27 | 1043 | null | null | 13 | cylinder lyner 1 & 2 wron out also damage piston and piston ring set | null | closed | Replace 2 liner and 3 set piston ring, clean wear filter
2019-09-21 | Kalp Marketing | Gujrat | D | Jay Chemical Industries Lyd | Ahmedabad | KCX3 | 3374K2006 | 2374643734 | 2019-09-07 | 237464 | 2019-09-07 | knocking / abnormal sound | 2019-01-16 | 2019-01-30 | 1850 | null | null | 1 | Piston broke from center | null | closed | Change Piston assembly
2019-09-21 | S M Refrigeraion Pvt Ltd | null | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2375623747 | 2019-09-13 | 237562 | 2019-09-11 | oil lifting | 2018-09-12 | 2019-02-02 | 289 | null | null | 5 | high consumption of oil, All ORV found faulty | null | closed | Change all ORV
2019-09-21 | Cool Comfort Private Limited | West Bengal | D | Annapurna Himghar Pvt Ltd | West Bengal | KCX4 | 3384K2109 | 2371863719 | 2019-09-02 | 237816 | 2019-09-06 | oil pressure not buildup | 2018-11-24 | 2019-03-11 | 1370 | null | null | 4 | Pump element tang broken. Gear wornout | null | closed | Replaced pump element
2019-09-21 | Geekay Pneumatic Pvt Ltd | null | D | R F Exports | Kerala | KC72 | 347K987 | 2370923736 | 2019-09-07 | 237092 | 2019-09-07 | oil pressure trip | 2019-01-20 | 2019-07-04 | 231 | null | null | 6 | Pump condition was ok but oil pressure not developed. | null | closed | Oil pump assembly replaced.
2019-09-21 | Trade Links | Secunderabad | D | Jai Shankar Icce Plant | Andhra Pradesh | KCX6 | 3394K1821 | 2374183735 | 2019-09-07 | 237418 | 2019-09-16 | op pressure switch malfunctioning | 2019-02-27 | 2019-06-26 | 746 | null | null | 4 | Air purging problem due to ball stuckup in OPR. | null | closed | Replaced OPR
2019-09-21 | S M Refrigeration | null | D | India Pesticide Ltd | Uttar Pradesh | KCX42 | 3444K139 | 2320323741 | 2019-09-10 | 232032 | 2019-07-04 | tal80/100 teflon missing | 2018-12-29 | 2019-07-04 | ZH | null | null | 6 | teflon seat bottom tal missing | null | closed | null
2019-09-22 | Geekay Pneumatic Pvt Ltd | null | D | Abm Marine Products | Kerala | KCX72 | 3474K284 | 2369763708 | 2019-08-28 | 236976 | 2019-08-28 | abnormal noise | 2019-03-30 | 2019-08-27 | ZH | null | null | 5 | Abnormal sound from compressor due to delivery valve leakage | null | closed | Replaced Piston, Gudgeon pin, Piston rings set , Discharge valve assly
2019-09-22 | Trade Links | Secunderabad | D | Amruth Agro Farms Pvt Ltd | Uttar Pradesh | KCX2 | 3364K1588 | 2335443588 | 2019-06-27 | 233544 | 2019-07-01 | abnormal noise | 2018-06-29 | 2019-02-25 | 1680 | null | null | 8 | Sound from cylinder, delivery valv and liner are ok. Sound shifted after interchanged DV. | null | closed | Change the dischsrge valve assembly
2019-09-22 | Trade Links | Secunderabad | D | 3F Industries Ltd | Andhra Pradesh | KCX63 | 3464K026 | 2371423716 | 2019-08-31 | 237142 | 2019-08-31 | abnormal noise and over heating | 2018-10-12 | 2019-08-28 | 26 | null | null | 10 | Found piston in seized condition due to delivery valve leakage. | null | closed | Change cylinder liner, piston, piston ring set, descharge valve assembly, buffer spring, spring curtain, linerassembly, gidgeon pin, bush connecting rod, ring suction valve spring suction kit delivery valve
2019-09-22 | Parag Marketing Services | Saswad | D | Soham Dye Chem Pvt Ltd | Krkumbh | KCX3 | 3374K1844 | 2363023676 | 2019-08-13 | 236302 | 2019-08-13 | air purging problem | 2018-06-22 | 2019-03-10 | 251 | null | null | 9 | Three times service visit done for air purging problem but issue not resolved hence replaced oil pump assly. | null | closed | Change pump assembly KCX
2019-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | New Faizan Foods | Gujrat | KCX51 | 3454K130 | 2367723699 | 2019-08-26 | 236772 | 2019-08-26 | delivery valve assembly leakage | 2019-08-14 | 2019-08-21 | ZH | null | null | 1 | Assembly completely leaking | null | closed | change descharge valve assembly
2019-09-22 | Kalp Marketing | Gujrat | D | New Faizan Foods | Gujrat | KCX51 | 3454K131 | 2367703698 | 2019-08-26 | 236770 | 2019-08-26 | delivery valve assembly leakage | 2019-08-14 | 2019-08-21 | ZH | null | null | 1 | Assembly completely leaking | null | closed | change descharge valve assembly
2019-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hejazi Foodstuff Pvt Ltd | null | KCX42 | 3444K154 | 2354223674 | 2019-08-09 | 235422 | 2019-08-17 | krms issue | 2019-05-06 | 2019-08-17 | ZH | null | null | 3 | Power supply adaptor & sensors malfuctioning | null | closed | Replace power supply adaptor, suction, transducer, descharge pressure transducer
2019-09-22 | Parag Marketing Services | Saswad | D | Beed Zilha Dudh Sangh | Barshi | KCX1 | 3354K051 | 2336803583 | 2019-06-27 | 233680 | 2019-06-27 | oil carry over | 2017-10-31 | 2018-04-21 | 4560 | null | null | 6 | Oil carryover 200ml oil in 10hrs from the separator | null | closed | Change Cylinder liner & piston ring set & ORV
2019-09-22 | Parag Marketing Services | Saswad | D | Beed Zilha Dudh Sangh | Barshi | KCX1 | 3354K049 | 2337263592 | 2019-06-29 | 233726 | 2019-06-29 | oil carry over | 2017-10-31 | 2018-04-21 | 2676 | null | null | 6 | Oil carryover 170ml oil in 9hrs | null | closed | Change Cylinder liner & piston ring set
2019-09-22 | Trade Links | Secunderabad | D | Surya Mitra Exim | Andhra Pradesh | KCX3 | 3374K2039 | 2357703664 | 2019-08-07 | 235770 | 2019-08-06 | oil lifting | 2019-02-15 | 2019-03-02 | 7868 | null | null | 1 | Liner and piston rings wornout | null | closed | Change cylinder liner, piston ring set spring curtain, liner assembly
2019-09-22 | S M Refrigeraion Pvt Ltd | null | D | Salik Ram Tiwari Cold Storage | Uttar Pradesh | KCX6 | 3394K1208 | 2367663692 | 2019-08-23 | 236766 | 2019-08-28 | oil lifting | 2019-02-10 | 2019-07-06 | 286 | null | null | 5 | 6 Liter oil consumption, Oil throw from cyl no.3 &6 also piston ring gap increased. | null | closed | Change piston ring set
2019-09-22 | S M Refrigeraion Pvt Ltd | null | D | Anand Dairy | Haryana | KCX3 | 3374K2032 | 2362043677 | 2019-08-13 | 236204 | 2019-08-13 | oil lifting problem & knocking sound | 2019-02-09 | 2019-05-05 | 1108 | null | null | 3 | Oil carry over problem | null | closed | Change piston ring set, cylinder liner & piston
2019-09-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K012 | 2359383661 | 2019-08-06 | 235938 | 2019-08-29 | over heating | 2017-12-11 | 2018-08-03 | 4012 | null | null | 8 | Overheating due to HP Cylinder 1 & 2 delivery valve leakage. | null | closed | Change piston, piston ring set, gudgeon pin, needle roller bearing, spacer for needle roller bearing, bearing bush big end con rod, descharge valve assembly, kit delivery valve, gasket head cover, gasket suct strainer & side cover
2019-09-22 | Trade Links | Secunderabad | D | Sri Rama Ice Factory | Andhra Pradesh | KCX3 | 3374K1748 | 2370583715 | 2019-08-30 | 237058 | 2019-08-30 | over heating & abnormal sound | 2018-03-05 | 2018-04-19 | 8067 | null | null | 1 | No. 1 piston over heating and abnormal sound due to delivery valve ring spring broken, liner & piston damaged. | null | closed | Change cylinder liner, piston, piston ring set, descgarge valve assembly, buffer spring, spring curtain, linerassembly, gidgeon pin, bush connecting rod, ring suction valve spring suction kit delivery valve
2019-09-22 | Parag Marketing Services | Saswad | D | Jeelani Marine Products | Ratnagiri | KCX72 | 3474K139 | 2369163701 | 2019-08-26 | 236916 | 2019-08-26 | overheating problem | 2018-01-21 | 2018-08-01 | 1285 | null | null | 7 | Due to the discharge valve leakage and high temp found piston damaged. | null | closed | Change piston & discharge valve
2019-09-22 | S M Refrigeraion Pvt Ltd | null | D | Mangalam Milk Chilling Center | Uttar Pradesh | KCX3 | 3374K2103 | 2371643717 | 2019-08-31 | 237164 | 2019-08-31 | pressure gauge defective | 2019-05-10 | 2019-08-31 | PC | null | null | 4 | Pressure gauge defective. | null | closed | Pressure gauge 16 kg/cm2
2019-09-22 | Parag Marketing Services | Saswad | D | Rupal Chemicals | Khed, Maharashtra | KCX2 | 3364K1742 | 2366143688 | 2019-08-21 | 236614 | 2019-08-21 | shaft seal leakage | 2019-03-11 | 2019-06-18 | 1317 | null | null | 3 | Found Shaft seal leakage | null | closed | change shaft seal leakage
2019-09-30 | Trade Links | Secunderabad | D | Synthochemlab Pvt Ltd | null | KCX2 | 3364K1768 | null | null | 238218 | 2019-09-24 | abnormal noise | 2019-04-24 | 2019-08-20 | 173 | null | null | 4 | Liner Gasket damage | null | closed | Gasket
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hejazi Foodstuff Pvt Ltd | null | KCX42 | 3444K154 | null | null | 237550 | 2019-09-10 | abnormal noise | 2019-05-06 | 2019-08-17 | 135 | null | null | 3 | Liner Gasket damage | null | closed | Piston, Liner & Gasket
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hari Orgochem | Savli, Vadodara | KCX72 | 3474K210 | 2379743784 | 2019-09-24 | 237974 | 2019-09-24 | abnormal noise piston crack | 2018-08-16 | 2019-05-06 | 2415 | null | null | 9 | Piston Broken Cyl No. 1,4 its HP Cyl | null | closed | Piston, Piston Ring Set, Bearing Bush Big End Con Rod
2019-09-30 | Trade Links | Secunderabad | D | Devi Ice Factory | Andhra Pradesh | KCX6 | 3394K1293 | null | null | 237792 | 2019-09-16 | air purging problem | 2019-03-10 | 2019-04-30 | 2065 | null | null | 1 | Air Purguing | null | closed | Replaced Orings & Gasket
2019-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Himalaya Ice & Cold Storage | Kerala | KCX3 | 3374K1839 | 2377463762 | 2019-09-17 | 237746 | 2019-09-15 | high oil carryoverpiston crack. | 2018-06-12 | 2018-09-14 | 5230 | null | null | 36 | Hair Line Crack on Piston & NRV damaged | null | closed | Piston, Piston Ring Set, Bolt Safety, Safety Plate For Gudgeon Pin, Lock Plate Con Rod & Inter HSG Bolt, ORV
2019-09-30 | Fridge House | null | D | Al Khajana Ice & Cold Storage | null | KCX4 | 3384K2253 | 2377243770 | 2019-09-19 | 237724 | 2019-09-14 | high oil consumption | 2019-04-30 | 2019-07-20 | 522 | null | null | 3 | Piston Seal Warn Out So While Checking In open Trial Oil Was Throwing Out In 4 Cylinder | null | closed | Piston Ring Set
2019-09-30 | Parag Marketing Services | null | D | Jeelani Marine Products | Ratnagiri | KCX72 | 3474K140 | null | null | 237442 | 2019-09-07 | knocking / abnormal sound | 2018-01-21 | 2018-06-07 | 1223 | null | null | 5 | Liner position shift & air purging of pump | null | closed | Liner part kit, O rings
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Transpek Industries Limited | Gujrat | KCX6 | 3394K1200 | 2383023789 | 2019-09-27 | 238302 | 2019-09-27 | loading and unloading | 2018-11-02 | 2018-11-19 | 18321 | null | null | 1 | Solenoid valve not working. | null | closed | Replaced Solenoid Valve 1 NO & 2NC
2019-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Torry Harris Seafoods Pvt Ltd | null | KCX3 | 3374K1857 | null | null | 237980 | 2019-09-21 | oil carry over | 2018-07-07 | 2018-10-17 | 1225 | null | null | 3 | Suction Line Insulation is not done also 2 nos ORV damaged | null | closed | Orings
2019-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Malabar Ice Factory | Kerala | KCX3 | 3374K1811 | 2379683775 | 2019-09-21 | 237968 | 2019-09-19 | oil carry over piston crack | 2018-05-09 | 2018-11-13 | 2928 | null | null | 6 | Piston Cracked And VLD O Ring Loose | null | closed | Piston, Safety Plate For Gadgeon Pin, Bolt Safety, Piston Ring Set, Lock Plate con Rod & Inter HSG Bolt
2019-09-30 | Fridge House | null | D | Mtc Cold Storage | Karnataka | KCX2 | 3364K1665 | 2375663771 | 2019-09-19 | 237566 | 2019-09-18 | oil pressure not buildup | 2018-11-12 | 2019-02-23 | 1495 | null | null | 3 | Dismantled the oil Pump checked found pump element assly worn out | null | closed | Pump Element Oil Pump
2019-09-30 | Kalp Marketing | Gujrat | D | Ushanti Colour Chem Pvt Ltd | null | KCX4 | 3384K1729 | 2322303529 | 2019-06-03 | 232230 | 2019-05-31 | oil pressure not buildup | 2017-11-24 | 2018-04-19 | 5242 | null | null | 5 | Oil Pump assly Warn Out, Also Pressure Regulater Not Working | null | closed | Pump Element Oil Pump KCX
2019-09-30 | Kalp Marketing | Gujrat | D | Radhanpur Chilling Center | Gujrat | KCX6 | 3394K1316 | 2383463786 | 2019-09-26 | 238346 | 2019-09-26 | oil seperator float valve issue | 2019-04-13 | 2019-08-28 | 50 | null | null | 4 | Float valve punctured. | null | closed | Float Valve Assly
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Phoenix Frozen Food | Gujrat | KCX72 | 3474K215 | 2369983705 | 2019-08-28 | 236998 | 2019-09-10 | over heating | 2018-09-11 | 2019-05-06 | 406 | null | null | 8 | Dely Valve Assly Passed Cly No. 4 | null | closed | Kit Delivery Valve, Buffer Spring, Ring Suction Valve
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K012 | 2375483740 | 2019-09-10 | 237548 | 2019-09-10 | over heating | 2017-12-11 | 2018-08-09 | 4959 | null | null | 8 | HP Cylinder 1 No. Head Dish Valve Passed | null | closed | Discharge Valve Assly
2019-09-30 | Kalp Marketing | Gujrat | D | Jay Chemical Industries Ltd | null | KCX6 | 3394K1195 | 2297123468 | 2019-05-04 | 229712 | 2019-05-03 | over heating compressor | 2018-10-26 | 2018-11-21 | 3223 | null | null | 1 | Open all 6 head cover, check all dilevery valve assembly found cylinder no. 3 d.v. Assly lecking condition and piston broken, also piston ring worn out and C.r Bering. | null | closed | Discharge Valve Assly, Piston, Suction Stroke Limiter, Gudgeon Pin, Bush Connecting Rod, Bearing Bush Big End Con Rod, Piston Ring Set, Descharge Valve Assly
2019-09-30 | Hss Solution Pvt Ltd | null | D | Durga Dairy Udyog | null | KCX3 | 3374K2145 | null | null | 237738 | 2019-09-14 | panel board bypass switch problem | 2019-07-24 | 2019-08-30 | PC | null | null | 1 | Bypass switch Replacement | null | closed | Bypass switch Replacement
2019-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Apex Pharmachem Pvt Ltd | Gujrat | KCX4 | 3384K2077 | 2347283689 | 2019-08-22 | 234728 | 2019-07-19 | seal leakage & over heating of head | 2018-09-16 | 2019-03-02 | 2119 | null | null | 6 | Delivery valve ring & spring broken in one cylinder | null | closed | Cylinder Liner, Descharge Valve Assly
2019-10-20 | Kalp Marketing | Gujrat | D | New Faizan Foods | Gujrat | KCX51 | 3454K131 | 2382523796 | 2019-09-30 | 238252 | 2019-09-30 | abnormal noise | 2019-08-14 | 2019-08-21 | 200 | null | null | 1 | Discharge valve leaked | null | closed | Kit Delivery valve
2019-10-20 | S M Refrigeraion Pvt Ltd | null | D | Shell Mount Fresh | Haryana | KCX42 | 3444K123 | 2377523757 | 2019-09-16 | 237752 | 2019-09-28 | abnormal noise | 2018-09-18 | 2019-02-26 | 2060 | null | null | 5 | Replace All Require Spares Parts Under Warranty Cyliner liner 01 no, piston ring set 01 no, gudgeon pin 01 no. Needal roaler bearing 02 nos suction valve spring 02 nos, buffer spring 01 no discharge valve assly 01no | null | closed | Change Cylinder Liner, Piston, Piston Ring Set, Gudgeon Pin, Descharge Valve assly, Needle Rollar Bearing, Buffer Spring, Valve Spring Suction
2019-10-20 | Cool Comfort Private Limited | West Bengal | D | Mother Dairy Fruits & Vegetables Pvt Ltd | Bihar | KCX4 | 3384K1974 | 2377542019 | 2019-09-15 | 237754 | 2019-09-15 | abnormal noisepiston crack | 2018-06-05 | 2019-01-02 | 1271 | null | null | 7 | Piston Cracked & Piston Ring Damaged | null | closed | Change Piston , Piston Ring Set
2019-10-20 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX63 | 3464K016 | 2323343535 | 2019-06-06 | 232334 | 2019-06-06 | compressor over heating | 2018-05-30 | 2019-03-20 | 175 | null | null | 10 | Piston & Liner Damage | null | closed | null
2019-10-20 | Kalp Marketing | Gujrat | D | Arabian Foods | Gujrat | KCX72 | 3474K273 | 2378043760 | 2019-09-16 | 237804 | 2019-09-16 | delivery valve assembly leakage | 2019-03-29 | 2019-08-28 | 35 | null | null | 5 | Discharge Valve Leaked | null | closed | Change Lit Delivery Valve
2019-10-20 | Kalp Marketing | Gujrat | D | Arabian Foods | Gujrat | KCX51 | 3454K123 | 2378063761 | 2019-09-16 | 237806 | 2019-09-16 | delivery vavlve assly leakage | 2019-06-22 | 2019-08-27 | 2 | null | null | 2 | Discharge Valve Leakage | null | closed | Change Kit Delivery Valve
2019-10-20 | Kalp Marketing | Gujrat | D | New Faizan Foods | Gujrat | KCX51 | 3454K131 | 237758375 | 2019-09-16 | 237758 | 2019-09-16 | high discharge pressure | 2019-08-14 | 2019-08-21 | 35 | null | null | 1 | Discharge Temperature High | null | closed | Change Valve Ring Discharge
2019-10-20 | Cool Comfort Private Limited | West Bengal | D | Maa Nalini Cold Storage | West Bengal | KCX6 | 3394K1253 | 2380583799 | 2019-10-03 | 238058 | 2019-10-03 | high oil carry over | 2019-01-11 | 2019-03-08 | 1560 | null | null | 3 | Oil carry over too high(700 ml hr) due to piston, piston ring & cylinder liner. No 1 orv leakage | null | closed | Piston Ring set, Piston, Cykinder Liner,Gudgeon Pin, Bush Con Rod
2019-10-20 | S M Refrigeraion Pvt Ltd | null | D | Ambey Cold Storage | Uttar Pradesh | KC4 | 338K5680 | 2381723779 | 2019-09-23 | 238172 | 2019-09-30 | knocking / abnormal sound | 2018-11-28 | 2019-02-26 | 2186 | null | null | 3 | Found Extra Sound From Cylinder No 1 & 3 No | null | closed | Change Cylinder liner, Piston, Piston Ring Set
2019-10-20 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX4 | 3384K1927 | 2372503733 | 2019-09-07 | 237250 | 2019-09-07 | knocking sound piston crack | 2018-03-24 | 2018-12-14 | 3959 | null | null | 9 | Piston Boken & delivery valve leakage | null | closed | Change Piston, Piston Ring Set, Cylinder Liner, Descharge ValveAssly, Gudgeon Pin, Bush Connecting Rod, lock Plate Con Rod, & Inter HSG Bolt, Gasket Liner, Side cover, Gasket Head Cover
2019-10-20 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2382143783 | 2019-09-24 | 238214 | 2019-09-24 | oil carry over | 2018-09-12 | 2019-02-08 | 349 | null | null | 5 | High Oil Consumption | null | closed | Change Piston ring Set
2019-10-20 | S M Refrigeraion Pvt Ltd | null | D | Salik Ram Tiwari Cold Storage | Uttar Pradesh | KCX6 | 3394K1208 | 2379783781 | 2019-09-23 | 237978 | 2019-10-05 | oil carry over | 2019-02-10 | 2019-07-06 | 714 | null | null | 5 | Found 96 hrs oil carryover 7 ltrs | null | closed | Change Cylinder Liner, Piston, Piston ring set
2019-10-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Melog Speciality Chemicals Pvt Ltd | Mumbai | KCX4 | 3384K2090 | 2388423814 | 2019-10-12 | 238842 | 2019-10-10 | oil carry over piston crack | 2010-09-19 | 2018-11-23 | 6817 | null | null | 2 | Piston no 2 & 4 center broken & Piston Ring Worn Out. | null | closed | Piston, Piston Ring Set, Gasket Set
2019-10-20 | Trade Links | null | D | Al Akbeer Exports Pvt Ltd | null | KCX9 | 3404K103 | 2377323759 | 2019-09-16 | 237732 | 2019-09-24 | oil lifting | 2018-08-27 | 2018-11-22 | 6053 | null | null | 4 | Delivery Valve Back Leaking | null | closed | Piston, Piston Rimg Set, Bush connecting rod, Gudgeon Pin, Descharge Valve Assly, Kit Delivery Avlve, Ring Suction Valve, Valve spring suction
2019-10-20 | Trade Links | null | D | Kali Ice Factory | Andhra Pradesh | KCX3 | 3374K1861 | 2378483772 | 2019-09-19 | 237848 | 2019-09-19 | oil lifting | 2018-07-11 | 2018-09-05 | 5450 | null | null | 2 | DV back Leakage Problem & Piston Cracked ORV back Leakage Problem | null | closed | ChangePiston, Piston Ring Se4t, Delivery Stroke Limiter, ORV, Kit Delivery Valve
2019-10-20 | S M Refrigeraion Pvt Ltd | null | D | Best Crop Science Llp | Uttar Pradesh | KCX6 | 3394K1277 | 2383183791 | 2019-09-28 | 238318 | 2019-10-07 | oil pressure not buildup | 2019-02-06 | 2019-05-11 | 499 | null | null | 3 | Oil Pump Element Broken | null | closed | Pump element replaced
2019-10-20 | Kalp Marketing | Gujrat | D | Rahemat Fish Center | Gujrat | KCX72 | 3474K163 | 2378623764 | 2019-09-17 | 237862 | 2019-09-17 | oil pressure not develop & knocking sound | 2018-02-18 | 2018-08-30 | 3673 | null | null | 6 | All main bearing worn out | null | closed | Bearing Bush Big End Con Rod, Bearing Inter half, oil pump assly, bearing bush plain, flywheel endBearing Bush Flange, Thrust Ring Pump End Bearing cover, Set Of gasket, Set Of O rings.
2019-10-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Gyaneshwari Enterprises | Ahmed Nagar | KCX2 | 3364K1672 | 2370423738 | 2019-09-09 | 237042 | 2019-09-06 | oil pressure problem | 2018-11-30 | 2019-05-07 | 1633 | null | null | 6 | HP oil pressure regulator of cerclip broken then oil pump of gear broken | null | closed | Pump element Oil Pump
2019-10-20 | Kalp Marketing | Gujrat | D | Shree Shiv Shakti Ice & Cold Storage | Gujrat | KCX4 | 3384K2262 | 2354503653 | 2019-08-02 | 235450 | 2019-08-02 | op pressure switch malfunctioning | 2019-05-28 | 2019-08-02 | ZH | null | null | 3 | Replaced OP Pressure switch | null | closed | Replaced OP Pressure switch
2019-10-20 | Trade Links | null | D | Aurbindo Pharma Pvt Ltd | Andhra Pradesh | KC63 | 346K271 | 2378243773 | 2019-09-19 | 237824 | 2019-09-20 | over heating | 2017-11-29 | 2018-08-10 | 980 | null | null | 9 | Delivery Valve Back Leaking | null | closed | Change Cylinder Liner, Piston ,Piston Ring Set, Ring suction Valve, Valve Spring Suction, Needle Roller Bearing, Gudgeon Pin & DV
2019-10-26 | Cool Comfort Private Limited | West Bengal | D | SSSea Foods (P) Ltd | West Bengal | KCX51 | 3454K115 | 2390583823 | 2019-10-16 | 239058 | 2019-10-25 | abnormal noise | 2019-03-17 | 2019-08-24 | 93 | null | null | 5 | Delivery valve leakage & Buffer spring sort. Valve leakage due to system dirt entred | null | closed | Replaced Piston , liner , piston ring set , buffer spring , delivery valve.
2019-10-26 | Cool Comfort Private Limited | West Bengal | D | B-One Buisness House Pvt Ltd | Bhubaneswar Orissa | KCX42 | 3444K085 | 2392983855 | 2019-10-22 | 239298 | 2019-10-23 | abnormal noise from cylinder | 2018-01-24 | 2018-05-20 | 2521 | null | null | 4 | HP Cylinder no.1 found buffer spring short by 6mm. | null | closed | Replaced buffer spring
2019-10-26 | Geekay Pneumatic Pvt Ltd | Kerala | D | Frontline Exports Pvt Ltd | Kerala | KCX72 | 3474K224 | 2390923832 | 2019-10-19 | 239092 | 2019-10-19 | abnormal noise from hp | 2018-09-22 | 2019-01-09 | 2943 | null | null | 4 | Dismentled cylinder found liner , piston has been worn out , bufferspring shrinked & delivery valve ring spring broken. | null | closed | Replaced buffer spring , liner , piston , piston rings, deliery valve assly & needle roller bearing.
2019-10-26 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX51 | 3454K064 | null | null | 238594 | 2019-10-04 | cylinder overheating | 2018-03-03 | 2019-01-25 | 915 | null | null | 9 | Liner gasket damaged. | null | closed | Replaced liner gasket
2019-10-26 | Geekay Pneumatic Pvt Ltd | Kerala | D | Mampilly Ice Factory | Kerala | KCX2 | 3364K1764 | 2385663800 | 2019-10-03 | 238566 | 2019-10-03 | female run tee thread damaged. | 2019-04-21 | 2019-10-03 | 2 | null | null | 6 | High discharge pressure & Run tee thread damaged while excess tightning. | null | closed | Replaced female run tee
2019-10-26 | Fridge House | null | D | Jubilant Generics Ltd | Mysore | KCX6 | 3394K1141 | 2384963816 | 2019-10-14 | 238496 | 2019-10-04 | high oil consumption | 2018-08-13 | 2019-04-26 | 14166 | null | null | 8 | No oil consumption complaint , Pump drive shaft tang broken due to liquid entry. | null | closed | Replaced pump element & piston ring set.
2019-10-26 | Kalp Marketing | Gujrat | D | Sun Marine Exports | Gujrat | KCX4 | 3384K1961 | 2378603763 | 2019-09-17 | 237860 | 2019-09-17 | knocking / abnormal sound | 2018-05-04 | 2018-08-21 | 2408 | null | null | 4 | Cylinder seized frequently due to high suction super heat & discharge temp. | null | closed | Replaced LINER , PISTON , GUDGEON PIN , PISTON RING SET , CON ROD BUS, SUCTION RING & SPRINGS.
2019-10-26 | S M Refrigeraion Pvt Ltd | Haryana | D | Anand Dairy | Haryana | KCX3 | 3374K2032 | 2390223821 | 2019-10-15 | 239022 | 2019-10-15 | oil carry over | 2019-02-09 | 2019-05-05 | 1813 | null | null | 3 | 1.5 lit oil consumption within 12 hrs. Observed oil separator float valve in damaged condition. | null | closed | Replaced float Valve Assly1no
2019-10-26 | Multivista Global Pvt Ltd | Chennai | D | Antony Micheal Ice Plant | Tamil Nadu | KCX4 | 3384K1941 | 2388023806 | 2019-10-09 | 238802 | 2019-10-09 | oil carry over | 2018-03-31 | 2018-11-03 | 4674 | null | null | 7 | Cylinder no.4 oil throw , Replaced piston ring set & ORV. | null | closed | Replaced piston ring set & ORV.
2019-10-26 | Parag Marketing Services | null | D | Mehta Dairies | Kolhapur | KCX3 | 3374K1832 | 2387943807 | 2019-10-10 | 238794 | 2019-10-10 | oil carry over | 2018-06-08 | 2018-09-07 | 7877 | null | null | 4 | Excess oil consumption was 540ml. Piston rings wornout & close gap observed 0.85mm | null | closed | Replaced Piston ring set1 no.
2019-10-26 | Parag Marketing Services | null | D | Burondekar Ice Factory | Ratnagiri | KCX3 | 3374K1829 | 2380503778 | 2019-09-22 | 238050 | 2019-09-22 | oil pressure not buildup | 2018-06-02 | 2018-10-04 | 4167 | null | null | 5 | Pump element broken. | null | closed | Replaced pump element
2019-10-26 | Parag Marketing Services | null | D | Sangamner Taluka Sahakari Dudh Utpadan Prakriya Sngh Ltd | Ahmed Nagar | KCX6 | 3394K1288 | 2389443831 | 2019-10-19 | 238944 | 2019-10-18 | over heating | 2019-02-20 | 2019-03-14 | 4213 | null | null | 2 | Compressor overheating due to delivery valve ring spring kit was broken resulting in to cylinder liner , piston , piston rings , gudgeon pin & con rod bush wornout for cyl no.4 | null | closed | Replaced Piston , Liner , piston rings, gudgeon pin , con rod bush and delivery valve kit.
2019-10-26 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Jain Cold Storage | Uttar Pradesh | KC3 | 337K4768 | null | null | 239220 | 2019-10-20 | shaft seal leakage | 2019-01-29 | 2019-03-12 | 877 | null | null | 2 | Shaft seal Oring damaged | null | closed | Replaced Oring
2019-10-26 | Parag Marketing Services | null | D | Bhoomi Agro Bio Foods | Pune | KCX51 | 3454K136 | null | null | 239410 | 2019-10-26 | toggal switch getting shock/current. | 2019-09-25 | 2019-10-26 | ZH | null | null | 1 | During commissioning he has found due to loos supply in TDV toggal switch getting shock from panel board. | null | closed | Replaced toggle switch 2 nos
2019-11-17 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun BeveragesPathankotPunjab | null | KCX9 | 3404K107 | 2395303852 | 2019-11-04 | 239530 | 2019-11-04 | abnormal noise | 2018-09-12 | 2019-02-08 | 628 | null | null | 6 | Liner tap bolt broken | null | closed | Replaced tap bolt 2 nos
2019-11-17 | Trade Links | null | D | Jay Ma Kali Ice Plant | Andhra Pradesh | KCX6 | 3394K1164 | 2394083845 | 2019-10-25 | 239408 | 2019-10-25 | abnormal noise | 2018-09-05 | 2018-10-29 | 7193 | null | null | 1 | Cylinder no.6 delivery valve leakage seat damaged & buffer spring shrink. | null | closed | Replaced DV & Buffer spring
2019-11-17 | Cool Comfort Private Limited | West Bengal | D | B-One Buisness House Pvt Ltd | Bhubaneswar Orissa | KCX42 | 3444K084 | 2392963834 | 2019-10-22 | 239296 | 2019-10-23 | abnormal noise | 2018-01-24 | 2018-05-20 | 3705 | null | null | 5 | Cyl no. 1 HP Buffer spring shrink by 5 mm. | null | closed | Replaaced buffer spring.
2019-11-17 | Trade Links | null | D | Sri Sai Ram Industries | Andhra Pradesh | KCX6 | 3394K1047 | 2381543788 | 2019-09-27 | 238154 | 2019-10-02 | abnormal noise | 2018-03-19 | 2018-08-28 | 6705 | null | null | 5 | Piston had broken in two pieces from gudgeon pin hub due to this connecting rod broken and other parts were damaged. | null | closed | Replaced Liner 2, Piston 5, Piston ring set 6,Connecting rod 1, Gudgeon pin2.
2019-11-17 | Parag Marketing Services | null | D | Jilani Marine Products | Ratnagiri | KCX72 | 3474K150 | 2393583841 | 2019-10-24 | 239358 | 2019-10-24 | kcx pump air purging | 2018-01-27 | 2018-08-01 | 2473 | null | null | 7 | Air purging problem | null | closed | Replaced pump assly
2019-11-17 | Model Pneumatic Co | Punjab | D | Go Fresh | J&K | KCX4 | 3384K1970 | 2384083815 | 2019-10-14 | 238408 | 2019-10-14 | oil carry over | 2018-05-26 | 2018-09-15 | 2407 | null | null | 4 | Cylinder liner 4 nos , Piston 3 nos & Piston rings 4 nos damaged. | null | closed | Replaced Piston , Piston ring sets & Liner 4 nos.
2019-11-17 | Parag Marketing Services | null | D | Beed Zila Dudh Sangh | Beed | KCX1 | 3354K049 | 2391403828 | 2019-10-18 | 239140 | 2019-10-19 | oil carry over | 2017-10-31 | 2018-04-21 | 2980 | null | null | 6 | Safety valve leakage & Breather assly slightly loose. Replaced & found ok | null | closed | Replaced SV Teflon & Breather assly
2019-11-17 | Kalp Marketing | Gujrat | D | Zenith Exports | Gujrat | KCX51 | 3454K071 | 2393283836 | 2019-10-23 | 239328 | 2019-10-23 | over heating | 2018-05-13 | 2019-08-10 | 1040 | null | null | 5 | Delivery valve leakage due to valve seat damaged. | null | closed | Replaced discharge valve assly.
2019-11-17 | Model Pneumatic Co | Punjab | D | Makheja Cold Storage | Punjab | KCX4 | 3384K1886 | 2378743843 | 2019-10-25 | 237874 | 2019-09-18 | over heating | 2018-02-28 | 2018-03-24 | 2339 | null | null | 1 | Discharge valve ring spring broken , Piston & piston rings worn out. | null | closed | Replaced DV , Piston & Piston ring set.
2019-11-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Arnala Machimar Vividh Karyakari Sanstha | Thane | KCX3 | 3374K2153 | 2393723844 | 2019-10-25 | 239372 | 2019-10-25 | piston crack | 2019-08-13 | 2019-08-21 | 700 | null | null | 1 | Piston hair crack on top side and temp issue. | null | closed | Replaced Piston & Piston ring set 2 nos.
2019-11-17 | S M Refrigeration | null | D | Pawan Enterprises | Uttar Pradesh | KC2 | 336K3397 | 2387523803 | 2019-10-08 | 238752 | 2019-10-07 | shaft seal leakage | 2017-12-29 | 2019-10-04 | 15 | null | null | 22 | Shaft seal leakage & Brg bush line marks | null | closed | Replaced shaft seal & bearing bush.
2019-11-17 | Kalp Marketing | Gujrat | D | Himalaya Cold Storage | Gujrat | KCX3 | 3374K1549 | 2390823822 | 2019-10-16 | 239082 | 2019-10-16 | shaft seal leakage | 2017-10-30 | 2019-03-28 | 293 | null | null | 17 | Shaft seal leakage , lapping done and replaced Oring kit . | null | closed | Replaced Oring kit
2019-11-29 | Cool Comfort Private Limited | West Bengal | D | Friends Industries | West Bengal | KCX3 | 3374K1821 | 2402223882 | 2019-11-18 | 240222 | 2019-11-18 | abnormal noise | 2018-05-23 | 2019-06-27 | 1043 | null | null | 13 | its repetitive issue of cylinder damage i.e. Liner wornout. | null | closed | Replaced Liner , Piston , Piston ring set , Gudgeon pin & bearings 3 sets.
2019-11-29 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K011 | 2396623865 | 2019-11-08 | 239662 | 2019-11-09 | cylinder overheating | 2017-12-11 | 2018-08-03 | 5920 | null | null | 8 | Cyl no.3 overheat due to DV leakage , ring spring broken also Safety valve leakage from teflon. | null | closed | Replaced kit delivery valve , safety valve spring & teflon.
2019-11-29 | Gargi Engineering Enterprices Pvt Ltd | null | D | Lupin Limited | Ankleshwar Gujarat | KCX72 | 3474K287 | 2398283868 | 2019-11-11 | 239828 | 2019-11-16 | cylinder overheating | 2019-05-22 | 2019-07-12 | 2000 | null | null | 2 | Cylinder no. 3,7 & 8 overheating due to delivery valve leakage and hence piston rings wornout | null | closed | Replaced discharge valve assly & Piston ring set 03 nos.
2019-11-29 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX72 | 3474K230 | 2388243809 | 2019-10-11 | 238824 | 2019-10-11 | delivery valve leakage | 2018-11-30 | 2019-05-03 | 159 | null | null | 6 | Foregin particals/ dirt in compressor and suction strainer. Discharge valve leakage. | null | closed | Replaced DV Kit.
2019-11-29 | Kalp Marketing | Gujrat | D | Jay Ice Factory | Gujrat | KCX4 | 3384K1966 | 2391903830 | 2019-10-18 | 239190 | 2019-10-18 | high oil consumption | 2018-05-18 | 2018-06-08 | 10800 | null | null | 1 | Piston rings gap oversized . Observed 0.7mm. | null | closed | Replaced all 4 set of piston ring sets.
2019-11-29 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX4 | 3384K1927 | 2391823829 | 2019-10-18 | 239182 | 2019-10-18 | knocking / abnormal sound | 2018-12-14 | 2018-03-24 | 4817 | null | null | 3 | Discharge valve ring spring broken | null | closed | Replaced delivery valve ring spring kit .
2019-11-29 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX63 | 3464K029 | 2401243877 | 2019-11-15 | 240124 | 2019-11-15 | loading and unloading problem | 2018-10-27 | 2019-11-07 | ZH | null | null | 13 | After 18 hrs , Solenoid valve not working | null | closed | Replaced solenoid valve
2019-11-29 | Trade Links | null | D | Ashirwad Carbonics India Ltd | Andhra Pradesh | KCX93 | 3485K061 | 2393603878 | 2019-11-16 | 239360 | 2019-11-16 | oil pump element tang broken | 2019-07-09 | 2019-11-16 | 15 | null | null | 4 | Oil pump element tang broken. | null | closed | Replaced pump element
2019-11-29 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX63 | 3464K029 | 2392803862 | 2019-11-07 | 239280 | 2019-11-07 | retainer plate bolt broken | 2018-10-27 | 2019-11-07 | ZH | null | null | 12 | Retainer plate assembly ruty & centre bolt broken. | null | closed | Replaced retainer plate assly
2019-11-29 | Kalp Marketing | Gujrat | D | Gold Fish Ice Factory | Daman & Diu | KCX6 | 3394K1333 | 2370643768 | 2019-09-18 | 237064 | 2019-09-18 | shaft seal cover leakage | 2019-05-31 | 2019-07-31 | 354 | null | null | 2 | Leakage from shaft seal cover. | null | closed | Replaced shaft seal cover.
2019-11-29 | Kalp Marketing | Gujrat | D | Kan Victual Pvt Ltd | Gujrat | KCX6 | 3394K1055 | 2388843813 | 2019-10-12 | 238884 | 2019-10-12 | solenoid valve not working | 2018-03-21 | 2019-10-12 | ZH | null | null | 19 | Solenoid valve not working mechanically | null | closed | Replaced solenoid valve 1 no. NC
2019-11-30 | Cool Comfort Private Limited | West Bengal | D | Babulal Bag Ice Plant | West Bengal | KCX2 | 3364K1736 | null | null | 239876 | 2019-11-11 | control pannel box wrong oil pressure connection | 2019-02-23 | 2019-08-06 | 508 | null | null | 6 | Troggal switch, indicator lamp & wireing burning. | null | closed | Replaced Troggal switch, indicator lamp & wireing
2019-12-21 | Trade Links | Secunderabad | D | Sri Venkateswara Ice & Cold Storage | Andhra Pradesh | KCX6 | 3394K1115 | 2394683851 | 2019-11-04 | 239468 | 2019-11-04 | abnormal noise | 2018-07-06 | 2018-12-04 | 6021 | null | null | 5 | Cyl no.3 abnormal sound. DV & liner damaged. -- Cylinder seized | null | closed | Replaced cylinder assembly.
2019-12-21 | Multivista Global Pvt Ltd | null | D | Hatsun Agro Products Ltd | Tamil Nadu | KCX3 | 3374K2156 | 2397303864 | 2019-11-07 | 239730 | 2019-11-07 | abnormal noise | 2019-08-27 | 2019-11-02 | ZH | null | null | 1 | Within 3 hours found all connecting rod bearings wornout, thrust ring and pump end bearing wornout. | null | closed | Replaced all bearings & Thrust ring.
2019-12-21 | Cool Comfort Private Limited | West Bengal | D | Friends Industries | West Bengal | KCX3 | 3374K1821 | 2410083928 | 2019-12-09 | 241008 | 2019-12-09 | abnormal noise | 2018-05-23 | 2019-06-27 | 1043 | null | null | 13 | Loose fitment of bearing bush in bearing cover. | null | closed | Replaced pump bearing cover
2019-12-21 | Model Pneumatic Co | Punjab | D | Highland Industries | J&K | KCX2 | 3364K1822 | 2406563908 | 2019-11-30 | 240656 | 2019-11-30 | bearing cover bh | 2019-08-03 | 2019-11-30 | ZH | null | null | 4 | Bearing cover leakage due to porous/ blow hole | null | closed | Replaced pump end bearing cover
2019-12-21 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX72 | 3474K230 | 2388243809 | 2019-10-11 | 238824 | 2019-10-11 | delivery valve leakage | 2018-11-30 | 2019-05-03 | 159 | null | null | 7 | DV leakage due to carbon & sytem dirt. Also dirt observed in suction strainer. System not flushed properly. | null | closed | Replaced Kit delivery valve
2019-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chand International | Thane | PC2 | 331K3045 | 2408063929 | 2019-12-10 | 240806 | 2019-12-06 | high oil consumption | 2019-06-23 | 2019-08-29 | 774 | null | null | 3 | Low suction Pr. 0.3 to 0.4 bar instead of required 1.1bar. Also dust found in compressor. | null | closed | Replaced Piston ring set2 nos.
2019-12-21 | Parag Marketing Services | null | D | Agrani Foods & Agro Processing Pvt Ltd | Sangli | KCX3 | 3374K2067 | 2402143895 | 2019-11-27 | 240214 | 2019-11-27 | knocking / abnormal sound | 2019-03-11 | 2019-05-28 | 407 | null | null | 2 | Cylinder no.1 cylinder liner & Piston ring set wornout | null | closed | Replaced Liner & Piston ring set.
2019-12-21 | Kalp Marketing | Gujrat | D | D Parfu Company Dave Dada Food | Gujrat | KCX2 | 3364K1659 | 2404403905 | 2019-11-30 | 240440 | 2019-11-30 | loading / unloading problem | 2018-10-29 | 2019-11-30 | 66 | null | null | 13 | Loading prblem due to NO Type solenoid valve not working. | null | closed | Replaced NO Type solenoid valve
2019-12-21 | Trade Links | Secunderabad | D | Aditya Industries | Andhra Pradesh | KCX6 | 3394K1260 | 2405863898 | 2019-11-28 | 240586 | 2019-11-28 | loading / unloading problem | 2019-01-21 | 2019-05-03 | 3764 | null | null | 5 | Loading prblem due to NO Type solenoid valve not working. | null | closed | Replaced NO Type solenoid valve
2019-12-21 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX63 | 3464K042 | 2406903906 | 2019-11-30 | 240690 | 2019-11-30 | loading / unloading problem | 2019-03-20 | 2019-10-12 | 35 | null | null | 7 | Solenoid valve NC 1 no. & NO 1 no malfunctioning. | null | closed | Replaced Solenoid valve NC 1 no. & NO 1 no.
2019-12-21 | Geekay Pneumatic Pvt Ltd | null | D | Frontline Exports Pvt Ltd | Kerala | KCX3 | 3374K1937 | 2403763890 | 2019-11-25 | 240376 | 2019-11-25 | oil carry over | 2018-10-08 | 2019-04-09 | 3156 | null | null | 6 | Cylinder no.2 piston hair line crack & piston rings wornout. | null | closed | Replaced Piston & Piston ring set.
2019-12-21 | Kalp Marketing | Gujrat | D | Salet Sea Food Pvt Ltd | Gujrat | KCX42 | 3444K151 | 2402743883 | 2019-11-19 | 240274 | 2019-11-19 | oil pressure problem | 2019-03-28 | 2019-08-26 | 171 | null | null | 5 | Crankshaft and all bearings found damaged and compressor tripped on OP. System dirt problem. | null | closed | Replaced Crankshaft , bearings & One piston & piston ring set.
2019-12-21 | Parag Marketing Services | null | D | Mehata Dairies | Kolhapur | KCX3 | 3374K1832 | 2387723805 | 2019-10-09 | 238772 | 2019-10-08 | oil pressure problem | 2018-06-08 | 2018-09-07 | 7841 | null | null | 1 | Compressor tripped on OP due to pump element tang broken. | null | closed | Replaced pump element.
2019-12-21 | Trade Links | Secunderabad | D | Sri Satya Ice Factory | Andhra Pradesh | KCX3 | 3374K1758 | 2398643871 | 2019-11-13 | 239864 | 2019-11-12 | oil pump purging | 2018-03-12 | 2018-10-11 | 4235 | null | null | 7 | Purging problem due to regulator problem. | null | closed | Replaced OPR
2019-12-21 | Geekay Pneumatic Pvt Ltd | null | D | Charley Fishries | Kerala | KCX3 | 3374K2140 | 2398883870 | 2019-11-12 | 239888 | 2019-11-12 | op pressure switch malfunctioning | 2019-07-05 | 2019-11-12 | ZH | null | null | 5 | OP Switch not tripping. Gky taken help of danfoss technical team but couldnt rectified. | null | closed | Replaced OP Swithch.
2019-12-21 | Parag Marketing Services | null | D | Lasa Laboratories Pvt Ltd | Ratnagiri | KCX6 | 3394K1357 | 2396003859 | 2019-11-06 | 239600 | 2019-11-06 | overheating problem | 2019-05-25 | 2019-08-25 | 1200 | null | null | 3 | Cylinder no.4 overheat due to delivery valve leakage. And cylinder no.6 Piston crack. | null | closed | Replaced DV & Piston.
2019-12-21 | Kalp Marketing | Gujrat | D | Gold Fish Ice Factory | Daman & Diu | KCX6 | 3394K1333 | 2407803930 | 2019-12-10 | 240780 | 2019-12-10 | shaft seal leakage | 2019-05-31 | 2019-07-31 | 1885 | null | null | 3 | Shaft seal leakage | null | closed | Replaced Oring kit
2019-12-31 | Kalp Marketing | Gujrat | D | New Faizan Foods | Gujrat | KCX51 | 3454K130 | 2382503795 | 2019-09-30 | 238250 | 2019-09-30 | high discharge pressure | 2019-08-14 | 2019-08-21 | 208 | null | null | 1 | Compresor running on high discharge. DV leakage & Buffer spring shrink. | null | closed | Replaced buffer spring & DV
2019-12-31 | Trade Links | Secunderabad | D | Frigerio Conserva Allana Ltd | Telangana | KCX42 | 3444K175 | 2415003958 | 2019-12-23 | 241500 | 2019-12-23 | krms temperature sensor problem. | 2019-08-05 | 2019-12-14 | 28 | null | null | 5 | Malfuctioning suction & discharge sensors. | null | closed | Replaced suction & discharge sensors.
2019-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Mampilly Ice Factory | Kerala | KCX2 | 3364K1764 | 2414983955 | 2019-12-21 | 241498 | 2019-12-21 | piston crack | 2019-04-21 | 2019-10-03 | 1096 | null | null | 6 | Both piston has been damaed , one liner wornout & delivery valve damaged. | null | closed | Replaced Piston , Piston ring set , Cylinder liner , Gudgeon pin .
2019-12-31 | Cool Comfort Private Limited | West Bengal | D | Sahada Exports | West Bengal | KCX51 | 3454K121 | 2413083940 | 2019-12-16 | 241308 | 2019-12-31 | solenoid valve leakage | 2019-05-29 | 2019-06-25 | 2705 | null | null | 1 | Leakage from bottom of solenoid valves. | null | closed | Replaced 2 solenoid valve
2019-12-31 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX72 | 3474K156 | 2412223937 | 2019-12-13 | 241222 | 2019-12-13 | solenoid valve leakage | 2018-02-06 | 2018-10-08 | 1896 | null | null | 8 | Solenoid valve leakage 3 nos. In loading & unloading condition. | null | closed | Replaced 3 solenoid valve
2019-12-31 | Cool Comfort Private Limited | West Bengal | D | Global Aqua | Howrah, West Bengal | KCX51 | 3454K064 | 2412403938 | 2019-12-13 | 241240 | 2019-12-31 | solenoid valve leakage | 2018-03-03 | 2019-01-25 | 1545 | null | null | 10 | Solenoid valve leakage 2 nos. In loading & unloading condition. | null | closed | Replaced 2 solenoid valve
2019-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Abn Exports | Kerala | KCX42 | 3444K134 | 2402323927 | 2019-12-09 | 240232 | 2019-12-09 | solenoid valve leakage | 2018-11-14 | 2019-12-09 | ZH | null | null | 13 | Leakage from solenoid valve adaptor and ferrules. After tightning leakage not rectified. | null | closed | Replaced adaptors & ferrules 3 nos.
2019-12-31 | Kalp Marketing | Gujrat | D | Balaji Cold Storage | Gujrat | KCX42 | 3444K185 | 2406463921 | 2019-12-05 | 240646 | 2019-12-05 | suction pressure gauge out 16kg/cm2. | 2019-10-26 | 2019-12-05 | ZH | null | null | 3 | Dial indicator jammed. | null | closed | Replaced Pressure gauge
2020-01-18 | Trade Links | null | D | Illios Breweries Pvt Ltd | Andhra Pradesh | KCX9 | 3404K110 | 2420124002 | 2020-01-06 | 242012 | 2020-01-10 | abnormal noise | 2018-08-28 | 2019-04-09 | 2425 | null | null | 7 | Delivery valve lealage , liner & piston damaged. | null | closed | Replaced Piston , Liner , Buffer spring , DV etc.
2020-01-18 | Trade Links | null | D | Sri Chaitanya Chilorides Pvt Ltd | Telangana | KCX4 | 3384K2270 | 2411703988 | 2020-01-01 | 241170 | 2019-12-13 | abnormal noise | 2019-06-03 | 2019-09-07 | 954 | null | null | 4 | Piston crack & Piston rings wornout. | null | closed | Relaced Piston & Piston ring set 2nos.
2020-01-18 | Trade Links | null | D | Sri Chaitanya Chilorides Pvt Ltd | Telangana | KCX4 | 3384K2270 | 2414263951 | 2019-12-19 | 241426 | 2019-12-20 | abnormal noise | 2019-06-03 | 2019-09-07 | 1107 | null | null | 4 | Abnormal sound due to buffer spring shrunk | null | closed | Replaced buffer spring
2020-01-18 | Kirloskar Dmcc | null | E | Kirloskar Middle East Fze | null | KCX4 | 3384K5664 | MAIL | 2020-01-18 | null | 2020-01-18 | fitting leakage & poor aesthetics | 2018-10-14 | 2020-01-12 | PC | null | null | 14 | Welding run poor quality, Fitting leakage, Oil strainer inclined, Stop valve handle not working , poor painting at pump arrow. TD Sticker attached to NC Solenoid valve etc. | null | open | null
2020-01-18 | Kalp Marketing | Gujrat | D | Welldone Impex | Gujrat | KCX51 | 3454K067 | 2406143901 | 2019-11-28 | 240614 | 2019-11-29 | high oil consumption | 2018-03-23 | 2018-09-18 | 341 | null | null | 5 | Piston rings wornout , ORV & DV Leakage 2 nos. | null | closed | Replaced 6 pistong ring sets , 2 ORV & 2 dv Kit.
2020-01-18 | Trade Links | null | D | Jai Shankar Icce Plant | Andhra Pradesh | KCX6 | 3394K1291 | 2416623990 | 2020-01-02 | 241662 | 2019-12-26 | krms issue | 2019-02-27 | 2019-06-26 | 2818 | null | null | 4 | Panel board and smps unit not working | null | closed | Replaced remote monitoring system kit
2020-01-18 | Trade Links | null | D | Ja Shankar Ice Industry | null | KCX4 | 3384K2216 | 2416643991 | 2020-01-02 | 241664 | 2019-12-26 | krms issue | 2019-02-27 | 2019-06-26 | 2729 | null | null | 4 | Panel board and smps unit not working | null | closed | Replaced remote monitoring system kit
2020-01-18 | Trade Links | null | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1951 | 2405383902 | 2019-11-29 | 240538 | 2019-11-29 | oil lifting | 2018-04-16 | 2018-08-24 | 6283 | null | null | 4 | Oil throw from all 4 cylinders and Cyl 1 & 2 piston crack. | null | closed | Replaced piston 2 nos & Piston ring set 04 nos.
2020-01-18 | Trade Links | null | D | Illios Breweries Pvt Ltd | Andhra Pradesh | KCX3 | 3374K1902 | 2419404001 | 2020-01-06 | 241940 | 2020-01-10 | over heating | 2018-08-27 | 2019-06-19 | 1355 | null | null | 9 | Cylinder overheating due to DV leakage | null | closed | Replaced delivery valve assembly.
2020-01-18 | Kalp Marketing | Gujrat | D | S S International | Gujrat | KCX72 | 3474K295 | 2404323889 | 2019-11-25 | 240432 | 2019-11-25 | over heating | 2019-06-17 | 2019-08-12 | 1998 | null | null | 3 | High discharge tempeature due to delivery valve ring spring broken, Liner , Piston and piston rings got damaged. | null | closed | Replaced Piston , Piston ring set , Cylinder liner & Kit DV.
2020-01-18 | Kalp Marketing | Gujrat | D | Sun Marine Exports | Gujrat | KCX93 | 3485K060 | 2417503984 | 2019-12-30 | 241750 | 2019-12-30 | over heating | 2019-06-30 | 2019-09-07 | 565 | null | null | 4 | Cylinder no.4 overheating due to delivery valve leakage.. | null | closed | Replaced delivery valve kit.
2020-01-18 | Trade Links | null | D | Venkata Mahadhavi Ice Factory | Andhra Pradesh | KCX6 | 3394K1114 | 2416463973 | 2019-12-26 | 241646 | 2019-12-26 | over heating | 2018-07-04 | 2018-12-29 | 9010 | null | null | 5 | Cylinder no. 4 overheated due to delivery valve leakage. Also buffer spring shrink. | null | closed | Replaced delivery valve and buffer spring.
2020-01-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | A One Milk Products Pvt Ltd | Kerala | KCX2 | 3364K1643 | 2420824005 | 2020-01-07 | 242082 | 2020-01-07 | pump purging problem | 2018-09-30 | 2019-05-21 | 733 | null | null | 9 | Compressor no load due to purging problem. | null | closed | Replaced pump assembly
2020-01-18 | Trade Links | null | D | Sri Chaitanya Chilorides Pvt Ltd | Telangana | KCX4 | 3384K2270 | 2418763394 | 2020-01-03 | 241876 | 2020-01-04 | shaft seal leakage | 2019-06-03 | 2019-09-07 | 1452 | null | null | 4 | Shaft seal leakage. | null | closed | Replaced shaft seal assembly.
2020-01-18 | Robin Refrigeration Works | Odisha | D | Pragati Milk Products (P) Ltd | Odisha | KCX3 | 3374K2123 | 2417683992 | 2020-01-02 | 241768 | 2020-01-08 | shaft seal leakage | 2019-06-08 | 2019-11-11 | 113 | null | null | 5 | Shaft seal leakage due to Oring missing. Oring fitted but leakage continue. | null | closed | Replaced shaft seal assembly
2020-01-18 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K1912 | 2409023919 | 2019-12-05 | 240902 | 2019-12-05 | shaft seal leakage | 2018-09-11 | 2018-09-18 | 4989 | null | null | 1 | Shaft seal screw broken . | null | closed | Replaced shaft seal assembly.
2020-01-18 | Robin Refrigeration Works | Odisha | D | Maa Jamuna Ice Factory | Odisha | KCX4 | 3384K2231 | 2420044011 | 2020-01-10 | 242004 | 2020-01-10 | vibration problem | 2019-03-16 | 2019-06-19 | 1020 | null | null | 3 | High vibration at suction & discharge . Visited site by Tapan mandal & sondkar. | null | closed | Replaced all bearings , Liner & Piston 2 nos.
2020-01-18 | Parag Marketing Services | null | D | Tripti Carbonic | Solapur | KCX42 | 3444K159 | Mail | 2019-12-28 | null | 2019-12-28 | wrong fitment of suction strainer element & cloth bag missing. | 2019-05-01 | 2019-12-28 | ZH | null | null | 7 | Suction strainer element fitted in opposite direction & Also cloth bag not fitted. | null | closed | Rectified at site
2020-01-20 | Fridge House | null | D | Yashawi Fish Meal & Oil Company | Karnataka | KCX6 | 3394K1075 | 2421504017 | 2020-01-13 | 242150 | 2020-01-09 | abnormal noise | 2018-05-06 | 2019-05-26 | 5093 | null | null | 12 | Cylinder no.4 delivery valve leakage, Liner , piston & piston rings wornout. | null | closed | Replaced liner , piston , piston ring set and Kit DV.
2020-01-20 | Cool Comfort Private Limited | West Bengal | D | Mother Dairy Fruits & Vegetables Pvt Ltd | Bihar | KCX4 | 3384K1974 | 2414243954 | 2019-12-21 | 241424 | 2020-01-07 | shaft seal leakage | 2018-06-05 | 2019-01-02 | 1746 | null | null | 7 | Rotory and stationary sealing ring wornout - Replaced shaft seal. | null | closed | Replaced shaft seal assembly
2020-01-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Brilliant Ice Factory | Kerala | KCX2 | 3364K1586 | 2420064003 | 2020-01-07 | 242006 | 2020-01-07 | shaft seal leakage | 2018-06-24 | 2019-07-25 | 1940 | null | null | 12 | Shaft seal wornout | null | closed | Replaced shaft seal assembly
2020-01-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Crescent Cold Storage Pvt Ltd | Mumbai | KCX4 | 3384K2056 | 2420364015 | 2020-01-13 | 242036 | 2020-01-09 | air purging problem | 2018-08-31 | 2019-06-15 | 665 | null | null | 10 | Oil pressure not develop at initial startup | null | closed | Replaced oil pump assembly
2020-01-22 | Trade Links | null | D | Soham Ice Industries | Andhra Pradesh | KCX4 | 3384K1950 | 2409123922 | 2019-12-06 | 240912 | 2019-12-06 | high oil consumption | 2018-04-16 | 2018-08-25 | 6444 | null | null | 4 | Oil lifting problem due to piston rings wornout and ORV Problem. | null | closed | Replaced piston ring set 4
2020-01-22 | Trade Links | Goa | D | Royal Foods Goa | null | KCX3 | 3374K1935 | 2413903952 | 2019-12-20 | 241390 | 2019-12-18 | oil carry over | 2018-10-05 | 2019-01-02 | 10 | null | null | 3 | Piston crack & piston rings worout | null | closed | Replaced Piston & piston rings
2020-01-22 | Trade Links | null | D | Ananda Fisheries | Andhra Pradesh | KCX3 | 3374K2164 | 2422084018 | 2020-01-13 | 242208 | 2020-01-10 | oil leakage & air purging | 2019-09-27 | 2019-11-30 | 863 | null | null | 3 | Oil leakage & air purging due to mail run tee threading spoil/damaged. | null | closed | Replaced male run tee
2020-01-28 | Multivista Global Pvt Ltd | null | D | Ammaya Dairy | Tamil Nadu | KCX2 | 3364K1470 | 2406163907 | 2019-11-30 | 240616 | 2019-11-30 | knocking / abnormal sound | 2018-01-06 | 2019-10-29 | ZH | null | null | 19 | Knocking sound due to suction spring broken. | null | closed | Replaced valve spring suction
2020-01-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Thane | KCX2 | 3364K1827 | 2415744031 | 2020-01-20 | 241574 | 2020-01-18 | low oil pressure problem | 2019-08-21 | 2020-01-18 | ZH | null | null | 5 | Oil pressure found 0.8Kg/cm2 i.e. Low oil pressure. | null | closed | Replaced oil pump assembly
2020-01-28 | Trade Links | Secunderabad | D | Ananda Fisheries | Andhra Pradesh | KCX3 | 3374K2164 | 2427024042 | 2020-01-24 | 242702 | 2020-01-10 | oil pressure problem | 2019-09-27 | 2019-11-30 | 900 | null | null | 3 | Air purging problem | null | closed | Replaced pump assembly
2020-01-28 | Trade Links | Secunderabad | D | Ananda Fisheries | Andhra Pradesh | KCX3 | 3374K2164 | 2424724037 | 2020-01-22 | 242472 | 2020-01-24 | op cutout not working | 2019-09-27 | 2019-11-30 | 981 | null | null | 3 | OP triped in 13 sec | null | closed | Replaced OP Cutout
2020-01-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vipul Organics Ltd | Mumbai | KCX4 | 3384K2048 | 2424504033 | 2020-01-21 | 242450 | 2020-01-21 | over heating | 2018-08-28 | 2019-12-08 | ZH | null | null | 16 | Cylinder no.1 delivery valve leakage and piston , piston rings damaged. | null | closed | Replaced DV , Piston & Piston ring set.
2020-01-31 | Multivista Global Pvt Ltd | null | D | Rr Ice Plant | Tamil Nadu | KCX2 | 3364K1766 | 2393983867 | 2019-11-10 | 239398 | 2019-10-25 | oil carry over | 2019-04-23 | 2019-06-04 | 1782 | null | null | 1 | Replaced cylinder liner and piston ring set-2nos. | null | closed | Replaced cylinder liner and piston ring set2nos.
2020-01-31 | Hss Solution Pvt Ltd | null | D | Anurag Ice Factory | Rajastan | KCX2 | 3364K1813 | 2423704032 | 2020-01-20 | 242370 | 2020-01-21 | short supply ferule and tee | null | null | null | null | null | null | Short supply -Ferule and Tee | null | closed | Short supply Ferule and Tee
2020-01-31 | Multivista Global Pvt Ltd | null | D | Prs DairyTamilnadu | null | PC2 | 331K3058 | 2421684044 | 2020-01-26 | 242168 | 2020-01-26 | valve lifting sleeve broken | 2019-09-02 | null | ZH | null | null | null | Cpompressor rusty and valve lifting sleeve broken | null | closed | Replace valve lifting sleeve PC2
2020-02-16 | Kirloskar Pneumatic Co Ltd | New Delhi | D | International Agro Food | Uttar Pradesh | KC72 | 347K992 | 2433464085 | 2020-02-11 | 243346 | 2020-02-11 | abnormal noise | 2019-10-25 | 2019-12-31 | 177 | null | null | 2 | Both HP Cylinder liners ,Piston & piston rings wornout. | null | closed | Replaced Liner , Piston & Piston rings.
2020-02-16 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Penam Laboratories Limited | Haryana | KCX84 | 3305K003 | 2434844079 | 2020-02-10 | 243484 | 2020-02-10 | abnormal noise | 2018-12-10 | 2019-01-29 | 7593 | null | null | 1 | Cylinder no. 1 Piston wornout & needle roller bearing in broken condition. | null | closed | Replaced Piston , Needle roller bearing & spacer.
2020-02-16 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2433784077 | 2020-02-10 | 243378 | 2020-02-10 | abnormal noise | 2018-09-12 | 2019-02-08 | 1139 | null | null | 5 | Abnormal sound from cylinder 3 & 6 . Delivery valve leakage for both cylinders. Spring broken. | null | closed | Replaced DV
2020-02-16 | Trade Links | null | D | Device Factory | Andhra Pradesh | KCX6 | 3394K1293 | 2434824084 | 2020-02-11 | 243482 | 2020-02-11 | air purging problem | 2019-03-10 | 2019-04-30 | 2872 | null | null | 1 | KCX Oil pump air purging problem. | null | closed | Replaced Pump element
2020-02-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Jay Chemical Industries Ltd | Gujrat | KCX6 | 3394K1379 | 2433684071 | 2020-02-07 | 243368 | 2020-02-07 | crankshaft wornout | 2019-07-27 | 2019-09-11 | 3084 | null | null | 3 | Crankshaft wornout and broken at key way. | null | closed | Replaced Crankshaft
2020-02-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K012 | 2405743900 | 2019-11-28 | 240574 | 2019-11-28 | cylinder overheating | 2017-12-11 | 2018-08-03 | 6030 | null | null | 8 | Cylinder no. 7 delivery valve leakage due to ring broken. | null | closed | Replaced kit delivery valve.
2020-02-16 | Trade Links | null | D | Virchow Petro Chemicals Pvt Ltd | Telangana | KCX72 | 3474K289 | 2422464040 | 2020-01-23 | 242246 | 2020-01-23 | cylinder overheating | 2019-05-26 | 2019-12-26 | 70 | null | null | 7 | Abnormal sound from cylinder no. 4 HP, Observed delivery valve leakage due to this liner , piston wornout. | null | closed | Replaced Delivery valve , Liner , Piston , Piston ring set & Buffer spring.
2020-02-16 | Kalp Marketing | Gujrat | D | Apex Industries | Ahmedabad | KCX4 | 3384K2477 | Mail Marwade | 2020-02-11 | null | null | flywheel paint peeloff | null | 2020-02-11 | ZH | null | null | null | At the time of commissioning observed flywheel paint peel off. | null | open | null
2020-02-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Lupin Limited | Ankleshwar Gujarat | KCX6 | 3394K1294 | 2422024012 | 2020-01-10 | 242202 | 2020-01-10 | knocking sound piston crack | 2019-03-15 | 2019-08-08 | 2865 | null | null | 5 | Piston crack | null | closed | Replaced piston & piston ring set.
2020-02-16 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun Beverages Limited | Punjab | KCX9 | 3404K107 | 2436324091 | 2020-02-12 | 243632 | 2020-02-12 | krms connection data loss | 2018-09-12 | 2019-02-08 | 1145 | null | null | 5 | KRMS Suction temperature sensor fitment problem in thremowell due to drill hole undersize. | null | closed | Replaced power supply adaptor/ Transformer .
2020-02-16 | Robin Refrigeration Works | Odisha | D | Teekay Marines Pvt Ltd | Odisha | KCX93 | 3485K053 | MailMandal | 2020-02-16 | 242780 | 2020-02-03 | machining burr in cylinder | 2019-03-23 | 2020-02-03 | ZH | null | null | 10 | Machining burr found in compressor cylinder no. 5,8 &11 during commissioning. | null | closed | null
2020-02-16 | Trade Links | null | D | Nadhi Bio Products Pvt Ltd | Telangana | KCX93 | 3485K054 | 2432384068 | 2020-02-07 | 243238 | 2020-02-06 | oil pressure problem | 2019-03-20 | 2019-06-13 | 3508 | null | null | 4 | Oil pressure not develop due to pump element tang broken. | null | closed | Replaced Pump element
2020-02-16 | Hss Solution Pvt Ltd | null | D | Shree Balaji Chilling Plant | Rajastan | KCX2 | 3364K1879 | 2432424067 | 2020-02-05 | 243242 | 2020-02-05 | op pressure switch malfunctioning | 2019-11-27 | 2019-12-12 | ZH | null | null | 1 | OP Cutout malfunctioning | null | closed | Replaced OP Cutout
2020-02-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shivangi Ice Factory | Gujrat | KCX6 | 3394K1301 | 2422504014 | 2020-01-11 | 242250 | 2020-01-11 | op pressure switch malfunctioning | 2019-03-28 | 2019-05-25 | 3500 | null | null | 2 | Oil pressure switch faulty. Backside connection burnt due to continuous power supply from micro switch. | null | closed | Replaced OP Switch
2020-02-16 | Gargi Engineering Enterprices Pvt Ltd | null | D | Thakur Mhatre Jv | Uran,Maharastra | KCX42 | 3444K169 | 2414923966 | 2019-12-24 | 241492 | 2019-12-23 | pressure gauge leak | 2019-06-30 | 2019-12-23 | ZH | null | null | 6 | Discharge pressure gauge glass swollen & glycerine leaked. | null | closed | Replaced pressure gaauge
2020-02-16 | Trade Links | null | D | Sri Chaitanya Chilorides Pvt Ltd | Telangana | KCX4 | 3384K2270 | 2433344072 | 2020-02-07 | 243334 | 2020-02-07 | shaft seal leakage | 2019-06-03 | 2019-09-07 | 2137 | null | null | 3 | Repeated shaft seal leakage - Freon gas application. | null | closed | Replaced shaft seal assly & COVER
2020-02-16 | Trade Links | null | D | Sri Chaitanya Chilorides Pvt Ltd | Telangana | KCX4 | 3384K2270 | 2430864062 | 2020-02-04 | 243086 | 2020-02-04 | shaft seal leakage | 2019-06-03 | 2019-09-07 | 2137 | null | null | 3 | Repeated shaft seal leakage - Freon gas application. | null | closed | Replaced shaft seal assly
2020-02-24 | S M Refrigeration | null | D | Kanisha Cold Storage | Kannauj | KCX6 | 3394K1461 | 2439984113 | 2020-02-19 | 243998 | 2020-02-24 | oil pressure not buildup | 2019-12-01 | 2020-02-18 | 20 | null | null | 2 | KCX oil pump tang broken | null | closed | KCX oil pump element
2020-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mothebaba Dudh Shitkaran Kendra | Ahmed Nagar | KCX2 | 3364K1810 | 2427284043 | 2020-01-25 | 242728 | 2020-01-25 | abnormal noise | 2019-06-29 | 2019-11-13 | 605 | null | null | 5 | Cylinder liner worn out and step observed | null | closed | Replaced cylinder liner,piston ring set, big end bearing
2020-02-28 | Trade Links | null | D | Mahalaxmi Ice Factory | Andhra Pradesh | KCX2 | 3364K1852 | 2439864110 | 2020-02-19 | 243986 | 2020-02-19 | kcx oil pressure problem | 2019-09-25 | 2019-10-16 | 1778 | null | null | 1 | KCX oil pump tang broken | null | closed | Replace KCX oil pump element
2020-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | V S K Ice Maker | Gujrat | KCX3 | 3374K2100 | 2224424036 | 2020-01-22 | 242442 | 2020-01-22 | oil carry over | 2019-05-04 | 2019-05-18 | 3454 | null | null | 1 | oil carryover 9 liters in 100 hours, piston crack | null | closed | Replaced Piston, Piston ring set, ORV
2020-02-28 | Trade Links | null | D | Welcome Fisheries | Andhra Pradesh | KC3 | 337K4787 | 2439564123 | 2020-02-25 | 243956 | 2020-01-29 | oil leakage from filter | 2020-01-29 | 2020-02-13 | ZH | null | null | 1 | Oil leakage due to damaged pipe and ferule | null | closed | Replaced KC discharge top housing with pipe.
2020-02-28 | Parag Marketing Services | null | D | Raj Ice Factory | Raipur, Chhatisgarh | PCX2 | 3106K0013 | 2416744013 | 2020-01-11 | 241674 | 2020-02-04 | pressure gauge malfunctioning | 2019-11-05 | 2020-02-04 | ZH | null | null | 3 | Pressure gauge out 0 to 16 kg/cm2 | null | closed | Replaced pr. Gauge 0 to16 kg/cm2
2020-02-28 | S M Refrigeration | null | D | Bul Bul Cold Storage | Uttar Pradesh | KCX4 | 3384K2349 | 2417903989 | 2020-01-01 | 241790 | 2020-01-01 | pressure gauge not working | 2019-09-18 | 2020-01-01 | ZH | null | null | 3 | Pr. Gauge not working -760mmhg to 16 Kg/cm2 | null | closed | Replaced pressure gauge 0 to 16.0 kg/cm2
2020-02-28 | S M Refrigeration | null | D | Rukmini Cold Storage | Uttar Pradesh | KC4 | 338K5714 | 2436864096 | 2020-02-13 | 243686 | 2020-02-13 | pressure gauge not working | 2019-10-28 | 2020-02-13 | ZH | null | null | 3 | Pr. Gauge not working -760mmhg to 16 Kg/cm2 | null | closed | Replaced pressure gauge 0 to 16.0 kg/cm2
2020-02-28 | Parag Marketing Services | null | D | Shantinath Ice Factory | Jalana | KCX3 | 3374K2193 | 2425964039 | 2020-01-23 | 242596 | 2020-01-23 | pressure gauge not working | 2019-11-17 | 2020-01-23 | ZH | null | null | 2 | Pr. Gauge not working | null | closed | Replaced pressure gauge 0 to 16.0 kg/cm2
2020-02-28 | S M Refrigeration | null | D | R S Kushwaha Cold Storage | Uttar Pradesh | KC4 | 338K5725 | 2433844074 | 2020-02-08 | 243384 | 2020-02-08 | pressure switch not working | 2020-01-15 | 2020-02-08 | ZH | null | null | 1 | OP Pressure switch not working | null | closed | Replaced OP Pressure switch
2020-02-28 | Trade Links | null | D | Finolex Industries Limited | Ratnagiri | KC6 | 339K3526 | 2429364073 | 2020-02-08 | 242936 | 2020-02-08 | shaft seal leakage | 2019-05-14 | 2020-01-20 | 155 | null | null | 8 | Shaft seal leakage 2 to 3 drops in 10 min /R-22 | null | closed | Replaced shaft seal assly
2020-03-14 | Parag Marketing Services | null | D | S L Agro Foods | null | KCX31 | 3434K0112 | null | null | null | null | alignment was out from 8 mm | null | null | null | null | alighnment out by 8mm, compressor suction discharge piping fitted without flywheel & motor pulley alignment, also no problem in compressor and base frame found. | null | CLOSE | null | null | null
2020-03-14 | Trade Links | Secunderabad | D | Mahalakshmi Ice Factory | null | KCX2 | 3364K1852 | 2453984203 | 2020-03-18 | 245398 | 2020-03-18 | abnormal noise | null | null | null | null | replaced cylinder liner 1 | null | CLOSE | null | replaced cylinder liner -1 | null
2020-03-14 | Geekay Pneumatic Pvt Ltd | null | D | Pulikkalakath Ice Factory | null | KCX3 | 3374K1987 | 2454904207 | 2020-03-20 | 245490 | 2020-03-20 | oil lifting | null | null | null | null | replaced cylinder liner 2 | null | CLOSE | null | replaced cylinder liner -2 | null
2020-03-14 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Varun BeveragesPathankotPunjab | null | KCX9 | 3404K108 | 2444744139 | 2020-02-29 | 244474 | 2020-02-29 | abnormal noise | 2018-09-12 | 2019-02-08 | 1211 | null | null | 4 | Tap bolt broken in cylinder no.09 | null | closed | Replaced tap bolt
2020-03-14 | S M Refrigeration | null | D | J K Cold Storage | Uttar Pradesh | KCX6 | 3394K1501 | 2443224132 | 2020-02-27 | 244322 | 2020-02-26 | pressure gauge not working | 2020-01-20 | 2020-02-26 | ZH | null | null | 1 | Replaced pressure gauge | null | closed | Suction Pressure gauge
2020-03-14 | Trade Links | null | D | Sphorthi Sri Cold Storage | Andhra Pradesh | KCX2 | 3364K1915 | 2441984121 | 2020-02-24 | 244198 | 2020-02-24 | pressure gauge not working | 2020-01-17 | 2020-02-24 | ZH | null | null | 1 | Negative error in suction pressure gauge | null | closed | Suction Pressure gauge
2020-03-14 | Export | null | E | Thai Union | Thailand | null | null | null | null | null | null | v belt fitment problem | null | null | ZH | null | null | null | CLOSE | null | null | null
2020-03-22 | Trade Links | null | D | Masqati Dairy Products | Telangana | KCX2 | 3364K1629 | 2449944176 | 2020-03-11 | 244994 | 2020-03-14 | abnormal noise | 2018-08-29 | 2019-01-31 | 997 | null | null | 5 | Delivery valve leakage, piston and liner siezed | null | closed | Replaced delivery valve, piston, piston rings.
2020-03-22 | Kalp Marketing | Gujrat | D | Sun Marine Exports | Gujrat | KCX93 | 3485K060 | 2445184141 | 2020-03-02 | 244518 | 2020-03-02 | abnormal noise | 2019-06-30 | 2019-09-07 | 636 | null | null | 3 | Delivery valve leak and buffer sping length shortened | null | closed | Buffer spring and delivery valve
2020-03-22 | Kalp Marketing | Gujrat | D | Indian Exports | Gujrat | KCX51 | 3454K126 | 2445484142 | 2020-03-02 | 244548 | 2020-03-02 | cylinder liner tap bolt broken | 2019-06-29 | 2019-07-31 | 1953 | null | null | 1 | Cylinder liner tap bolt broken | null | closed | Tap bolts replaced
2020-03-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jehoshamma Ice Factory | Andhra Pradesh | KCX4 | 3384K2312 | 2442584127 | 2020-02-25 | 244258 | 2020-02-26 | cylinder overheating | 2019-08-21 | 2019-10-25 | 1141 | null | null | 2 | Delivery valve ring spring broken and piston siezed | null | closed | Replaced del. Valve,liner,piston, piston ring set
2020-03-22 | Parag Marketing Services | null | D | Himalaya Ice Factory | null | KCX4 | 3384K2085 | 2436304093 | 2020-02-12 | 243630 | 2020-02-12 | high oil consumption | 2018-09-18 | 2019-07-03 | 12 | null | null | 10 | oil carryover | null | closed | Replaced piston ring set
2020-03-22 | S M Refrigeration | null | D | Gareeb Nawaj Cold Storage | Uttar Pradesh | KC4 | 338K5726 | 2448604161 | 2020-03-07 | 244860 | 2020-03-07 | kc oil pump tang broken | 2020-01-29 | 2020-02-21 | 24 | null | null | 1 | Tang broken and scoring on cover plate | null | closed | Replaced oil pump assly
2020-03-22 | S M Refrigeration | null | D | Gareeb Nawaj Cold Storage | Uttar Pradesh | KC4 | 338K5726 | 2442344130 | 2020-02-25 | 244234 | 2020-03-06 | kc oil pump tang broken | 2020-01-29 | 2020-02-21 | 24 | null | null | 1 | Tang broken and scoring on cover plate | null | closed | Replaced Gear kit and cover plate
2020-03-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | H P Ice FactoryBhigwan | Pune | KCX3 | 3374K2035 | 2441124117 | 2020-02-22 | 244112 | 2020-02-21 | knocking / abnormal sound | 2019-02-27 | 2019-04-04 | 4122 | null | null | 2 | Piston crack, ring spring kit broken | null | closed | Replaced piston2nos. and del valve1no.
2020-03-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jay Chemicals | Vapi, Gujarat | KCX6 | 3394K1379 | 2447904159 | 2020-03-06 | 244790 | 2020-03-08 | piston crack | 2019-07-27 | 2019-09-11 | 3084 | null | null | 2 | Piston and piston ring set replaced | null | closed | Piston and piston ring set replaced
2020-03-22 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX4 | 3384K2286 | 2427884173 | 2020-03-11 | 242788 | 2020-05-14 | power supply adaptor and hardware for remote monitoring replaced. required for field trial suggested by d&d. | 2019-06-30 | 2020-03-13 | ZH | null | null | 8 | Remote monitoring system hardware and power supply adaptor upgradation | null | closed | Remote monitoring system hardware and power supply adaptor upgradation
2020-03-22 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX31 | 3434K0105 | 2427724180 | 2020-03-13 | 242772 | 2020-01-30 | power supply adaptor and hardware for remote monitoring replaced. required for field trial suggested by d&d. | 2019-06-30 | 2020-03-13 | ZH | null | null | 8 | Remote monitoring system hardware and power supply adaptor upgradation | null | closed | Remote monitoring system hardware and power supply adaptor upgradation
2020-03-22 | S M Refrigeration | null | D | Kajal Cold Storage | Uttar Pradesh | KCX6 | 3394K1442 | 2437384152 | 2020-03-05 | 243738 | 2020-03-05 | pressure gauge glycerin leak | 2019-12-10 | 2020-03-05 | ZH | null | null | 3 | Replaced pressure gauge | null | closed | Suction Pressure gauge
2020-03-22 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX31 | 3434K0106 | 2427904179 | 2020-03-13 | 242790 | 2020-03-13 | remote monitoring hardware and power supply adaptor upgradation | 2019-06-30 | 2020-03-13 | ZH | null | null | 8 | Remote monitoring system hardware and power supply adaptor upgradation | null | closed | Remote monitoring system hardware and power supply adaptor upgradation
2020-03-22 | Parag Marketing Services | null | D | Frigerio Conserva Allana Ltd | Telangana | KCX42 | 3444K175 | 2410543939 | 2019-12-14 | 241054 | 2019-12-14 | rusting of internal parts i.e. liner del. vlave | 2019-08-05 | 2019-12-14 | 8 | null | null | 4 | Replaced cylinder liner, Del valve,Bearings. | null | closed | null
2020-04-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Delta Referiferation | Thane | KCX3 | 3374K2073 | 2452924204 | 2020-03-19 | 245292 | 2020-03-17 | high oil consumption | 2019-03-22 | 2019-04-13 | 2459 | null | null | 1 | ORV , VLD orings replaced | null | closed | ORV , VLD orings replaced
2020-04-28 | Trade Links | null | D | Mahalaxmi Ice Factory | Andhra Pradesh | KCX2 | 3364K1852 | 2453984203 | 2020-03-18 | 245398 | 2020-03-19 | high oil consumption | 2019-09-25 | 2019-10-16 | 2146 | null | null | 1 | Piston crack , liner and piston rings worn out. | null | closed | Piston, liner,piston rings
2020-04-28 | Kalp Marketing | Gujrat | D | Ambika Ice Factory | Gujrat | KCX2 | 3364K1670 | 2444144134 | 2020-02-28 | 244414 | 2020-02-28 | kcx oil pressure problem | 2018-11-27 | 2019-04-15 | 2200 | null | null | 5 | KCX oil pressure problem | null | closed | Replaced KCX old type oil pump
2020-04-28 | Trade Links | null | D | 3F Industries Ltd | Andhra Pradesh | KCX63 | 3364K026 | 2426984206 | 2020-03-20 | 242698 | 2020-02-04 | kcx oil pump purging | 2018-10-12 | 2019-08-28 | 2481 | null | null | 10 | KCX oil pump purging issue-Replaced oil pump | null | closed | Replaced oil pump assly
2020-04-28 | Robin Refrigeration Works | Odisha | D | Daitri Ice Plant | Odisha | KCX3 | 3374K2062 | 2445764181 | 2020-03-14 | 244576 | 2020-03-14 | op pressure switch malfunctioning | 2019-03-05 | 2020-03-14 | 25 | null | null | 12 | OP pressure switch not working | null | closed | Replaced OP Pressure switch
2020-04-28 | Trade Links | null | D | Adi Lakshmi Cold Storage | Andhra Pradesh | KCX3 | 3374K1955 | 2452544186 | 2020-03-17 | 245254 | 2020-03-16 | stop valve problem | 2018-11-19 | 2019-02-12 | 1979 | null | null | 3 | Discharge tal valve spindle damaged | null | closed | Spindle assly and teflon seat
2020-04-28 | Kalp Marketing | Gujrat | D | Ram Hi Tech | Gujrat | KCX3 | 3374K2237 | 2441404115 | 2020-02-21 | 244140 | 2020-02-21 | v belt broken | 2019-12-23 | 2020-02-21 | ZH | null | null | 2 | V belt broken 01 no. may be due to wrong fitment | null | closed | Replaced V belt
2020-05-29 | S M Refrigeration | null | D | A&R Sons Cold Storage And General Mills | Uttar Pradesh | KCX4 | 3384K2410 | 2451704216 | 2020-05-06 | 245170 | 2020-05-16 | op pressure switch malfunctioning | 2019-12-09 | 2020-05-16 | ZH | null | null | 5 | OP Pressure switch not working | null | closed | OP Pressure switch
2020-06-13 | Gargi Engineering Enterprices Pvt Ltd | null | D | Yogiraj Cold Storage | Gujrat | KCX3 | 3374K2203 | 2458864230 | 2020-06-01 | 245886 | 2020-05-20 | kcx oil pressure problem | 2019-11-27 | 2020-03-19 | ZH | null | null | 4 | KCX oil pump air purging | null | closed | KCX oil pump assly
2020-06-13 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K2299 | 2456884229 | 2020-06-01 | 245688 | 2020-04-19 | kcx oil pressure problem | 2020-02-14 | 2020-03-21 | 95 | null | null | 1 | KCX oil pump air purging | null | closed | KCX oil pump assly
2020-06-13 | Robin Refrigeration Works | Odisha | D | Daitri Ice Plant | Odisha | KCX3 | 3374K2062 | 2460904235 | 2020-06-05 | 246090 | 2020-06-04 | overheatingpiston crack | 2019-03-05 | 2020-03-14 | 678 | null | null | 12 | Cylinder temprature very high | null | null | Piston and bearings,pump element
2020-06-13 | Cool Comfort Private Limited | West Bengal | D | Za Sea Foods | West Bengal | KCX72 | 3474K350 | 2461384236 | 2020-06-05 | 246138 | 2020-06-05 | pressure gauge malfunctioning | 2020-01-22 | 2020-06-05 | ZH | null | null | 5 | Pressure gauges out, pressure gauges damaged | null | closed | pr gauge 760 to 16 kg/cm2 2nos.
2020-06-21 | Multivista Global Pvt Ltd | null | D | Avathar Chilling Centre | Tamil Nadu | PCX2 | 3106K0010 | 2463244244 | 2020-06-10 | 246324 | null | crankshaft not rotates. | 2019-10-25 | 2019-12-16 | 101 | null | null | 2 | Carbon settled in compressor, suction valve springs 02 nos missing, piston rings wornout | null | closed | Replaced piston ring set 02 nos. and suction valve springs fitted.
2020-06-21 | Cool Comfort Private Limited | West Bengal | D | Mondal Ice & Cold Storage | West Bengal | KCX6 | 3394K1405 | 2460484239 | 2020-06-06 | 246048 | 2020-06-06 | oil lifting and abnormal sound | 2019-10-06 | 2019-10-22 | 1537 | null | null | 1 | Liquid entry-Buisness promotion. | null | closed | Replaced piston4,piston ring set6,gudgeonpin4 bush conrod4
2020-06-21 | Cool Comfort Private Limited | West Bengal | D | Radhanagar Cold Storage | West Bengal | KCX4 | 3384K2224 | 2461464246 | 2020-06-10 | 246146 | 2020-06-17 | oil pressure not buildup | 2019-03-02 | 2020-02-22 | 55 | null | null | 11 | Oil pump outer rotor tang broken and inner rotor bush siezed | null | closed | Oil pump outer rotor tang broken and inner rotor bush siezed
2020-06-21 | Multivista Global Pvt Ltd | null | D | Hatsun Agro Products Ltd | Tamil Nadu | KCX4 | 3384K2185 | 2458424220 | 2020-05-18 | 245842 | 2020-05-18 | oil pressure not buildup | 2019-01-27 | 2020-01-08 | 1460 | null | null | 11 | Pump element broken | null | closed | Replaced pump element
2020-06-21 | Robin Refrigeration Works | Odisha | D | Maa Dhamri Ice Plant | Odisha | KCX4 | 3384K2497 | 2460924240 | 246092 | 246092 | 2020-06-06 | op pressure switch malfunctioning | 2020-02-19 | 2020-06-06 | ZH | null | null | 4 | OP pressure switch not working | null | closed | OP pressure switch
2020-06-21 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX31 | 3434K0105 | 2427884173 | 2020-03-11 | 242788 | 2020-05-14 | upgradation of krms | 2019-06-30 | 2020-05-14 | ZH | null | null | 11 | Power supply adaptor and Hardware for remote monitoring replaced. Required for field trial suggested by D&D. | null | closed | Power supply adaptor and Hardware for remote monitoring replaced. Required for field trial suggested by D&D.
2020-06-21 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX4 | 3384K2286 | 2427724180 | 2020-03-13 | 242772 | 2020-01-30 | upgradation of krms | 2019-06-30 | 2020-01-30 | ZH | null | null | 6 | Power supply adaptor and Hardware for remote monitoring replaced. Required for field trial suggested by D&D. | null | closed | Power supply adaptor and Hardware for remote monitoring replaced. Required for field trial suggested by D&D.
2020-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Lupin Limited | null | KCX72 | 3474K302 | Service email | 2020-07-03 | 246150 | 2020-06-05 | crank case welding leakage | null | 2019-07-23 | PC | null | null | null | Leakage observed at lp discharge line. Welding of the leakage joint done at site. | null | closed | W/O FRR
2020-06-30 | Kalp Marketing | Gujrat | D | Mahakali Ice | Gujrat | KCX4 | 3384K2499 | 2464824255 | 2020-06-16 | 246482 | 2020-06-16 | high oil consumption | 2020-02-22 | 2020-06-05 | 601 | null | null | 1 | Replaced piston ring set and ORV | null | closed | Replaced piston ring and ORV
2020-06-30 | Kalp Marketing | Gujrat | D | Jagdama Ice | Gujrat | KCX4 | 3384K2501 | 2464804250 | 2020-06-16 | 246480 | 2020-06-16 | high oil consumption | 2020-02-22 | 2020-06-04 | 1151 | null | null | 1 | Replaced piston ring set and ORV | null | closed | Replaced piston ring and ORV
2020-06-30 | S M Refrigeraion Pvt Ltd | null | D | Mitra Cold Storage Pvt Ltd | null | KCX3 | 3374K2246 | Service email | 2020-07-03 | 246756 | 2020-06-24 | high oil consumptionorv blockage | null | 2020-03-13 | PC | null | null | null | Oil Carryover problem | null | closed | W/O FRR
2020-06-30 | Trade Links | null | D | Albys Agro Pvt Ltd | Goa | KC72 | 347K989 | 2442844133 | 2020-02-28 | 244284 | 2020-02-27 | kc oil pump assly oil pr not develop | 2019-08-10 | 2019-09-14 | 1125 | null | null | 1 | Kc oil pump low oil pressure | null | closed | Replaced KC oil pump
2020-06-30 | Kalp Marketing | Gujrat | D | Mehsana Ice Cold Storage | Gujrat | KCX2 | 3364K1774 | 2461044233 | 2020-06-04 | 246104 | 2020-06-04 | overheatingcylinder liner gasket broken | 2019-05-08 | 2020-03-04 | 150 | null | null | 3 | Replaced cylinder liner gasket and piston ring set | null | closed | Replaced cylinder liner gasket and piston ring set
2020-06-30 | Trade Links | null | D | Dodla Dairy Ltd | null | KCX6 | 3394K1419 | 2465864258 | 2020-06-22 | 246586 | 2020-06-22 | overheatingdelivery valve leak | 2019-11-11 | 2020-02-13 | 1930 | null | null | 3 | Delivery valve leak | null | closed | Replaced delivery valve,Piston ring , buffer spring
2020-06-30 | S M Refrigeration | null | D | Agrotech Cold Storage | null | KCX4 | 3384K2078 | 2465164253 | 2020-06-17 | 246516 | 2020-06-17 | overheatingdelivery valve leak | 2018-09-17 | 2019-05-30 | 564 | null | null | 12 | Delivery valve leak | null | closed | Replaced delivery valve,piston cylinder liner.
2020-06-30 | Geekay Pneumatic Pvt Ltd | null | D | Pulikkalakath Ice Factory | null | KCX3 | 3374K1987 | 2458344222 | 2020-05-20 | 245834 | 2020-05-20 | overheatingpiston crack | 2018-12-29 | 2019-06-15 | 2260 | null | null | 12 | piston crack | null | closed | Replaced piston, liner ,piston ring
2020-06-30 | S M Refrigeration | null | D | Nadhi Bio Products Pvt Ltd | null | KCX93 | 3485K054 | 2460364228 | 2020-05-31 | 246036 | 2020-05-31 | overheatingpiston crack | 2019-03-20 | 2019-06-13 | 4016 | null | null | 12 | Replced piston due to crack, liner,del valve, piston ring | null | closed | Replced piston due to crack, liner,del valve, piston ring
2020-06-30 | Shree Engineering Services | null | D | Raipur Logitics | null | KCX3 | 3374K2219 | 2460444238 | 2020-06-06 | 246044 | 2020-06-06 | pressure gauge malfunctioning | 2019-12-13 | 2020-05-04 | ZH | null | null | 1 | Pressure gauges not working | null | closed | Replaced pressure gauge76to 16 kg/cm2
2020-06-30 | S M Refrigeraion Pvt Ltd | null | D | Balaji Beverages | Uttar Pradesh | KCX3 | 3374K2231 | Service email | 2020-07-03 | 246290 | 2020-06-08 | shaft seal leakage | null | 2020-02-29 | PC | null | null | null | Shaft Seal leakage | null | closed | W/O FRR
2020-06-30 | Hss Solution Pvt Ltd | null | D | Rajasthan Antibiotics Ltd | Rajastan | KCX42 | 3444K158 | Service email | 2020-07-03 | 246484 | 2020-06-15 | shaft seal leakage | null | 2019-11-07 | PC | null | null | null | Shaft Seal Oring Damaged. | null | closed | W/O FRR
2020-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K2299 | 2468664286 | 2020-07-13 | 246866 | 2020-06-29 | shaft seal leakage | 2020-02-14 | 2020-03-21 | PC | null | null | 1 | Shaft seal leakage | null | closed | W/O FRR
2020-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K2299 | 2266364256 | 2020-06-16 | 246636 | 2020-06-16 | shaft seal leakage | 2020-02-14 | 2020-03-21 | 340 | null | null | 1 | Replaced shaft seal assly | null | closed | Replaced Shaft seal asly
2020-07-20 | Parag Marketing Services | null | D | Jai Hanuman Milk & Milk Products | Ahmed Nagar | KCX3 | 3374K1946 | 2471724279 | 2020-07-09 | 247172 | 2020-07-08 | delivery valve failure | 2018-10-27 | 2019-05-08 | 3804 | null | null | 7 | Delivery valve ring and spring broken,overheating | null | closed | Delivery valve assly
2020-07-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Fine Organic Industries | Thane | KCX3 | 3374K1966 | 2466024262 | 2020-06-25 | 246602 | 2020-06-19 | oil carry over | 2018-11-30 | 2019-09-10 | 7600 | null | null | 10 | Piston ring set & ORV replaced -3nos. | null | closed | Piston ring set & ORV replaced 3nos.
2020-07-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Krishna Industries | Gujrat | KCX4 | 3384K2307 | 2472244289 | 2020-07-13 | 247224 | 2020-07-11 | oil separator flanges replacedwrong name plate fitted | 2019-07-31 | 2019-10-29 | ZH | null | null | 3 | Oil separator flanges replaced-wrong name plate fitted | null | closed | null
2020-07-20 | Trade Links | null | D | Archemedies Laboratories Limited | Telangana | KCX9 | 3404K117 | 2467624267 | 2020-06-27 | 246762 | 2020-06-27 | piston crackoil lifting | 2018-10-28 | 2019-02-04 | 8081 | null | null | 4 | Piston crack at cylinder no.1,5,8,9 | null | closed | Piston 4 nos.,piston ring set
2020-07-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bhakti Ice Factory | Gujrat | KCX4 | 3384K2450 | 2448624163 | 2020-03-07 | 244862 | 2020-03-07 | pressure gauge malfunctioning | 2020-01-06 | 2020-02-27 | 60 | null | null | 1 | HP & LP Prressure gauge error | null | closed | Replaced pressure gauge76to 16 kg/cm2 & 25kg/cm2
2020-07-20 | Trade Links | null | D | Nestle India Ltd | Goa | KCX4 | 3384K2152 | 2471384281 | 2020-07-11 | 247138 | 2020-07-10 | shaft seal leakageoring replaced | 2018-12-21 | 2019-04-17 | 5424 | null | null | 4 | Shaft seal leakage-Oring replaced | null | closed | Shaft seal leakageOring replaced
2020-07-21 | S M Refrigeration | null | D | Anik Milk Products | Uttar Pradesh | KCX4 | 3384K2066 | 2459924242 | 2020-06-08 | 245992 | 2020-06-08 | kcx oil pressure problem | 2018-09-12 | 2019-09-05 | 3796 | null | null | 12 | Replaced oil pump-old type | null | closed | oil pumpold type
2020-07-21 | S M Refrigeration | null | D | Al Takbeer Frozen Foods | Uttar Pradesh | KCX42 | 3444K202 | 2464604252 | 2020-06-16 | 246460 | 2020-06-16 | pressure gauge malfunctioning | 2020-02-21 | 2020-06-15 | ZH | null | null | 4 | Pressure gauge failure | null | closed | Replaced pr gauge 760 to 16 kg/cm2 1no.
2020-07-21 | Trade Links | null | D | Vallabha Milk Products | Telangana | KCX4 | 3384k2205 | 2467544261 | 2020-06-24 | 246754 | 2020-06-24 | pressure gauge malfunctioning | 2019-02-19 | 2019-06-26 | 1997 | null | null | 4 | Pressure gauge failure | null | closed | Replaced pr gauge 760 to 16 kg/cm2 1no.
2020-07-21 | S M Refrigeration | null | D | Balaji Beverages | Uttar Pradesh | KCX3 | 3374K2230 | 2473404306 | 2020-07-18 | 247340 | 2020-07-18 | shaft seal leakage | 2019-12-21 | 2020-02-18 | 202 | null | null | 2 | Shaft seal leakage-deep cut mark on bronze ring | null | closed | Shaft seal assly
2020-07-31 | Cool Comfort Private Limited | West Bengal | D | Shahada Exports | null | KCX51 | 3454K121 | 2470884276 | 2020-07-06 | 247088 | 2020-07-06 | abnormal noise | 2019-05-29 | 2019-06-25 | PC | null | null | 1 | Delivery valve failure | null | closed | Delivery valve kit
2020-07-31 | Kalp Marketing | Gujrat | D | Bholenath Ice & Cold Storage | null | KCX4 | 3384K2098 | 2470344272 | 2020-07-04 | 247034 | 2020-07-04 | high oil consumptionpiston crack | 2018-11-13 | 2019-07-20 | 2280 | null | null | 8 | Piston crack-1no. | null | closed | Piston and orv replaced
2020-07-31 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX31 | 3434K0105 | 2476124323 | 2020-07-27 | 247612 | 2020-07-27 | issue in krms sysytem | 2019-06-30 | 2020-05-14 | 360 | null | null | 12 | Issue in KRMS Sysytem | null | closed | Replaced hardware for remote monitoring
2020-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Rutu Agro Food Cold Storage | null | KCX42 | 3444K210 | 2472704290 | 2020-07-13 | 247270 | 2020-07-13 | retaining plate welding broken | 2020-06-23 | 2020-07-13 | ZH | null | null | 1 | Retaining plate welding joint broken | null | closed | Retaining plate assly
2020-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Real Frozen Foods | null | KCX72 | 3474K300 | 2471764287 | 2020-07-13 | 247176 | 2020-07-13 | shaft seal leakage | 2019-07-01 | 2019-09-16 | 3899 | null | null | 2 | Minor shaft seal leakage , oring found in compressed condition | null | closed | O ring
2020-07-31 | S M Refrigeraion Pvt Ltd | null | D | Balaji Beverages | Uttar Pradesh | KCX3 | 3374K2231 | Service email | 2020-07-03 | 246290 | 2020-06-08 | shaft seal leakage | null | 2020-02-29 | PC | null | null | null | Shaft Seal leakage | null | closed | W/O FRR
2020-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K334 | 2469864274 | 2020-07-04 | 246986 | 2020-07-04 | solenoid valve malfuctioning | 2019-09-27 | 2020-07-04 | ZH | null | null | 9 | Solenoid valve not operate properly | null | closed | Solenoid valve
2020-07-31 | Kirloskar Dmcc | null | E | Natural Ice | Dubai | KCX4 | 3384K2457 | KDMCC/FRR/NATURAL ICE /62020 | 2020-07-21 | 36 | 2020-07-21 | tap bolt broken and deep impression mark on lever. | 2020-01-01 | 2020-03-03 | 100 | null | null | 2 | Tap bolt bbroken and deep impression mark on lever. | null | closed | Replace lever and tap bolt
2020-08-04 | S M Refrigeration | null | D | Tirupati Wood Products | Uttar Pradesh | KC4 | 338K5732 | 2473784328 | 2020-07-30 | 247378 | 2020-07-31 | high oil consumption | 2020-02-03 | 2020-07-31 | 32 | null | null | 6 | Oil carry over due to Cylinder liner , piston , piston rings wornout | null | closed | Replaced Cylinder liner , piston , piston rings wornout
2020-08-04 | S M Refrigeration | null | D | Bhagwan Cold Storage | Uttar Pradesh | KCX6 | 3394K1143 | 2473484296 | 2020-07-14 | 247348 | 2020-07-14 | oil pressure problem | 2018-08-13 | 2019-02-28 | 603 | null | null | 7 | Oil pump element broken | null | closed | Replaced pump element
2020-08-04 | Geekay Pneumatic Pvt Ltd | null | D | Gks Business Associates Pvt Ltd | Kerala | KCX72 | 3474K378 | 2475404316 | 2020-07-23 | 247540 | 2020-07-23 | pressure gauge out | 2020-03-08 | 2020-07-23 | 2 | null | null | 5 | Discharge pressure gauge out | null | closed | Replaced Pressure gauge 16.00Kg/cm2.
2020-08-04 | Trade Links | null | D | Sri Bharati Milk Products | Andhra Pradesh | KCX1 | 3354K124 | 2473864300 | 2020-07-16 | 247386 | 2020-07-16 | solenoid valve leakage | 2019-06-29 | 2020-02-15 | 419 | null | null | 8 | Solenoid valve leakage from bottom manual knob. | null | closed | Replaced solenoid valve assembly
2020-08-22 | S M Refrigeration | null | D | Jitendra Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1501 | 2475024322 | 2020-07-27 | 247502 | 2020-08-11 | abnormal noise | 2020-01-20 | 2020-02-26 | 342 | null | null | 1 | Cut marks on liner and discharge valve assembly due to improper fitment. | null | closed | cylinder liner,piston ring set, discharge valve assly
2020-08-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | International Agro Food | Uttar Pradesh | KC72 | 347K992 | 2466264356 | 2020-08-05 | 246626 | 2019-10-25 | abnormal noise and low oil pressure problem. | 2019-10-25 | 2019-12-31 | 937 | null | null | 2 | Abnormal noise and low oil pressure problem. | null | closed | Replaced Piston.liner,piston ring set,bearings,shaft seal assly, conrod assly HP2
2020-08-22 | Kalp Marketing | Gujrat | D | S S International | Gujrat | KCX72 | 3474K295 | 2479704553 | 2020-08-04 | 247970 | 2020-08-04 | delivery valve leakage | 2019-06-17 | 2019-08-12 | 2705 | null | null | 3 | HP discharge valve observed leak | null | closed | Replaced HP discharge valve leak
2020-08-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bharat Ice Factory | Gujrat | KCX4 | 3384K2475 | 2478304346 | 2020-08-01 | 247830 | 2020-08-01 | hour meter not working | 2020-01-28 | 2020-03-12 | ZH | null | null | 2 | Hour meter not working | null | closed | Replaced hour meter
2020-08-22 | Parag Marketing Services | null | D | Agrani Foods & Agro Processing Pvt Ltd | Sangli | KCX3 | 3374K2067 | 2474224311 | 2020-07-21 | 247422 | 2020-07-21 | knocking / abnormal sound | 2019-03-11 | 2019-05-28 | 1905 | null | null | 2 | Abnormal noise and rubbing of cylinder liner,piston piston ring. | null | closed | Replaced cylinder liner, piston and piston ring set.
2020-08-22 | Kalp Marketing | Gujrat | D | Kedareshwar Ice And Cold Storage | Gujrat | KCX4 | null | 2481004360 | 2020-08-07 | 248100 | 2020-08-07 | knocking soundpiston crack | 2019-07-15 | 2019-08-10 | 3500 | null | null | 1 | Piston crack | null | closed | Replaced piston
2020-08-25 | Parag Marketing Services | null | E | Dce Refrigeration Yak Brewery | Pune / Nepal | KCX4 | null | null | null | null | null | compressor foot crack | null | null | null | null | null | null | Compressor foot crack - photo received for rectification guidelines. Ref mail from YRP to GPV date 9 Aug 20. | null | null | null
2020-08-25 | Kalp Marketing | Gujrat | D | Arabian Foods | Gujrat | KCX72 | 3474K276 | Mail Marwade Atul | 2020-08-21 | 248076 | 2020-08-17 | compressor overheating | 2019-03-29 | 2019-09-04 | 3515 | null | null | 6 | Buffer spring broken in cylinder no.9 | null | closed | Replaced buffer spring..FRR Awaited
2020-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Alpesh Ice Industries | Alibaug | KCX3 | 3374K2113 | 2473184362 | 2020-08-10 | 247318 | 2020-07-14 | oil carry over | 2019-05-21 | 2019-10-19 | 3341 | null | null | 6 | Replaced piston ring set 3 , VLD Orings - 6 & ORV-3 & Filter - 2 | null | closed | Replaced piston ring set 3 , VLD Orings 6 & ORV3 & Filter 2
2020-08-25 | Cool Comfort Private Limited | West Bengal | D | Sahada Exports | West Bengal | KCX72 | 3374K362 | 2483124374 | 2020-08-14 | 248312 | 2020-08-14 | oil lifting | 2020-01-11 | 2020-06-10 | 522 | null | null | 6 | Cylinder no.7 buffer spring broken. 2 Piston ring sets wornout. | null | closed | Replaced Buffer spring1 & Piston ring set 2
2020-08-25 | S M Refrigeration | null | D | Mohan Clod Storage | Bihar | KCX6 | 3394K1524 | 2483904386 | 2020-08-20 | 248390 | 2020-08-20 | overheating & oil lifting | 2020-03-07 | 2020-06-16 | 474 | null | null | 3 | In Piston and liner over clearance and delivery valve leakage. In 2 cylinders ORV Blocked. The failures occurred passing delivery valve assembly. | null | closed | Replaced ORV2,PISTON4,PISTON RING SET6,BEARINGS BE6
2020-08-25 | Multivista Global Pvt Ltd | null | D | Oscar Sea Foods | Tamil Nadu | KCX4 | 3384K2401 | 2471824282 | 2020-07-12 | 247182 | 2020-07-12 | pressure gauge not working | 2019-11-30 | 2020-07-12 | ZH | null | null | 9 | Suction pressure gauge and hour meter not working | null | closed | Replaced Pressure gauge 16.00Kg/cm2.
2020-08-25 | Multivista Global Pvt Ltd | null | D | Sri Elumalai Storage Pvt Ltd | Tamil Nadu | KCX2 | 3364K1968 | 2467404263 | 2020-06-25 | 246740 | 2020-06-24 | pressure gauge not working | 2020-06-08 | 2020-06-24 | ZH | null | null | 1 | In zero hour defect oil pressure gauge not working within 3 hours. | null | closed | Replaced Pressure gauge 16.00Kg/cm2.
2020-08-31 | Trade Links | null | D | Snow Line Ice Industries | Andhra Pradesh | KCX72 | 3474K244 | 2486464398 | 2020-08-26 | 248646 | 2020-08-29 | abnormal noise from coupling | 2018-11-03 | 2019-08-05 | 1700 | null | null | 9 | Disc pack of coupling broken | null | closed | Replaced disc pack
2020-08-31 | Kalp Marketing | Gujrat | D | Arabian Foods | Gujrat | KCX72 | 3474K276 | 2480764376 | 2020-08-17 | 248076 | 2020-08-11 | compressor overheating | 2019-03-29 | 2019-09-04 | 3514 | null | null | 6 | Buffer spring broken in cylinder no.9 | null | closed | Replaced buffer spring
2020-08-31 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX72 | 3474K381 | W/O FRR | null | 248344 | 2020-08-17 | hp cutouts wiring connection wrong | 2020-06-17 | 2020-08-17 | ZH | null | null | 2 | HP cut-outs wiring connection was wrong | null | closed | Wiring corrected
2020-08-31 | S M Refrigeration | null | D | Sugauti Cold Storage | Uttar Pradesh | KC6 | 339K3581 | 2485964391 | 2020-08-25 | 248596 | 2020-08-24 | kc oil pump tang broken | 2019-11-30 | 2020-02-15 | ZH | null | null | 3 | Service guideline not followed as compressor not running since 5+ months,Service team already discussed with concorn service engineer. | null | closed | Replaced gear kit with OP cover
2020-08-31 | Kalp Marketing | Gujrat | D | Gangotri Ice And Cold Storage | Gujrat | KCX3 | 3374K2132 | 2483604377 | 2020-08-17 | 248360 | 2020-08-17 | pressure switch not working | 2019-06-26 | 2020-08-17 | ZH | null | null | 1 | tripping even in ok parameters | null | closed | Replaced OP Pr. switch
2020-08-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K2299 | 2485764408 | 2020-08-30 | 248576 | 2020-08-24 | shaft seal leakage | 2020-02-14 | 2020-03-21 | 847 | null | null | 1 | Shaft seal leakage | null | closed | Bearing cover
2020-09-08 | Kalp Marketing | Gujrat | D | Vilayat Pharma | Gujrat | KCX72 | 3474K230 | 2480364358 | 2020-08-06 | 248036 | 2020-08-06 | delivery valve leakage | 2018-11-30 | 2019-05-03 | 1063 | null | null | 6 | In last visit we have replaced kit delivery valve. Now replaced DV. | null | closed | Replaced delivery valve assly 2
2020-09-08 | Hss Solution Pvt Ltd | null | D | Garima Milk & Foods Products Ltd | Rajastan | KCX4 | 3384K2484 | 2471004394 | 2020-08-25 | 247100 | 2020-08-27 | oil carry over | 2020-02-09 | 2020-05-08 | 638 | null | null | 3 | Found liquid in compressor and cloth bag condition very poor, filters also dirty. Components wornout | null | closed | Replaced Piston, Piston rings , Bush & Gudgeon pins 4 sets.
2020-09-12 | Trade Links | null | D | Total Drugs & Intermidiates Pvt Ltd | Telangana | KCX4 | 3384K2275 | 2488564409 | 2020-08-31 | 248856 | 2020-09-01 | abnormal noisepiston crack | 2019-06-12 | 2019-11-29 | 3563 | null | null | 5 | Piston crack and cylinder siezed | null | closed | Replace, piston, liner,piston ring set, del valve assly
2020-09-12 | Kalp Marketing | Gujrat | D | Vanita Foods | Gujrat | KCX72 | 3474K316 | 2485884395 | 2020-08-25 | 248588 | 2020-08-25 | cylinder overheating | 2019-08-30 | 2020-08-25 | ZH | null | null | 12 | Delivery valve ring and spring replaced -1 no. | null | closed | Delivery valve ring and spring replaced 1 no.
2020-09-12 | Trade Links | null | D | Nekkanti Sea Foods | Andhra Pradesh | KCX6 | 3394K1349 | 2484064383 | 2020-08-19 | 248406 | 2020-08-19 | cylinder overheating | 2019-05-19 | 2019-09-30 | 1326 | null | null | 4 | Cylinder overheated and piston siezed | null | closed | Replaced Piston, liner,buffer spring,piston ring set,del. Valve assly.
2020-09-12 | Kalp Marketing | Gujrat | D | Radhanpur Chilling Center | Gujrat | KCX3 | 3374K2094 | 2491944420 | 2020-09-08 | 249194 | 2020-09-08 | discharge valve malfunctioning | 2019-04-13 | 2019-08-28 | 1156 | null | null | 3 | Del.Valve ring and springs broken,Piston and liner seazed | null | closed | Replaced Piston, liner,buffer spring,piston ring set,del. Valve assly.
2020-09-12 | Kalp Marketing | Gujrat | D | Jai Balaji Cold Storage | Madhya Pradesh | KCX4 | 3384K2186 | 2474664390 | 2020-08-21 | 247466 | 2020-08-21 | kcx oil pressure problemouter rotor tang broken | 2019-01-28 | 2019-09-02 | 92 | null | null | 8 | Replaced KCX oil pump element,ORV,Kit delivery valve. | null | closed | Replaced KCX oil pump element,ORV,Kit delivery valve.
2020-09-12 | Trade Links | null | D | The Krishna DistMilk | Andhra Pradesh | KCX9 | 3404K148 | 2480104382 | 2020-08-19 | 248010 | 2020-08-10 | krms issue | 2019-12-10 | 2020-08-10 | ZH | null | null | 8 | RMS signal transmitting issue | null | closed | Replaced RMS device
2020-09-12 | Trade Links | null | D | DrReddy'S Laboratories | Andhra Pradesh | KCX63 | 3464K076 | 2487284405 | 2020-08-28 | 248728 | 2020-08-28 | oil carry over | 2020-06-01 | 2020-06-30 | 1281 | null | null | 1 | Replaced piston ring set and delivery valve assly-1No. | null | closed | Replaced piston ring set and delivery valve assly1No.
2020-09-12 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K1912 | 2475684317 | 2020-07-23 | 247568 | 2020-07-23 | oil carry over | 2018-09-11 | 2018-09-18 | 6381 | null | null | 1 | ORV blocked | null | closed | Replaced ORV
2020-09-22 | Awaited Details | null | E | M/S Mir Habibul Alam | null | KC6 | 339K3597 | Email | 2020-09-15 | null | 2020-09-15 | compressor crankcase inside rusty | 2020-06-25 | 2020-09-15 | ZH | null | null | 2 | Compressor crankcase inside rusty | null | open | null
2020-09-22 | Awaited Details | null | E | Iran | null | null | null | Email | 2020-09-22 | null | 2020-09-22 | flywheel wobbling | null | null | ZH | null | null | null | null | null | open | null
2020-09-22 | Kalp Marketing | Gujrat | D | Balaji Industries | Gujrat | KCX3 | 3374K2195 | 2492584425 | 2020-09-10 | 249258 | 2020-09-10 | oil carry over | 2019-11-22 | 2020-01-20 | 2365 | null | null | 2 | Cylinder no.3 Piston crack & All 3 Piston ring set close gap high. | null | closed | Replaced Piston1 & Piston ring sets 3
2020-09-22 | Geekay Pneumatic Pvt Ltd | null | D | Maraine Ice Factory | Kerala | KCX4 | 3384K2504 | 2486484400 | 2020-08-26 | 248648 | 2020-08-26 | oil carry over | 2020-02-25 | 2020-06-16 | 580 | null | null | 4 | Oil throw from cylinder no.1,2&4. | null | closed | Replaced Piston ring set 3 , ORV1 & VLD Orings 2
2020-09-22 | Geekay Pneumatic Pvt Ltd | null | D | Jalasree Ice Plant | Kerala | KCX2 | 3364K1910 | 2487544406 | 2020-08-29 | 248754 | 2020-08-29 | oil carry over | 2020-01-12 | 2020-01-28 | 1050 | null | null | 1 | One piston hair line crack . | null | closed | Replaced Piston1, Piston ring set1, ORV1
2020-09-22 | Cool Comfort Private Limited | West Bengal | D | Shree Mahamaya Agro Industries Pvt Ltd | West Bengal | KCX4 | 3384K2460 | 2492464424 | 2020-09-10 | 249246 | 2020-09-10 | oil carry over | 2020-01-15 | 2020-08-07 | 50 | null | null | 7 | Cylinder no. 4 Piston ring set wornout & ORV Malfunctioning. | null | closed | Replaced Piston ring set1 & ORV1
2020-09-22 | Cool Comfort Private Limited | West Bengal | D | Gourhari Multipurpose Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K2459 | 2491384421 | 2020-09-09 | 249138 | 2020-09-13 | oil carry over | 2020-01-15 | 2020-02-21 | 1625 | null | null | 1 | Cylinder no.3 Piston wornout and all 4 cylinders piston rings wornout & close gap high. | null | closed | Replaced Piston1 & Piston ring sets 4
2020-09-22 | Kalp Marketing | Gujrat | D | Mahakali Ice Naroda | Gujrat | KCX4 | 3384K2499 | 2492404428 | 2020-09-11 | 249240 | 2020-09-11 | oil pressure switch problem | 2020-02-22 | 2020-06-05 | 1155 | null | null | 4 | Tripping not done. | null | closed | Replaced Pressure swich MP55A
2020-09-22 | S M Refrigeration | null | D | Jpls Dairy Pvt Ltd | Uttar Pradesh | KCX1 | 3354K137 | 2481904431 | 2020-09-14 | 248190 | 2020-09-14 | suction pressure gauge malfunctioning | 2019-09-30 | 2020-09-14 | ZH | null | null | 12 | Suction Pressure gauge needle not free - within 3 hrs. | null | closed | Replaced Suction Pressure gauge
2020-09-26 | Cool Comfort Private Limited | West Bengal | D | Sadaf Sea Foods | West Bengal | KCX72 | 3474K348 | 2496384452 | 2020-09-21 | 249638 | 2020-09-21 | oil carry over | 2019-12-28 | 2020-06-10 | 852 | null | null | 6 | Piston,piston ring set wornout,visible marks on cylinder liner,scratch marks on bearing bush. | null | closed | Replaced piston,piston ring set,cylinder liner,bearing bush
2020-09-30 | Kirloskar Pneumatic Co Ltd | New Delhi | D | India Pesticide Ltd | Uttar Pradesh | KCX12 | 3415K005 | Service email | 2020-10-02 | 249446 | 2020-09-15 | crankcase welding leakage | 2019-03-25 | 2019-07-06 | 5872 | null | null | 4 | Crankcase welding leakage | null | closed | null
2020-09-30 | Kalp Marketing | Gujrat | D | Arabian Foods | Gujrat | KCX51 | 3454K118 | 2495444444 | 2020-09-18 | 249544 | 2020-09-18 | delivery valve leakage | 2019-03-29 | 2019-08-28 | 890 | null | null | 5 | Delivery valve leak due to dust particles found in refrigerant. | null | closed | Kit delivery valve 3 nos.
2020-09-30 | Kalp Marketing | Gujrat | D | Natural Foods | Gujrat | KCX51 | 3454K119 | 2495464445 | 2020-09-18 | 249546 | 2020-09-18 | delivery valve leakage | 2019-03-29 | 2019-09-02 | 865 | null | null | 6 | Delivery valve leak due to dust particles found in refrigerant. | null | closed | Kit delivery valve 3 nos.
2020-09-30 | Geekay Pneumatic Pvt Ltd | null | D | Premier Marine Foods | Kerala | KCX31 | 3434K012 | 2492864437 | 2020-09-15 | 249286 | 2020-09-15 | high oil carryover | 2019-12-20 | 2020-01-14 | 1401 | null | null | 1 | Replaced piston ring sets-3,VLD O rings-4 | null | closed | piston ring sets3,VLD O rings4
2020-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K334 | Service email | 2020-10-02 | null | null | krms controller panel mounting hole shift. | 2019-09-27 | 2020-07-04 | ZH | null | null | 9 | KRMS Controller Panel mounting hole shift. | null | closed | KRMS Controller Panel
2020-09-30 | Trade Links | null | D | Pmc Ym Pharama Pvt Ltd | Telangana | KCX84 | 3305K012 | 2495404455 | 2020-09-23 | 249540 | 2020-09-23 | piston crack high oil consumption | 2020-06-23 | null | null | null | null | 3 | Replaced Piston-2,Cylinder liner-1,Piston ring set-12 | null | closed | Piston2,Cylinder liner1,Piston ring set12
2020-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mahrook Seafoods PvtLtd Raigad | Maharashtra | KCX72 | 3474K376 | Service email | 2020-10-02 | 249898 | 2020-09-29 | shaft seal leakage | 2020-06-09 | 2020-09-17 | 30 | null | null | 3 | Oil leakage from bearing housing drive and seal leakage. | null | closed | Replaced shaft seal Oring
2020-09-30 | Parag Marketing Services | null | D | D J Exports Pvt Ltd | Nashik | PCX2 | 3106K0003 | Service email | 2020-10-02 | 249206 | 2020-09-13 | shaft seal leakage | 2019-09-30 | 2020-09-13 | ZH | null | null | 12 | Within 1 hr shaft seal leakage. | null | closed | Replaced shaft seal Oring
2020-09-30 | Parag Marketing Services | null | D | D J Exports Pvt Ltd | Nashik | PCX2 | 3106K0005 | Service email | 2020-10-02 | 249208 | 2020-09-13 | shaft seal leakage | 2019-09-30 | 2020-09-13 | ZH | null | null | 12 | Within 2 hrs shaft seal leakage. | null | closed | Replaced shaft seal Oring
2020-10-03 | Trade Links | null | D | The Krishna DistMilk | Andhra Pradesh | KCX9 | 3404K147 | 2496284450 | 2020-09-21 | 249628 | 2020-09-21 | krms issue | 2019-12-10 | 2020-08-10 | ZH | null | null | 8 | RMS device not working | null | closed | Replaced RMS device
2020-10-03 | Cool Comfort Private Limited | West Bengal | D | Shimpo ExportsPvt Ltd | West Bengal | KCX72 | 3474K338 | 2489264411 | 2020-09-02 | 248926 | 2020-09-04 | oil leakage from solenoid valve | 2019-12-21 | 2020-06-13 | 943 | null | null | 6 | Oil leakage from solenoid valve manual knob. | null | closed | Replaced sol. Valve
2020-10-03 | Kalp Marketing | Gujrat | D | Asiatec Traders | Madhya Pradesh | KCX3 | 3374K2288 | 2477984340 | 2020-07-31 | 247798 | 2020-07-31 | pressure transducer wrong supply | 2020-01-31 | 2020-07-08 | ZH10 | null | null | 6 | Pressure transducer wrong supply | null | closed | Replaced Pressure transducer
2020-10-11 | Trade Links | null | D | Pmc Ym Pharama Pvt Ltd | Telangana | KCX84 | 3305K012 | 2499704477 | 2020-10-01 | 249970 | 2020-10-01 | abnormal noise | 2020-06-23 | 2020-09-09 | 356 | null | null | 3 | Field issue, high intermidiate pressure,Piston siezed, intermidiate crank pin worn out. | null | closed | Replaced piston, piston rings, cylinder liner,C.shaft assly.
2020-10-11 | Parag Marketing Services | null | D | Naik Sea Foods Pvt Ltd | Ratnagiri | KCX42 | 3444K213 | 2493144433 | 2020-09-15 | 249314 | 2020-09-12 | delivery valve leakage | 2020-07-13 | 2020-09-12 | ZH | null | null | 2 | Delivery valve leak and found marking on rig spring kit | null | closed | Delivery valve assly
2020-10-11 | Geekay Pneumatic Pvt Ltd | null | D | Hindustan Organic Chemicals Limited | Kerala | KCX4 | 384K2444 | 2495564465 | 2020-09-28 | 249556 | 2020-09-28 | high oil carryover | 2019-12-31 | 2020-07-13 | 250 | null | null | 7 | Piston ring set uneven wornout | null | closed | Piston ring set
2020-10-11 | Parag Marketing Services | null | D | D J Exports Pvt Ltd | Nashik | PCX2 | 3106K0008 | 2492104432 | 2020-09-15 | 249210 | 2020-09-13 | hour meter not working | 2019-09-30 | 2020-09-13 | ZH | null | null | 12 | Hour meter not working | null | closed | Hour meter
2020-10-11 | Kirloskar Pneumatic Co Ltd | New Delhi | D | International Agro Food | Uttar Pradesh | KC72 | 347K992 | 2499504471 | 2020-10-01 | 249950 | 2020-09-30 | kclow oil pressure problem | 2019-10-25 | 2019-12-31 | 985 | null | null | 2 | Low oil pressure problem, replaced oil pump | null | closed | KC oil pump
2020-10-11 | Trade Links | null | D | Sri Ram Krishna Polymer | Andhra Pradesh | KCX3 | 3374K2233 | 2498144476 | 2020-10-01 | 249814 | 2020-10-01 | oil liftingpiston crack | 2019-12-22 | 2020-03-21 | 3734 | null | null | 3 | Piston crack, piston rings worn out | null | closed | Replaced piston and piston rings
2020-10-11 | Parag Marketing Services | null | D | Kolhapur Zila Sahakari Dudh Utpadak Sangh | Kolhapur | KCX6 | 3394K1307 | 2498464469 | 2020-09-26 | 249846 | 2020-09-28 | op pressure switch malfunctioning | 2019-04-10 | 2020-09-28 | ZH | null | null | 17 | OP pressure switch not working | null | closed | OP pressure switch
2020-10-11 | Trade Links | null | D | Avr Organics Pvt Ltd | Telangana | KCX6 | 3394K1512 | 2498664473 | 2020-10-01 | 249866 | 2020-09-30 | pressure gauge error | 2020-02-19 | 2020-09-30 | ZH | null | null | 7 | Error in discharge pressure gauge -0.50 kg/cm2 | null | closed | Pressure gauge
2020-10-11 | Trade Links | null | D | Nestle India Ltd | Goa | KCX4 | 3384K2152 | 2484264414 | 2020-09-03 | 248426 | 2020-08-27 | shaft seal leakage | 2018-12-21 | 2019-04-17 | 6533 | null | null | 4 | Shaft seal face scoring, replaced shaft seal assly | null | closed | Shaft seal assly
2020-10-23 | Trade Links | null | D | Aov Agro Foods Pvt Ltd | Haryana | KCX42 | 3444K203 | 2499124474 | 2020-10-01 | 249912 | 2020-09-30 | delivery valve leakage | 2020-02-28 | 2020-09-30 | ZH | null | null | 7 | Cylinder no.3 delivery valve leakage and defective suction pressure gauge. | null | closed | Replaced delivery valve kit and pressure gauge.
2020-10-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K068 | 2496004488 | 2020-10-06 | 249600 | 2020-10-06 | flywheel keyway taper | 2019-12-10 | 2020-10-06 | ZH | null | null | 10 | 0.1mm gap below key & no gap above key. Same flywheel fitted to other cmpressor and found same problem. Other ok compressor flywheel fitted to this compressor found ok. Various trial taken but problem not resolved. | null | closed | Replaced flywheel
2020-10-23 | S M Refrigeration | null | D | Tirupati Wood Products | Uttar Pradesh | KCX4 | 338K5732 | 2498364486 | 2020-10-06 | 249836 | 2020-10-14 | high oil carryover | 2020-02-03 | 2020-07-31 | 845 | null | null | 5 | Within 28 hrs oil consumption is 1100ml within rage. Still some parts replaced no oil consumption rate is 6ml/cyl. | null | closed | Replaced VLD Piston2, Orings 4,ORV4 & VLD Hsg2
2020-10-23 | S M Refrigeration | null | D | Agricom Foods Pvt Ltd | Uttar Pradesh | KCX6 | 3394K1285 | 2493964451 | 2020-09-21 | 249396 | 2020-09-21 | high oil carryover | 2019-02-19 | 2019-09-14 | 422 | null | null | 7 | ORV out of order | null | closed | Replaced ORV1
2020-10-23 | Kalp Marketing | Gujrat | D | Amar Food Products | Gujrat | KCX3 | 3374K2339 | 2497784462 | 2020-09-25 | 249778 | 2020-09-25 | high oil carryover | 2020-06-15 | 2020-08-17 | 251 | null | null | 2 | Direct cylinder piston broken from centre (Piston crack)and ORV block. | null | closed | Replaced Piston1 ORV2
2020-10-23 | Trade Links | null | D | Sai Samarth Ice Plants | Goa | KCX4 | 3384K2404 | 2424444237 | 2020-06-06 | 242444 | 2020-01-30 | knocking / abnormal sound | null | null | null | null | null | 1 | Cylinder liner, Piston , Piston rings abnormaly wornout. | null | closed | Replaced Cylinder liner1, Piston1 , Piston rings 2, Gudgeon pin1& Bearings BE
2020-10-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Transpek Silox Inductries Pvt Ltd | Gujrat | KCX4 | 3384K2542 | 2499524480 | 2020-10-02 | 249952 | 2020-10-01 | low oil pressure | 2020-07-14 | 2020-09-25 | 105 | null | null | 2 | Oil pump element gear tang broken. | null | closed | Replaced pump element mod
2020-10-23 | Kalp Marketing | Gujrat | D | Natural Foods | Gujrat | KCX51 | 3454K119 | 2504024495 | 2020-10-13 | 250402 | 2020-10-13 | oil pressure not buildup | 2019-03-29 | 2019-09-02 | 865 | null | null | 6 | Due to electrical failure pump element broken and solenoid valve malfunctioning | null | closed | Replaced sol.valve and pump element.
2020-10-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shuddham Milk Products | Madhya Pradesh | KCX2 | 3364K1740 | 2504664498 | 2020-10-14 | 250466 | 2020-10-14 | piston crack | 2019-02-27 | 2019-04-15 | 2928 | null | null | 2 | Piston crack,replaced piston and ORV-1No. | null | closed | Replaced piston and ORV1No.
2020-10-31 | Kirloskar Pneumatic Co Ltd | New Delhi | D | India Pesticide Ltd | Uttar Pradesh | KCX12 | 3415K005 | Service email | 2020-11-01 | 249994 | 2020-10-01 | c.case weld leakage | 2019-03-25 | 2019-07-06 | 5872 | null | null | 4 | Crankcase welding leakage | null | open | null
2020-10-31 | S M Refrigeration | null | D | Pandit Shiv Shankar Lal Preservation | Uttar Pradesh | KC4 | 338K5713 | Service email | 2020-11-01 | 250990 | 2020-10-29 | shaft seal leakage | 2019-10-26 | 2020-02-04 | 628 | null | null | 4 | Shaft seal leak | null | closed | O ring
2020-11-09 | Hss Solution Pvt Ltd | null | D | United Breweries Ltd | Rajastan | KCX9 | 3404K153 | 2502024534 | 2020-11-06 | 250202 | 2020-11-06 | porosity in coupling piece | 2020-01-18 | 2020-11-06 | 0 | Metaflex | beverage / breweries | 11 | Replaced Coupling piece | null | closed | Replaced coupling piece
2020-11-09 | S M Refrigeration | null | D | Kripa Shankar Devendra Kumar CS | Uttar Pradesh | KCX6 | 3394K1435 | 2500124482 | 2020-10-05 | 250012 | 2020-10-05 | low oil pressure | 2019-11-26 | 2020-02-24 | 1788 | M/S LDK | cold storage | 3 | oil pressure not devoloped above 1.5kg/cm2, replaced pump element | null | closed | Replaced OP element
2020-11-09 | Shree Engineering Services | null | D | Manvi Cold Storage | Chhattisgarh | KCX4 | 3384K2422 | 2502284512 | 2020-10-23 | 250228 | 2020-10-26 | oil carry over | 2020-02-07 | 2020-05-31 | 693 | Inhouse | cold storage | 3 | Piston no 03 observed splattering lots of oil outside. | null | closed | Replaced piston ring sets.
2020-11-09 | Cool Comfort Private Limited | West Bengal | D | India Dairy Products Ltd | West Bengal | KCX4 | 3384K2546 | 2498604466 | 2020-09-28 | 249860 | 2020-09-30 | kcx oil pump tang broken | 2020-07-19 | 2020-09-23 | 46 | M/S LDK | dairy / ice cream | 2 | KCX oil pump tang broken | null | closed | Replaced pump element
2020-11-09 | Trade Links | null | D | Krishna District Milk Products | Andhra Pradesh | KCX9 | 3404K147 | 250522 | 2020-10-20 | 250522 | 2020-10-20 | krms issue | 2019-12-10 | 2020-08-10 | 560 | Cloud Q | dairy / ice cream | 8 | RMS device not working | null | closed | Replaced RMS device
2020-11-09 | S M Refrigeration | null | D | The Ballbgarh Cooperative Milk Producers Union Ltd | Faridabad,Haryana | KCX4 | 3384K2570 | 2508604515 | 2020-10-27 | 250860 | 2020-10-27 | pressure gauge defective | 2020-08-30 | 2020-10-27 | 4 | M/S Walchandnagar industries | dairy / ice cream | 2 | Pressure gauge found defective at time of commissioning | null | closed | Replaced Pressure gauge
2020-11-09 | Parag Marketing Services | null | D | Freshtrop Fruits Ltd | Nashik | KCX51 | 3454K111 | 2491444418 | 2020-09-07 | 249144 | 2020-09-07 | solenoid valve leakageleak from manual knob | 2019-03-08 | 2019-03-30 | 3536 | M/S Rotex | food processing | 1 | Leakage from manual knob | null | closed | Replaced sol. Valve assly
2020-11-09 | Geekay Pneumatic Pvt Ltd | null | D | Shaw Ice Factory | Kerala | KCX4 | 3384K2512 | 2505384501 | 2020-10-16 | 250538 | 2020-10-16 | oil carry over | 2020-03-13 | 2020-09-05 | 623 | Inhouse | ice plant | 6 | Replace piston ring set-1no. | null | closed | Replaced piston ring set
2020-11-09 | Trade Links | null | D | Sri Venkateshwar Ice Factory | Andhra Pradesh | KCX6 | 3394K1510 | 2494084435 | 2020-09-15 | 249408 | 2020-09-15 | oil carry over | 2020-02-03 | 2020-03-09 | 2950 | Inhouse | ice plant | 6 | Piston and piston rings worn out | null | closed | Replaced piston and piston ring sets
2020-11-09 | Parag Marketing Services | null | D | Harbour Ice And Cold Storage | Ratnagiri | KCX4 | 3384K2269 | 2506664513 | 2020-10-26 | 250666 | 2020-10-24 | oil carryover piston crack | 2019-05-31 | 2019-11-23 | 2281 | Inhouse | ice plant | 6 | Piston crack-2 nos , cylinder liner step-1 , and piston ring set close gap increased up to 2.7,2.3,1.05mm-3nos. | null | closed | Replaced piston ,liner, piston ring set.
2020-11-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Royal Ice Factory | Palghar | KCX3 | 3374K2311 | 2497984467 | 2020-09-28 | 249798 | 2020-09-28 | oil consumptionpiston crack | 2020-02-28 | 2020-07-08 | 10 | Inhouse | ice plant | 4 | Piston crack and piston ring set worn out | null | closed | Replaced piston and piston rings
2020-11-09 | Gargi Engineering Enterprices Pvt Ltd | null | D | Krishna Industries | Gujrat | KCX4 | 3384K2307 | 2487784413 | 2020-09-03 | 248778 | 2020-08-29 | overheatingdelivery valve leak | 2019-07-31 | 2019-10-29 | 1979 | Inhouse | ice plant | 3 | Delivery valve leakage and buffer spring length shortened | null | closed | Replace delivery valve assly
2020-11-09 | Trade Links | null | D | Sri Ragvendra EntPvt | Andhra Pradesh | KCX4 | 3384K2298 | 250618 | 2020-10-20 | 250618 | 2020-10-19 | piston crack | 2019-07-20 | 2019-10-12 | 7052 | M/S Paramount pistons | ice plant | 3 | Piston crack and piston rings worn out | null | closed | Piston1,Piston ring set1
2020-11-09 | Geekay Pneumatic Pvt Ltd | null | D | Ocean Wealth Export | Kerala | KCX72 | 3474K312 | 2505984511 | 2020-10-23 | 250598 | 2020-10-19 | delivery valve leakage | 2019-08-26 | 2020-08-20 | 296 | Inhouse | meat/fish process | 12 | Replaced delivery valve assly due to del.stroke limitor lug wornout | null | closed | Delivery valve asly
2020-11-09 | Trade Links | null | D | Dwarka Sea Foods | Andhra Pradesh | KCX4 | 3384K2500 | 2505884508 | 2020-10-20 | 250588 | 2020-10-20 | solenoid valve malfuctioning | 2020-02-21 | 2020-10-20 | 0 | M/S Rotex | meat/fish process | 8 | Replaced solenoid valve assly due to teflon swellout | null | closed | Solenoid valve
2020-11-09 | Parag Marketing Services | null | D | Godavari Drugs Ltd | null | KCX3 | 3374K2325 | 2505244503 | 2020-10-17 | 250524 | 2020-10-17 | tap bolt broken loading unloading problem | 2020-05-29 | 2020-09-17 | 369 | M/S Uttam Engg | chemical / pharma | 4 | Tap bolt broken,piston ring broken, curtain spring replaced | null | closed | Replaced tap bolt,piston ring set, curtain spring
2020-11-12 | Model Pneumatic Co | Punjab | D | Anil Cold Storage | Punjab | KCX4 | 3384K2445 | 2492644528 | 2020-11-03 | 249264 | 2020-09-10 | hour meter not working | 2020-01-04 | 2020-09-10 | 4 | null | cold storage | 8 | Hour meter not working | null | closed | Replaced hour meter
2020-11-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aries Color Chem Pvt Ltd | Gujrat | KCX9 | 3404K157 | 2510744531 | 2020-11-05 | 251074 | 2020-11-05 | delivery valve leakage | 2020-10-13 | 2020-10-23 | 1 | Inhouse | ice plant | 1 | Valve ring shifted from it's location & delivery valve leak | null | closed | Replaced del valve assly
2020-11-23 | Kalp Marketing | Gujrat | D | Shri Gayatri Krupa Ice & Cs | Veraval, Gujarat | KCX4 | 3384K2552 | 2508944520 | 2020-10-29 | 250894 | 2020-10-29 | high oil consumption | 2020-08-02 | 2020-09-24 | 620 | Inhouse | ice plant | 1 | Replaced piston ring set-2 and ORV-4nos. | null | closed | Replaced ORV4 & Piston ring set2
2020-11-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K332 | 2504684535 | 2020-11-06 | 250468 | 2020-10-16 | krms controller panel is malfunctioning | 2019-09-17 | 2020-10-16 | 5 | Carel | ice plant | 13 | KRMS Controller Panel malfunctioning | null | closed | Replaced KRMS Control panel
2020-11-23 | Kalp Marketing | Gujrat | D | Shree Ganesh Ice & Cs | Gujrat | KCX4 | 3384K2517 | 2500864487 | 2020-10-06 | 250086 | 2020-10-06 | overheatingdelivery ring broken | 2020-05-30 | 2020-08-08 | 805 | Inhouse | ice plant | 3 | Replaced del.valve ring, bearing,piston ring set,ORV,kit del.valve | null | closed | Del.valve ring, bearing,piston ring set,ORV,kit del.valve for analysis
2020-11-23 | Geekay Pneumatic Pvt Ltd | null | D | Abn Exports | Kerala | KCX42 | 3444K134 | 2513844542 | 2020-11-15 | 251384 | 2020-11-15 | high oil consumption | 2018-11-14 | 2019-12-09 | 538 | Inhouse | meat/fish process | 13 | Replaced Piston ring sets -5Nos. | null | closed | Replaced Piston ring sets 5Nos.
2020-11-23 | Kalp Marketing | Gujrat | D | Jagdamaba Polymers | Gujrat | KCX4 | 3384K2521 | 2515504541 | 2020-11-13 | 251550 | 2020-11-13 | shaft seal leakage | 2020-03-14 | 2020-11-11 | 15 | Inhouse | chemical / pharma | 8 | Replaced Kit shaft seal and bearing cover | null | closed | Replaced Kit shaft seal and bearing cover
2020-11-30 | Trade Links | null | D | Tirumala Milk Products Ltd | Andhra Pradesh | KCX6 | 3394K1520 | 2507204519 | 2020-10-28 | 250720 | 2020-10-28 | pressure gauge error | 2020-02-28 | 2020-10-28 | 1 | Walchandnagar Inductries | cold storage | 8 | Replaced suction pressure gauge 16kg/cm2. | null | closed | Replaced suction pressure gauge 16kg/cm2.
2020-11-30 | Cool Comfort Private Limited | West Bengal | D | India Dairy Products Ltd | West Bengal | KCX4 | 3384K2546 | 2517464559 | 2020-11-30 | 251746 | 2020-11-30 | high oil consumption & abnormal sound | 2020-07-19 | 2020-09-23 | 776 | null | dairy / ice cream | 2 | Oil lifting in cylinder no. 1,3&4 | null | closed | Replaced Cylinder liner1, Piston1 , Piston rings 2, Piston 1
2020-11-30 | Kalp Marketing | Gujrat | D | Shri Gayatri Krupa Ice & Cs | Veraval, Gujarat | KCX4 | 3384K2552 | 2503784494 | 2020-10-13 | 250378 | 2020-10-13 | high oil consumption | 2020-08-02 | 2020-09-24 | 339 | null | ice plant | 1 | 3 nos ORV found leakage | null | closed | 3 nos ORV found leakage
2020-11-30 | Cool Comfort Private Limited | West Bengal | D | Anjana Ice Factory | West Bengal | KCX3 | 3374K2076 | 2508764516 | 2020-10-27 | 250876 | 2020-10-27 | oil pressure not buildup | 2019-03-24 | 2020-08-05 | 1020 | null | ice plant | 17 | Oil colour black , liner & Piston ring set wornout , Oil pump tang broken. | null | closed | Replaced Liner , Piston ring set and KCX Oil pump assembly.
2020-11-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Yogiraj Cold Storage | Gujrat | KCX3 | 3374K2203 | null | null | 251816 | 2020-11-24 | shaft seal leakage | 2019-11-27 | 2020-03-19 | 2511 | null | ice plant | 4 | Shaft seal Orings were loose and exponded | null | closed | Replaced Orings
2020-11-30 | Cool Comfort Private Limited | West Bengal | D | Sadaf Sea Foods | West Bengal | KCX72 | 3474K348 | 2517804560 | 2020-11-30 | 251780 | 2020-11-30 | abnormal noise | 2019-12-28 | 2020-06-10 | 1111 | null | meat/fish process | 6 | Cylinder no. 1,5&7 liner wornout | null | closed | Replaced Piston , Connecting rod , Cylinder liner , Piston ring sets etc.
2020-11-30 | Cool Comfort Private Limited | West Bengal | D | Basu International | West Bengal | KCX72 | 3474K389 | 2516084550 | 2020-11-23 | 251608 | 2020-11-23 | high oil consumption | 2020-07-27 | 2020-09-03 | 215 | null | meat/fish process | 2 | Cylinder no.3 has excessive oil throw. | null | closed | Replaced Piston ring set and Breather assembly
2020-11-30 | Trade Links | null | D | Conalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K015 | 2509004537 | 2020-11-11 | 250900 | 2020-11-10 | delivery valve leakage | 2020-08-16 | 2020-11-10 | 3 | Inhouse | chemical / pharma | 3 | Cylinder no.4 (HP) found delivery valve backleaking. | null | closed | Replaced delivery valve kit
2020-12-21 | null | null | E | Kirloskar South East Co Ltd | null | null | null | Mail | 2020-12-21 | null | 2020-12-21 | pressure not develop | 2020-10-07 | null | Spares | LDK | null | null | Oil pressure not develop | null | closed | null
2020-12-21 | Parag Marketing Services | null | D | Vishaka Agri Cold Storage | Nashik | KCX3 | 3374K2054 | 2502264505 | 2020-10-19 | 250226 | 2020-10-19 | shaft seal leakage | 2019-02-27 | 2019-07-18 | 6 | Supplier | cold storage | 5 | Replaced shaft seal assly | null | closed | Shaft seal assly
2020-12-21 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Amar Dairy | Buldhana | KCX2 | 3364K1998 | 2502464530 | 2020-11-04 | 250246 | 2020-10-16 | kcx oil pump tang broken | 2020-08-26 | 2020-10-16 | 2 | LDK | dairy / ice cream | 2 | Replaced oil pump element | null | closed | Replaced pump element
2020-12-21 | S M Refrigeraion Pvt Ltd | null | D | The Ballbgarh Cooperative Milk Producers Union Ltd | Faridabad,Haryana | KCX4 | 3384K2570 | 2522024572 | 2020-12-04 | 252202 | 2020-12-04 | oil carry over | 2020-08-30 | 2020-10-27 | 859 | Inhouse | dairy / ice cream | 2 | Replaced piston ring set | null | closed | Replaced piston ring set
2020-12-21 | Kirloskar Pneumatic Co Ltd | Lucknow | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K388 | 2513464567 | 2020-12-02 | 251346 | 2020-12-18 | abnormal noise | 2020-07-12 | 2020-12-18 | 35 | Site issue | meat/fish process | 5 | Replaced cylinder liner , piston,del valve assly, buffer spring, | null | closed | Replaced cylinder liner , piston,del valve assly, buffer spring,
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mahrook Seafoods PvtLtd Raigad | Maharashtra | KCX72 | 3474K376 | 2520764563 | 2020-12-01 | 252076 | 2020-11-30 | abnormal noisedelivery valve leak | 2020-07-09 | 2020-09-17 | 427 | Inhouse | meat/fish process | 2 | Replaced delivery and suction valve ring spring | null | closed | Replaced delivery and suction valve ring spring
2020-12-21 | Cool Comfort Private Limited | West Bengal | D | Basu International | West Bengal | KCX72 | 3474K389 | 2524204583 | 2020-12-09 | 252420 | 2020-12-10 | delivery valve leakage | 2020-07-27 | 2020-09-03 | 306 | Inhouse | meat/fish process | 2 | Replaced piston , pston ring set,Gudgeon pin | null | closed | Replaced piston , pston ring set,Gudgeon pin
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Chand International | Thane | PC2 | 331K3045 | 2475564320 | 2020-07-26 | 247556 | 2020-07-26 | high oil consumption | 2019-06-23 | 2019-08-29 | 2141 | Inhouse | meat/fish process | 2 | Replaced piston ring set 2 nos. | null | closed | Piston ring set2
2020-12-21 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX72 | 3474K381 | 2517824577 | 2020-12-07 | 251782 | 2020-12-17 | oil carry over | 2020-06-17 | 2020-08-21 | 1003 | System issue | meat/fish process | 2 | Replaced cylinder liner & piston ring set | null | closed | Replaced cylinder liner & piston ring set
2020-12-21 | Parag Marketing Services | null | D | S S Agro Foods Bhawarapur | Pune | KCX51 | 3454K139 | 2519024553 | 2020-11-26 | 251902 | 2020-11-26 | knocking soundpiston crack | 2019-11-29 | 2020-07-17 | 1065 | Inhouse | food processing | 8 | Replaced piston , cylinder liner, del valve assly.piston ring set, | null | closed | Replaced piston , cylinder liner, del valve assly.piston ring set,
2020-12-21 | Parag Marketing Services | null | D | Royal Food Stuff Pvt Ltd | Satara | KCX72 | 3474K411 | 2523544581 | 2020-12-08 | 252354 | 2020-12-08 | stop valve problemwelding crack | 2020-10-20 | 2020-12-08 | 0 | Supplier | food processing | 2 | Replaced stop valve TAL100 | null | closed | Replaced stop valve TAL100
2020-12-21 | Geekay Pneumatic Pvt Ltd | null | D | Marain Ice Factory | Kerala | KCX4 | 3384K2504 | 2518644554 | 2020-11-27 | 251864 | 2020-11-27 | high oil carryover | 2020-02-25 | 2020-06-16 | 2852 | Inhouse | ice plant | 4 | Repalced piston ring sets | null | closed | Replaced piston ring set
2020-12-21 | Cool Comfort Private Limited | West Bengal | D | Anjana Ice Factory | West Bengal | KCX3 | 3374K2076 | 2524724587 | 2020-12-10 | 252472 | 2020-12-10 | oil carry over | 2019-03-24 | 2020-08-05 | 1037 | Inhouse | ice plant | 5 | Replaced bearings,piston piston ring sets. | null | closed | Replaced bearings,piston piston ring sets.
2020-12-21 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX6 | 3394K1518 | 2524664589 | 2020-12-12 | 252466 | 2020-12-11 | oil carry over | 2020-02-29 | 2020-07-13 | 62 | Inhouse | ice plant | 5 | Replaced ORV,VLD oring | null | closed | Replaced ORV,VLD oring
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Uttam Machimar V S S Ltd | Thane | KCX3 | 3374K2301 | 2509724526 | 2020-11-03 | 250972 | 2020-10-29 | oil carry over | 2020-02-18 | 2020-07-31 | 1565 | Inhouse | ice plant | 5 | Replaced piston ring sets and VLD Orings | null | closed | Replaced piston ring sets and VLD Orings
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Neotrend Chemical Pvt Ltd | Thane | KCX3 | 3374K2390 | 2519884562 | 2020-12-01 | 251988 | 2020-11-28 | oil carryover piston crack | 2020-09-23 | 2020-10-17 | 750 | Inhouse | ice plant | 1 | Replaced piston and pston ring set-2nos | null | closed | Replaced piston2 and piston ring set2
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sarita Ice Factory | Thane | KCX2 | 3384K2030 | 2519264561 | 2020-12-01 | 251926 | 2020-11-27 | oil consumptionpiston crack | 2020-10-23 | 2020-10-30 | 486 | Inhouse | ice plant | 1 | Replaced piston and pston ring set-1no. | null | closed | Replaced piston and pston ring set1no.
2020-12-21 | Kalp Marketing | Gujrat | D | Shradha Ice And Cold Storage | Jafrabad, Gujrat | KCX4 | 3384K2540 | 2521544573 | 2020-12-05 | 252154 | 2020-12-12 | shaft seal leakage | 2020-07-13 | 2020-09-01 | 1558 | Inhouse | ice plant | 2 | Replaced shaft seal assly due to leakage | null | closed | Replaced Shaft seal assly
2020-12-21 | Kalp Marketing | Gujrat | D | Jagdamaba Polymers | Gujrat | KCX4 | 3384K2521 | 2521224571 | 2020-12-04 | 252122 | 2020-12-02 | shaft seal leakage | 2020-03-14 | 2020-11-11 | 51 | Inhouse | chemical / pharma | 8 | Replaced oring kit | null | closed | Replaced O ring kit
2020-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sajjan India Limited | Gujrat | KCX93 | 3485K068 | 2519724555 | 2020-11-28 | 251972 | 2020-11-28 | abnormal noise | 2019-12-10 | 2020-11-12 | 12 | Inhouse | chemical / pharma | 11 | Replaced piston, piston ring set,kit delivery valve | null | closed | Replaced piston, piston ring set,kit delivery valve
2020-12-21 | Kalp Marketing | Gujrat | D | Msn Intermidaites Pvt LtdNaroda | Gujrat | KCX3 | 3374K2416 | 2519764556 | 2020-11-28 | 251976 | 2020-11-28 | kcx oil pump purging | 2020-11-06 | 2020-11-20 | 33 | Lubricare | chemical / pharma | 1 | Replaced oil pump due to purging | null | closed | Replaced oil pump due to purging
2020-12-21 | Geekay Pneumatic Pvt Ltd | null | D | Hindustan Organic Chemicals Limited | Kerala | KCX4 | 3384K2444 | 2520304564 | 2020-12-01 | 252030 | 2020-12-01 | oil carry over | 2019-12-31 | 2020-07-13 | 353 | Inhouse | chemical / pharma | 7 | Replaced piston and piston ring set | null | closed | Replaced piston and piston ring set
2020-12-26 | Multivista Global Pvt Ltd | null | D | Kumaresh Cold Storage | Tamil Nadu | KCX2 | 3364K1808 | 2523464594 | 2020-12-13 | 252346 | 2020-12-07 | krms problemdischarge temp sensor not working | 2019-06-27 | 2019-07-28 | 5044 | Cloud Q | cold storage | 1 | Sensor not working properly showing 125 degre selcius constantly | null | closed | Replaced discharge sensor
2020-12-26 | Multivista Global Pvt Ltd | null | D | MSR & Co Ice Plant | null | KCX4 | 3384K2279 | 2521944575 | 2020-12-05 | 252194 | 2020-12-05 | pressure gauge malfunctioning | 2020-06-30 | 2020-12-05 | 0 | Walchandnagar Industries | ice plant | 4 | Pressure gauge not working | null | closed | Replaced Pressure gauge
2020-12-26 | Multivista Global Pvt Ltd | null | D | Tcp LtdTamilnadu | null | KCX3 | 3374K2419 | 2518624568 | 2020-12-03 | 251862 | 2020-12-03 | oil carry over | 2020-11-09 | 2020-12-03 | 114 | Inhouse | chemical / pharma | 1 | Replaced Piston ring set and ORV | null | closed | Replaced piston ring set and ORV
2020-12-30 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Shanti Frozen Foods | Uttarakhand | KC63 | 346K287 | Service email | 2021-01-02 | 252588 | 2020-12-14 | shaft seal oring damaged | 2020-11-26 | 2020-02-13 | 2073 | Supplier | food processing | 3 | Shaft seal Orig damaged | null | closed | Replaced Oring
2020-12-30 | Cool Comfort Private Limited | West Bengal | D | Shimpo ExportsPvt Ltd | West Bengal | KCX72 | 3474K338 | 2527304601 | 2020-12-17 | 252730 | 2020-12-18 | null | 2019-12-21 | 2020-06-13 | 1789 | Inhouse | meat/fish process | 6 | Liner & Piston ring set wornout | null | closed | Replaced Liner & Piston ring set 1
2021-01-18 | Trade Links | Secunderabad | D | Prime Gases Private Limited | Rangapur | KCX93 | 3485K076 | 2524344591 | 2020-12-12 | 252434 | 2020-12-09 | discharge stop valve back leaking | 2019-11-23 | 2020-12-12 | 0 | Supplier | chemical/gas processing | 1 | Stop valve back leaking | null | closed | null
2021-01-18 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | null | KCX6 | 3394K1665 | 2527204605 | 2020-12-19 | 252720 | 2020-12-17 | k5 valve thread damaged | 2020-11-03 | 2020-12-19 | 0 | Inhouse | chemical/pharma | 1 | K5 valve threading damaged | null | closed | K5 Valve
2021-01-18 | S M Refrigeraion Pvt Ltd | null | D | Shri Satyanarain Cold Storage & Ice Factory | null | KCX1 | 3354K140 | 2496144449 | 2020-09-24 | 249614 | 2020-09-19 | oil lifting problem replaced pison ring set | 2019-11-29 | 2020-02-23 | 687 | Inhouse | cold storage | 3 | Oil Lifting problem -Replaced pison ring set | null | closed | Oil Lifting problem Replaced pison ring set
2021-01-18 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Sai All Season | null | KCX72 | 3474K344 | 2533884660 | 2021-01-16 | 253388 | 2021-01-04 | toggle switch not working | 2019-12-23 | 2021-01-16 | 0 | Supplier | cold storage | 1 | Replaced toggle switch | null | closed | Replaced toggle switch
2021-01-18 | Kalp Marketing | Gujrat | D | Humble Cows Pvt Ltd | null | KCX3 | 3374K2184 | 2477924339 | 2020-07-31 | 247792 | 2020-07-30 | shaft seal leakage | 2019-10-23 | 2019-12-04 | 1200 | Supplier | dairy / ice cream | 2 | Shaft seal leak | null | closed | Shaft seal assly
2021-01-18 | Trade Links | Secunderabad | D | Nava Quality Foods Pvt LtdChittoor | Andhra Pradesh | KCX72 | 3474K370 | Email | 2020-12-22 | null | 2020-12-22 | compressor rusty from inside | 2020-02-28 | 2020-12-22 | 0 | Customer | food processing | 10 | Compressor received back | null | closed | Compressor received back
2021-01-18 | Kalp Marketing | Gujrat | D | New Faizan Foods | Gujrat | KCX51 | 3454K130 | 2532164644 | 2021-01-07 | 253216 | 2020-12-30 | damage in flywheel | 2019-08-14 | 2019-08-21 | 1957 | Jineshwar | food processing | 1 | Replaced flywheel due to hub broken | null | closed | Replaced flywheel hub due to broken
2021-01-18 | Trade Links | Secunderabad | D | Nava Quality Foods Pvt LtdChittoor | Andhra Pradesh | KCX72 | 3474K371 | Email | 2020-12-22 | null | 2020-12-22 | scoring marks on crank shaft od & c.case rusty | 2020-02-28 | 2020-12-22 | 0 | Customer | food processing | 10 | Compressor received back | null | closed | Compressor received back
2021-01-18 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K328 | 2531784634 | 2021-01-02 | 253178 | 2020-12-29 | delivery valve leakage | 2019-09-24 | 2020-12-29 | 14 | Inhouse | ice plant | 3 | Delivery valve leak , cyl no.06 overheating | null | closed | Replaced del valve kit.
2021-01-18 | Cool Comfort Private Limited | West Bengal | D | Anjana Ice Factory | West Bengal | KCX3 | 3374K2076 | Emai | null | null | 2020-12-09 | oil carry over | 2019-03-24 | 2020-08-05 | 1037 | Customer | ice plant | 5 | Compressor received back | null | closed | Compressor received back
2021-01-18 | Kalp Marketing | Gujrat | D | Jai Khodiyar | null | KCX4 | 3384K2524 | Email | 2021-01-12 | null | 2021-01-12 | oil carry over | 2020-03-01 | 2020-08-06 | 1700 | Customer | ice plant | 5 | Compressor received back | null | closed | Compressor received back
2021-01-18 | Geekay Pneumatic Pvt Ltd | null | D | Ajmo Ice & Freezers | null | KCX2 | 3364K2043 | 2530684633 | 2021-01-02 | 253068 | 2020-12-26 | oil pump purging | 2020-11-09 | 2020-12-02 | 191 | M/S Dinesh Ent. | ice plant | 1 | Replaced oil pump assly | null | closed | Oil pump assly
2021-01-18 | Kalp Marketing | Gujrat | D | Sagar Ice | null | KCX3 | 3374K2364 | 2530784619 | 2020-12-29 | 253078 | 2020-12-26 | pressure gauge not working | 2020-08-12 | 2020-12-27 | 0 | Walchandnagar ind | ice plant | 4 | Pr. Gauge not working | null | closed | Pressure gauge
2021-01-18 | Kalp Marketing | Gujrat | D | Shiv Shakti Ice Factory | null | KCX4 | 3384K2582 | 2527644632 | 2021-01-01 | 252764 | 2020-12-18 | shaft seal leakageoring replaced | 2020-09-22 | 2020-11-05 | 1100 | Inhouse | ice plant | 2 | Shaft seal leak replaced Oring kit | null | closed | O ring kit
2021-01-18 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Asahi Tennants Colors Pvt Ltd | Gujrat | KCX3 | 3374K2312 | 2514124649 | 2021-01-09 | 251412 | 2020-12-29 | flywheel fitment issue | 2020-02-28 | 2020-12-19 | 4 | Jineshwar | chemical / pharma | 10 | Replaced Flywheel due to fitment problem | null | closed | Replaced flywheel
2021-01-18 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K014 | 2528584630 | 2020-12-31 | 252858 | 2020-12-21 | oil liftingliner and piston ring set replaced | 2020-08-16 | 2020-11-21 | 400 | Inhouse | chemical / pharma | 3 | Replaced piston ring sets and liner | null | closed | Replaced piston ring sets and liner
2021-01-18 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Kiri Industries Limited | null | KCX12 | 3415K006 | 2532884635 | 2021-01-02 | 253288 | 2021-01-02 | piston crackknocking sound in compressor | 2019-03-31 | 2019-12-06 | 8611 | Inhouse | chemical / pharma | 8 | Piston crack | null | closed | Replace piston
2021-01-18 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | null | KCX6 | 3394K1665 | 2530964623 | 2020-12-29 | 253096 | 2020-12-28 | stop valve passing tal100/125teflon damaged | 2020-11-03 | 2020-12-18 | 143 | Supplier | chemical / pharma | 1 | Replaced Teflon ring | null | closed | Teflon ring
2021-01-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aries Color Chem Pvt Ltd | Gujrat | KCX9 | 3404K157 | 2533844643 | 2021-01-06 | 253384 | 2021-01-07 | high oil consumptionpiston crack | 2020-10-13 | 2020-10-23 | 1600 | Paramount pistons | ice plant | 1 | Cyl no. 01,02,03,04 pistons crack-replaced | null | closed | null
2021-01-30 | Geekay Pneumatic Pvt Ltd | null | D | Abees Ice Plant | Kerala | KCX3 | 3374K2228 | 2527084610 | 2020-12-21 | 252708 | 2020-12-21 | pressure gauge out | 2019-12-18 | 2020-12-21 | 3 | Walchandnagar industries | ice plant | 12 | Pressure gauge out | null | closed | Replaced Oil pressure gauge
2021-01-30 | Multivista Global Pvt Ltd | null | D | Nas Fisheries Pvt Ltd | Kerala | KCX72 | 3474K372 | 2527624604 | 2020-12-19 | 252762 | 2020-12-19 | pressure gauge out | 2020-03-13 | 2020-12-19 | 2 | Walchandnagar industries | meat/fish process | 9 | Replaced Int. pressure gauge | null | closed | Replaced Int. pressure gauge
2021-01-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shubhlaxmi Cold Storage | Gujrat | KCX3 | 3374K2185 | Service email | 2021-02-01 | 254248 | 2021-01-25 | oil carry over | 2019-10-26 | 2020-02-20 | 3482 | Inhouse | cold storage | 4 | VLD Orings expand | null | closed | Replaced VLD Orings
2021-01-31 | Parag Marketing Services | null | D | D J Exports Pvt Ltd | Nashik | PCX2 | 3106K0006 | 2530844638 | 2021-01-04 | 253084 | 2020-12-27 | shaft seal leakage | 2019-09-30 | 2020-02-05 | 1828 | Inhouse | cold storage | 5 | Shaft seal leakage . Freon gas application | null | closed | Replaced Shaft seal assly
2021-01-31 | Kalp Marketing | Gujrat | D | Sahara Frozen Foods | Madhya Pradesh | KCX63 | 3464K061 | 2537364669 | 2021-01-22 | 253736 | 2021-01-22 | delivery valve leakage | 2019-12-21 | 2021-01-22 | 1 | Inhouse | food processing | 13 | 2 nos HP Discharge valve leakage due to rusty DD TO DC 13 months. Pressure gauge glycerin colour changed & leakage. | null | closed | Replaced DV & Pr gauge
2021-01-31 | Trade Links | Secunderabad | D | Sagar Grandhi Exoports Pvt Ltd | Andhra Pradesh | KCX4 | 3384K2233 | 2525304592 | 2020-12-13 | 252530 | 2020-12-13 | abnormal noisepiston crack | 2019-03-18 | 2019-11-05 | 2346 | Paramount pistons | ice plant | 8 | Replaced Delivery valve,piston-1,Liner, piston ring set | null | closed | Replaced Delivery valve,piston1,Liner, piston ring set
2021-01-31 | Kalp Marketing | Gujrat | D | Jagdama Ice | Gujrat | KCX4 | 3384K2501 | 2526964599 | 2020-12-17 | 252696 | 2020-12-17 | high oil consumption | 2020-02-22 | 2020-06-04 | 5072 | Inhouse | ice plant | 1 | Replace VLD orings | null | closed | null
2021-01-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shree Jalaram Tube Ice | Gujrat | KCX4 | 3384K2567 | 2540844668 | 2021-01-22 | 254084 | 2021-01-21 | shaft seal leakage | 2020-09-29 | 2020-10-20 | 4 | Supplier M/s. ME | ice plant | 1 | Shaft seal leakage | null | closed | Replaced shaft seal
2021-01-31 | Kalp Marketing | Gujrat | D | Mahakali Ice Naroda | Gujrat | KCX4 | 3384K2499 | 2526984600 | 2020-12-17 | 252698 | 2020-12-17 | high oil consumption | 2020-02-22 | 2020-06-05 | 4512 | Inhouse | ice plant | 4 | High oil consumption | null | closed | Replaced VLD Orings
2021-01-31 | Cool Comfort Private Limited | West Bengal | D | Za Sea Foods | West Bengal | KCX72 | 3474K350 | 2538124655 | 2021-01-13 | 253812 | 2021-01-19 | shaft seal leakage | 2021-01-22 | 2020-01-05 | 1110 | Inhouse | meat/fish process | 5 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2021-01-31 | Geekay Pneumatic Pvt Ltd | null | D | Premier Marine Foods | Kerala | KCX31 | 3434K0120 | 2533064639 | 2021-01-04 | 253306 | 2021-01-04 | oil pressure not buildup | 2019-12-20 | 2020-01-14 | 2415 | Lubricare old type pump | meat/fish process | 1 | Purging problem | null | closed | Replaced oil pump assly
2021-01-31 | Geekay Pneumatic Pvt Ltd | null | D | Economic Food Solutions Pvt Ltd | Kerala | KCX21 | 3424K111 | 2538844658 | 2021-01-16 | 253884 | 2021-01-16 | oil pressure not buildup | 2020-11-30 | 2021-01-02 | 56 | DK Industries | meat/fish process | 1 | Oil pressure not develop , frequent purging required. | null | closed | Replaced Pump assembly
2021-01-31 | Parag Marketing Services | null | D | Hma Agro Industries Ltd | Maharashtra | KCX72 | 3474K317 | 2536164646 | 2021-01-06 | 253616 | 2021-01-08 | over heating | 2019-10-04 | 2020-04-01 | 36 | Customer | meat/fish process | 6 | Overheating problem.Piston , Cylinder liner , discharge valve , piston rings wornout | null | closed | Replaced Piston , Cylinder liner , discharge valve , piston rings wornout
2021-01-31 | Parag Marketing Services | null | D | Aquachill System India Pvt Ltd | Pune | PCX2 | 3106K0029 | 2537344656 | 2021-01-13 | 253734 | 2021-01-13 | bearing cover leakage | 2020-02-10 | 2021-01-13 | 4 | Supplier | chemical / pharma | 11 | Bearing cover porous / Lekage from stud hole. | null | closed | PC2 Bearing cover
2021-01-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2037 | 2540304665 | 2021-01-20 | 254030 | 2021-01-20 | overheating delivery valve leakage | 2020-11-03 | 2021-01-12 | 1 | Inhouse | chemical / pharma | 3 | Cylinder overheating due to delivery valve leakage | null | closed | Replaced delivery valve assly
2021-01-31 | Kalp Marketing | Gujrat | D | Ami Pigments | Gujrat | KCX4 | 3384K2502 | 2531484624 | 2020-12-29 | 253148 | 2020-12-30 | abnormal noisedelivery valve leak | 2020-02-25 | 2020-09-01 | 1406 | Inhouse | chemical / pharma | 7 | Replaced piston,linerdel valve assly,piston ring set | null | closed | Replaced piston,linerdel valve assly,piston ring set
2021-02-17 | Trade Links | null | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K2315 | 2533924647 | 2021-01-08 | 253392 | 2021-01-07 | delivery valve leakage | 2019-09-30 | 2019-12-07 | 4259 | Inhouse | food processing | 3 | Replaced cylinder liner, piston , piston ring set. | null | closed | Replaced cylinder liner, piston , piston ring set.
2021-02-17 | Parag Marketing Services | null | D | Royal Food Stuff Pvt Ltd | Satara | KCX42 | 3444K146 | 2539084684 | 2021-02-03 | 253908 | 2021-02-03 | knocking soundpiston crack | 2019-03-09 | 2019-08-17 | 7785 | Paramount pistons | food processing | 5 | Piston crack in cylinder no 04 | null | closed | Replaced piston and piston ring set1No.
2021-02-17 | Trade Links | Secunderabad | D | Mahalaxmi Ice Factory | Andhra Pradesh | KCX2 | 3364K1852 | 2524004578 | 2020-12-08 | 252400 | 2020-12-08 | kcx low oil pressure | 2019-09-25 | 2019-10-16 | 2800 | M/S LDK | ice plant | 1 | OPR Malfunctioning | null | closed | Replaced KCX oil pump OPR
2021-02-17 | Trade Links | Secunderabad | D | Jai Shankar Ice Plant | Telangana | KCX6 | 3394K1291 | 2510384545 | 2020-11-17 | 251038 | 2020-11-17 | kcx oil pump purging | 2019-02-27 | 2019-06-26 | 8411 | Inhouse | ice plant | 4 | KCX oil pump purging issue. | null | closed | Replaced KCX oil pump element
2021-02-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K329 | 2553804735 | 2021-02-21 | 255380 | 2021-02-20 | krms controller board problem | 2019-09-24 | 2020-10-16 | 428 | Carel | ice plant | 13 | IP & OP Ports are not working | null | closed | Replaced control board
2021-02-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K329 | 2552664717 | 2021-02-17 | 255266 | 2021-02-16 | krms sensor overheated | 2019-09-24 | 2020-10-16 | 428 | Cloud Q | ice plant | 13 | HP discharge sensor overheated and broken | null | closed | HP discharge sensor
2021-02-17 | Trade Links | Secunderabad | D | Vijaya Laxmi Ice And Cold Storage | Andhra Pradesh | KCX3 | 3374K2420 | 2544924686 | 2021-02-03 | 254492 | 2021-02-03 | op pressure switch malfunctioning | 2020-11-12 | 2021-02-03 | 3 | Danfoss | ice plant | 3 | OP pressure switch not working | null | closed | Replace OP pressure switch
2021-02-17 | Geekay Pneumatic Pvt Ltd | null | D | Nas Fisheries Pvt Ltd | Kerala | KCX72 | 3474K372 | 2546624698 | 2021-02-08 | 254662 | 2021-02-06 | oil carry over | 2020-03-13 | 2020-12-19 | 328 | Inhouse | meat/fish process | 9 | Piston ring sets wornout | null | closed | Piston ring sets
2021-02-17 | Trade Links | Secunderabad | D | Akshay Food Impex | Andhra Pradesh | KCX72 | 3474K392 | 2495244459 | 2020-09-24 | 249524 | 2020-09-20 | delivery valve leakage | 2020-08-29 | 2020-09-20 | 2 | Inhouse | meat/fish process | 1 | Cylinder no 04 HP delivery valve leak and piston siezed | null | closed | Replace Piston , gudgeon pin neddle bearing,liner,del valve assly.
2021-02-17 | Trade Links | Secunderabad | D | Arch Pharma Labls Ltd | Telangana | KCX4 | 3384K2537 | 2546464705 | 2021-02-10 | 254646 | 2021-02-10 | kcx low oil pressure | 2020-06-22 | 2021-02-10 | 22 | M/S LDK | chemical / pharma | 8 | OPR Malfunctioning | null | closed | Replaced KCX oil pump OPR
2021-02-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jay Chemicals | Vapi, Gujarat | KCX3 | 3374K2137 | 2543544691 | 2021-02-04 | 254354 | 2021-02-02 | abnormal noisepiston crack | 2019-06-30 | 2020-02-11 | 3760 | Paramount pistons | chemical / pharma | 8 | Piston crack , kit del valve ring spring broken | null | closed | Replaced piston, buffer spring,del valve assly, buffer spring.
2021-02-17 | Kalp Marketing | Gujrat | D | Meghmani Dyes | Gujrat | KCX9 | 3404K160 | 2539024661 | 2021-01-16 | 253902 | 2021-01-16 | kcx oil pressure not develops | 2020-09-30 | 2020-12-29 | 26 | M/S LDK | chemical / pharma | 3 | KCX pump element tang broken | null | closed | Replaced OP element
2021-02-17 | Parag Marketing Services | null | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K015 | 2544864685 | 2021-02-03 | 254486 | 2021-02-05 | oil carry over | 2020-08-16 | 2020-11-10 | 1100 | Inhouse | chemical / pharma | 3 | Oil throw from cylinder no.3,4,6,7,8,9. | null | closed | Replaced piston ring sets6
2021-02-17 | Parag Marketing Services | null | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K015 | 2540984670 | 2021-01-22 | 254098 | 2021-01-28 | oil carry over | 2020-08-16 | 2020-11-10 | 920 | Inhouse | chemical / pharma | 3 | Replaced ORV 6nos | null | closed | Replaced ORV 6nos
2021-02-17 | Trade Links | Secunderabad | D | Avr Organics Pvt Ltd | Telangana | KCX6 | 3394K1511 | 2496244453 | 2020-09-22 | 249624 | 2020-09-24 | oil carry over | 2020-02-19 | 2020-05-09 | 1159 | Inhouse | chemical / pharma | 3 | Piston ring sets wornout | null | closed | Repalced piston ring sets4,piston1
2021-02-26 | Fridge House | null | D | Basaveshwar Cold Storage | Karnataka | KCX3 | 3374K 2428 | Service email | 2021-02-24 | 255544 | 2021-02-23 | wrong sbm no punching on compressor name plate. | 2020-11-25 | 2021-02-23 | 0 | Inhouse | cold storage | 3 | wrong serial number punched on a nameplate. Correct Serial Number : KCX 3 - 3374K2428 Wrong Serial Number : KCX 3 - 3384K2428 | null | closed | Name plate replaced
2021-02-27 | Parag Marketing Services | null | D | Agrani Foods & Agro Processing Pvt Ltd | Sangli | KCX3 | 3374K1967 | 2500184727 | 2021-02-18 | 250018 | 2021-02-18 | knocking / abnormal sound | 2018-12-01 | 2019-05-27 | 2948 | Inhouse | dairy / ice cream | 5 | Cylinder liner , piston and piston ring set worn out | null | closed | Replaced cylinder liner,piston ring set, piston
2021-02-27 | Geekay Pneumatic Pvt Ltd | null | D | Pearl Ice Plant | Kerala | KCX3 | 3374K2360 | 2544944711 | 2021-02-13 | 254494 | 2021-02-01 | pressure gauge malfunctioning | 2020-08-11 | 2021-01-12 | 306 | M/S Walchandnagar industries | ice plant | 5 | Pressure gauge bulged and ammonia leaking | null | closed | Replaced Pressure gauge
2021-02-27 | Geekay Pneumatic Pvt Ltd | null | D | A M Fisheries | Kerala | KCX42 | 3444K216 | 2553004722 | 2021-02-17 | 255300 | 2021-02-17 | kcx low oil pressuretang broken | 2020-07-27 | 2021-01-28 | 5 | null | meat/fish process | 6 | KCX oil pump element tang broken | null | closed | Replaced pump element
2021-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aimjay Agro Fresh Llp | Mumbai | KCX3 | 3374K2077 | 2547684696 | 2021-02-06 | 254768 | 2021-02-06 | shaft seal leakage | 2019-03-24 | 2019-11-06 | 5067 | Supplier | cold storage | 8 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2021-02-28 | Cool Comfort Private Limited | West Bengal | D | India Dairy Products Ltd | West Bengal | KCX4 | 3384K2546 | 2551804714 | 2021-02-15 | 255180 | 2021-02-22 | high oil consumption | 2020-07-19 | 2020-09-23 | 1030 | Inhouse | dairy / ice cream | 2 | Replaced cylinder liner,piston,piston ring set, gudgeon pin,bearings | null | closed | Replaced cylinder liner,piston,piston ring set, gudgeon pin,bearings
2021-02-28 | Kalp Marketing | Gujrat | D | Sarvottam Dairy | Bhavnagar | KCX6 | 3394K1513 | Service email | 2021-02-12 | null | 2021-02-12 | paint peeloff | 2020-02-22 | null | 0 | Inhouse | dairy / ice cream | 12 | The compressor is observed with significant pillage of paint in Compressor Body. The Photograph is attached. Installation work is going on. OEM have complained about poor color quality . | null | closed | null
2021-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Amar Ice & Cold Storage | Gujrat | KCX3 | 3374K2299 | 2552284715 | 2021-02-16 | 255228 | 2021-02-16 | oil carry over | 2020-02-14 | 2020-03-21 | 1734 | Inhouse | ice plant | 1 | Replaced VLD piston Orings | null | closed | Replaced VLD piston Orings
2021-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Aries Color Chem Pvt Ltd | Gujrat | KCX9 | 3404K157 | 2545884687 | 2021-02-03 | 254588 | 2021-02-04 | piston crack | 2020-10-13 | 2020-10-23 | 2300 | Paramount pistons | ice plant | 1 | Replaced piston-2,kit del valve-1 | null | closed | Replaced piston2,kit del valve1
2021-02-28 | Gargi Engineering Enterprices Pvt Ltd | null | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2037 | 2530884653 | 2021-01-12 | 253088 | 2021-01-12 | delivery valve leakage | 2020-11-03 | 2021-01-12 | 4 | Inhouse | chemical / pharma | 3 | Replaced valve kit due to del valve leak | null | closed | Replaced valve kit
2021-02-28 | Kalp Marketing | Gujrat | D | Navin Fluorine International Ltd | Madhya Pradesh | KCX2 | 3364K1871 | Service email | 2021-03-01 | 254638 | 2021-02-05 | loading problemtap bolt broken | 2019-11-25 | 2020-08-07 | 661 | Supplier | chemical / pharma | 9 | Direct cylinder head tap bolt broken | null | closed | Replaced Tap bolt
2021-03-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Upl Limited | Baruch,Gujarat | KCX12 | 3415K019 | 2559164766 | 2021-03-04 | 255916 | 2021-03-04 | oil carryover piston crack | 2020-09-11 | 2020-12-05 | 680 | Inhouse | chemical | 3 | Piston crack | null | closed | Replaced piston and piston ring set
2021-03-21 | Cool Comfort Private Limited | West Bengal | D | Bhaktimoyee Cold Storage | West Bengal | KCX6 | 3394K1748 | 2562344777 | 2021-03-08 | 256234 | 2021-03-09 | kcx oil pump tang broken | 2021-02-13 | 2021-03-09 | 1 | M/S LDK | cold storage | 1 | Replaced oil pump element | null | closed | Replaced oil pump element
2021-03-21 | Kalp Marketing | Gujrat | D | Mahaveer Agri Cold | Gujrat | KCX2 | 3364K2046 | 2559324779 | 2021-03-10 | 255932 | 2021-03-09 | oil pump purging | 2020-11-24 | 2021-03-09 | 3 | Supplier Dinesh Enterprices | cold storage | 4 | Air purging problem in oil pump assly | null | closed | Replaced pump assly
2021-03-21 | Hss Solution Pvt Ltd | null | D | Mewar Dairy | Rajastan | KCX2 | 3364K1934 | 2553944761 | 2021-03-02 | 255394 | 2021-02-19 | kcx oil pump tang broken | 2020-02-19 | 2020-08-24 | 158 | Supplier | dairy / ice cream | 6 | Element broken | null | closed | Replaced element
2021-03-21 | Cool Comfort Private Limited | West Bengal | D | Anjana Ice Factory | West Bengal | KCX3 | 3474K2076 | 2553044733 | 2021-02-20 | 255304 | 2021-02-20 | bottom plate and screw from tool box damaged | 2019-03-24 | 2020-08-05 | 1079 | M/S Uttam Engg | ice plant | 5 | Bottom plate and screw damaged | null | closed | Replaced Bottom plate and screw.
2021-03-21 | Trade Links | null | D | Vijaya Lakshmi Ice & Cold Storage | Andhra Pradesh | KCX3 | 3374K2420 | 2559684769 | 2021-03-04 | 255968 | 2021-03-04 | loading & uloading problem | 2020-11-12 | 2021-02-03 | 545 | Inhouse | ice plant | 3 | Loading problem & overheating cylinder no.1 due to delivery valve leakage , buffer spring shrink & piston rings wornout | null | closed | Replaced Piston ring set , Delivery valve & Buffer spring
2021-03-21 | Trade Links | null | D | Ananda Fisheries | Andhra Pradesh | KCX6 | 3394K1634 | 2544404681 | 2021-02-01 | 254440 | 2021-02-01 | oil carry over | 2020-09-15 | 2020-12-17 | 781 | Inhouse | ice plant | 3 | Piston rings wornout & oil throw | null | closed | Piston rings 6
2021-03-21 | Trade Links | null | D | Ananda Fisheries | Andhra Pradesh | KCX6 | 3394K1634 | 2549884710 | 2021-02-11 | 254988 | 2021-02-13 | oil carry over | 2020-09-15 | 2020-12-17 | 1004 | Inhouse | ice plant | 3 | Cylinder no.1 Piston and Piston rings wornout & oil throw | null | closed | Replaced Cylinder Liner , Piston , piston rings & orv
2021-03-21 | Geekay Pneumatic Pvt Ltd | null | D | Ajmo Ice & Freezers | null | KCX2 | 3364K2043 | 2551824732 | 2021-02-20 | 255182 | 2021-02-20 | oil carryover piston crack | 2020-11-09 | 2020-12-02 | 1110 | Paramount pistons | ice plant | 1 | Hair line crack on 1 piston | null | closed | Replaced Piston , Piston ring sets , 1
2021-03-21 | Geekay Pneumatic Pvt Ltd | null | D | AVA Ice & Cold Storage | Kerala | KCX3 | 33742384 | 2552744730 | 2021-02-19 | 255274 | 2021-02-19 | oil carryover piston crack | 2020-09-19 | 2020-11-05 | 1505 | Paramount pistons | ice plant | 2 | Hair line crack on all pistons | null | closed | Replaced Piston , Piston ring sets , 3
2021-03-21 | Trade Links | null | D | Naga Hanuman Fish Packers | Andhra Pradesh | KCX6 | 3394K1528 | 2551704721 | 2021-02-17 | 255170 | 2021-02-17 | oil carryover piston crack | 2020-05-23 | 2020-09-06 | 1882 | Paramount pistons | ice plant | 4 | Piston crack & Liner wornout | null | closed | Replaced Piston , Piston ring set & Cylinder Liners 3
2021-03-21 | Fridge House | null | D | Ideal Ice Cream | Mangalore, Karnataka | KCX4 | 3384K2434 | 2554784790 | 2021-03-13 | 255478 | 2021-03-13 | tah8 valve and adaptor not supplied | 2019-12-31 | 2021-03-13 | 0 | Inhouse | ice plant | 14 | short supply case | null | closed | null
2021-03-21 | Fridge House | null | D | Ideal Ice Cream | Mangalore, Karnataka | KCX63 | 3464K0063 | 2554804791 | 2021-03-14 | 255480 | 2021-03-14 | tah8 valve and adaptor not supplied | 2020-01-22 | 2021-03-23 | 0 | Inhouse | ice plant | 14 | short supply case | null | closed | null
2021-03-21 | Fridge House | null | D | Ideal Ice Cream | Mangalore, Karnataka | KCX63 | 3464K0067 | 2554824792 | 2021-03-14 | 255482 | 2021-03-14 | tah8 valve and adaptor not supplied | 2020-02-07 | 2021-03-14 | 0 | Inhouse | ice plant | 12 | short supply case | null | closed | null
2021-03-21 | Trade Links | null | D | Akshay Food Impex | Andhra Pradesh | KCX72 | 3474K392 | 2539844674 | 2021-01-24 | 253984 | 2021-01-24 | oil carry over | 2020-08-29 | 2020-09-20 | 1126 | null | meat/fish process | 1 | Cylinder no. 1,4,7 Liners wornout & Cyl no. 1,2,4,5,7,9 Piston rings wornout | null | closed | Replaced Liners & Piston ring sets
2021-03-21 | Trade Links | null | D | Akshay Food Impex | Andhra Pradesh | KCX72 | 3474K412 | 2561804776 | 2021-03-08 | 256180 | 2021-03-07 | piston crack | 2020-10-21 | 2020-11-10 | 1430 | Paramount pistons | meat/fish process | 1 | Piston crack & Piston rings wornout | null | closed | Replaced Piston & Piston ring set
2021-03-21 | Trade Links | null | D | Akshay Food Impex | Andhra Pradesh | KCX42 | 3444K241 | 2542384678 | 2021-01-29 | 254238 | 2021-01-28 | shaft seal leakage | 2020-10-21 | 2020-11-12 | 49 | Site issue | meat/fish process | 1 | Shaft seal and Crank shaft main bearings wornout. Oil brand changed | null | closed | Replaced Shaft seal & bearings
2021-03-21 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Kanpur Plastipack Ltd | Uttar Pradesh | KCX4 | 3384K2611 | 2555964775 | 2021-03-06 | 255596 | 2021-02-26 | oil carry over | 2020-11-04 | 2021-02-11 | 318 | Inhouse | chemical / pharma | 3 | Breather assly leakage | null | closed | Replaced breather assly
2021-03-21 | Trade Links | null | D | Arch Pharma Labls Ltd | Telangana | KCX63 | 3464K075 | 2562244784 | 2021-03-10 | 256224 | 2021-03-10 | oil carry over | 2020-06-01 | 2020-09-27 | 2394 | Site issue | chemical / pharma | 4 | ORV Blockage and system side issue of high intermediate pressure | null | closed | Replaced ORV
2021-03-21 | Trade Links | null | D | Virchow Petro Chemicals Pvt Ltd | Telangana | KCX84 | 3305K006 | 2542144672 | 2021-01-23 | 254214 | 2021-01-23 | over heating | 2019-06-25 | 2019-10-12 | 6774 | Inhouse | chemical / pharma | 4 | HP Cylinder 4 delivery valve leakage due to ring spring broken | null | closed | Replaced Liner , Piston ring set and Delivery valve assly
2021-03-21 | Fridge House | null | D | Ideal Ice Cream | Mangalore, Karnataka | KCX93 | 3485K0081 | 2554844793 | 2021-03-14 | 255484 | 2021-03-14 | control panel selector switch & lock damaged | 2019-12-31 | 2021-03-14 | 0 | Transit damage | transit damage | 14 | Transit damage | null | closed | Selector switch & lock
2021-03-23 | S M Refrigeraion Pvt Ltd | null | D | Tiwari Cold Storage | Uttar Pradesh | KCX2 | 3364K2065 | 2564864799 | 2021-03-16 | 256486 | 2021-03-20 | oil pressure not buildup | 2021-01-05 | 2021-02-14 | 130 | LDK | cold storage | 1 | Oil pump elemnt broken | null | closed | Replaced pump element
2021-03-23 | Kalp Marketing | Gujrat | D | Alps Exim Pvt Ltd | Gujrat | KCX42 | 3444K243 | 2562184785 | 2021-03-11 | 256218 | 2021-03-11 | op pressure switch malfunctioning | 2020-10-23 | 2021-03-11 | 7 | Danfoss | cold storage | 5 | Oil pressure switch tripping to 2 min | null | closed | Replaced OP pressure switch
2021-03-23 | Kalp Marketing | Gujrat | D | Divyashakti Fertilizer & Chemicals Pvt Ltd | Madhya Pradesh | KCX4 | 3384K2397 | 2565724801 | 2021-03-17 | 256572 | 2021-03-16 | shaft seal leakage | 2019-11-27 | 2020-02-13 | 1969 | null | cold storage | 3 | Shaft seal leakage | null | closed | Replaced shaft seal assly
2021-03-23 | Kalp Marketing | Gujrat | D | Elite Dairy Products | Madhya Pradesh | KCX2 | 3364K1777 | 2551144781 | 2021-03-10 | 255114 | 2021-03-01 | delivery valve leakage | 2019-05-12 | 2021-03-01 | 2 | Inhouse | dairy / ice cream | 20 | Long stock compressor , Discharge valve assly leakage. | null | closed | Changed kit delivery valve
2021-03-23 | Cool Comfort Private Limited | West Bengal | D | Anjana Ice Factory | West Bengal | KCX3 | 3374K2076 | 2565244802 | 2021-03-17 | 256524 | 2021-03-18 | courtesy visit | 2019-03-24 | 2020-08-05 | 4 | null | ice plant | 5 | null | null | null | null
2021-03-23 | Kalp Marketing | Gujrat | D | J J Industries | Gujrat | KCX4 | 3384K2604 | 2561624780 | 2021-03-10 | 256162 | 2021-03-06 | high oil consumption | 2020-10-21 | 2021-02-15 | 320 | Inhouse | ice plant | 5 | ORV 4 Nos found malfuctioning , VLD | null | closed | Replaced VLD Orings, VLD Piston & ORV 4 Nos.
2021-03-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mahisagar Ice Fcatory | Gujrat | KCX3 | 3374K2523 | 2567164816 | 2021-03-20 | 256716 | 2021-03-20 | krms control panel box burnt | 2021-02-27 | 2021-03-20 | 0 | Inhouse | ice plant | 1 | When KRMS box was open . It was found control panel was sloghtly burnt. | null | closed | Replaced Control panel
2021-03-23 | null | null | E | Ying Charoen Ice Khon Kaen Co Ltd Khon Kaen Province | Thailand | KCX6 | 3394K1677 | null | null | 653 | 2021-02-27 | low oil pressure & c.case rusty | 2020-10-01 | 2021-02-05 | 77 | Inhouse | tube ice | 3 | C.case rusty, filter blocked,low oil pressure | null | closed | null
2021-03-24 | Fridge House | null | D | Ideal Ice Cream | Mangalore, Karnataka | KCX93 | 3485K0080 | 2554884794 | 2021-03-14 | 255488 | 2021-03-14 | tah8 valve and adaptor not supplied | 2020-02-07 | 2020-02-07 | 0 | Inhouse | ice plant | 1 | TAH8 valve and adaptor not supplied | null | closed | null
2021-03-24 | Trade Links | null | D | Akshay Food Impex | Andhra Pradesh | KCX72 | 3474K393 | 2554544773 | 2021-03-06 | 255454 | 2021-03-05 | abnormal noise | 2020-08-29 | 2020-09-18 | 1908 | null | meat/fish process | 1 | Cylinder No.4 Liner worn out piston & piston rings damaged. | null | closed | Replaced cylinder liner , Piston & Piston ring sets
2021-03-24 | Kalp Marketing | Gujrat | D | Jagdamaba Polymers | Gujrat | KCX4 | 3384K2352 | 2567064819 | 2021-03-22 | 256706 | 2021-03-20 | oil pressure problem | 2019-09-25 | 2019-12-26 | 1367 | LDK Old pump | others | 3 | Pump element broken - old type | null | closed | Replaced pump element
2021-03-27 | Parag Marketing Services | null | D | D J Exports Pvt Ltd | Nashik | PCX2 | 3106K0007 | 2531224787 | 2021-03-11 | 253122 | 2021-03-11 | shaft seal leakage | 2019-09-30 | 2020-02-05 | 1859 | Inhouse | cold storage | 5 | Site issue-Buisness promotion (incomplete foundation work) | null | closed | Replaced shaft seal assly
2021-03-27 | Hss Solution Pvt Ltd | null | D | Jasaram Milk Food Pvt Ltd | Rajastan | KCX4 | 3384K2547 | 256800 | 2021-03-20 | 256800 | 2021-03-22 | kcx oil pump tang broken | 2020-07-21 | 2020-11-24 | 488 | M/S LDK | food processing | 4 | Tang broken, inner race jam with ball bearing, pump element replaced | null | closed | Replaced pump element
2021-03-30 | Cool Comfort Private Limited | West Bengal | D | Shubhasoumya Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K2414 | 2570784828 | 2021-03-26 | 257078 | 2021-03-26 | abnormal noise | 2019-12-11 | 2020-07-06 | 2520 | null | cold storage | 6 | Cylinder no. 2 delivery valve kit broken , piston rings , gudgeon pin , con rod bush damaged. | null | closed | Replaced delivery valve kit broken , piston rings , gudgeon pin , con rod bush
2021-03-30 | Trade Links | null | D | A B Ice Factory | Andhra Pradesh | KCX4 | 3384K2415 | 2564524800 | 2021-03-17 | 256452 | 2021-03-17 | high oil consumption | 2019-12-13 | 2020-01-20 | 7583 | null | ice plant | 1 | Cylinder no. 2 seized due to delivery valve kit broken | null | closed | Replaced buffer spring , piston , cylinder liner & DV
2021-03-31 | Cool Comfort Private Limited | West Bengal | D | Bileshwar Cold Storage Pvt Ltd | Gujrat | KCX3 | 3374K2485 | Service email | 2021-04-03 | 256874 | 2021-03-22 | kcx oil pump low oil pressure | 2021-01-20 | 2021-03-13 | 0 | M/S DE | cold storage | 2 | Low oil pressure problem, replaced pump cover gasket | null | closed | Pump cover gasket
2021-03-31 | Cool Comfort Private Limited | West Bengal | D | Shivalaya Cold Storage Pvt Ltd | null | KCX6 | 3394K1721 | Service email | 2021-04-03 | 256908 | 2021-03-23 | kcx oil pump low oil pressure | 2021-01-08 | 2021-03-16 | 0 | M/S Lubricare | cold storage | 2 | Low oil pressure problem, replaced pump cover gasket | null | closed | Pump cover gasket
2021-03-31 | Parag Marketing Services | null | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX31 | 3434K0139 | 2539364729 | 2021-02-19 | 253936 | 2021-01-22 | pressure gauge not working | 2020-08-19 | 2021-01-22 | 6 | M/S Walchandnagar industries | cold storage | 5 | Pressure gauge not working | null | closed | Replaced Pr.Gauge
2021-03-31 | Geekay Pneumatic Pvt Ltd | null | D | Elandu Milk Pvt Ltd | Kerala | KCX3 | 3374K2226 | 2565064823 | 2021-03-24 | 256506 | 2021-03-24 | oil carryover piston crack | 2019-12-17 | 2020-07-15 | 1280 | M/S Paramount pistons | dairy / ice cream | 7 | Piston crack 1no. and piston ring sets 03 nos wornout | null | closed | Replaced Piston 1no. and piston ring sets 03 nos.
2021-03-31 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Mohyal Foods Pvt Ltd | Uttarakhand | KCX93 | 3485K050 | 2490004426 | 2020-09-10 | 249000 | 2020-10-04 | abnormal noise | 2019-01-30 | 2019-12-13 | 239 | Shimoga piston rings | food processing | 11 | Piston rings wornout | null | closed | Replaced piston,liner and piston ring sets
2021-03-31 | Multivista Global Pvt Ltd | null | D | Leon And Sons Ice Plant | Tamil Nadu | KCX4 | 3384K2559 | 2564144789 | 2021-03-13 | 256414 | 2021-03-12 | abnormal noise | 2020-08-11 | 2020-11-20 | 1701 | Inhouse | ice plant | 3 | Piston siezed due to overheating & delivery valve found leak | null | closed | Replaced piston,piston ring set, del valve,liner
2021-03-31 | Geekay Pneumatic Pvt Ltd | null | D | Friends Ice | Kerala | KCX4 | 3384K2635 | 2568064821 | 2021-03-24 | 256806 | 2021-03-24 | kcx oil pump purging | 2020-11-30 | 2021-03-18 | 40 | M/S DE | ice plant | 4 | Oil pump pressure not develops after power failure restart. | null | closed | Replaced Oil pump
2021-03-31 | Geekay Pneumatic Pvt Ltd | null | D | Salis Ice Products | Kerala | KCX72 | 3394K1736 | 2566904814 | 2021-03-20 | 256690 | 2021-03-18 | oil pump purging | 2021-01-22 | 2021-02-16 | 485 | M/S DE | ice plant | 1 | Oil pump purging issue | null | closed | Replaced oil pump
2021-03-31 | Kalp Marketing | Gujrat | D | Sun International | Gujrat | KCX72 | 3474K424 | 2570564827 | 2021-03-26 | 257056 | 2021-03-26 | pressure gauge not working | 2020-11-30 | 2021-03-04 | 33 | M/S Walchandnagar industries | meat/fish process | 4 | HP Pressure gauge not working . Glass cover expanded. | null | closed | Replaced pressure gauge 025Kg/cm2
2021-03-31 | Trade Links | null | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K014 | 2556104781 | 2021-02-25 | 255610 | 2021-02-24 | flywheel groove problem | 2020-08-16 | 2020-11-21 | 24 | Jineshwar | chemical / pharma | 3 | Flywheel groove oversize, belt sagging in one groove | null | closed | Replaced Flywheel
2021-03-31 | Multivista Global Pvt Ltd | null | D | Tcp LtdTamilnadu | null | KCX1 | 3354K182 | 2552244719 | 2021-02-17 | 255224 | 2021-02-17 | op pressure switch malfunctioning | 2021-01-11 | 2021-02-17 | 7 | M/S Danfoss | chemical / pharma | 1 | Pressure switch not working | null | closed | Replaced pressure switch
2021-03-31 | Multivista Global Pvt Ltd | null | D | Tcp LtdTamilnadu | null | KCX3 | 3374K2465 | 2551184746 | 2021-02-24 | 255118 | 2021-02-13 | v belt broken | 2020-12-31 | 2021-02-13 | 24 | Pix | chemical / pharma | 2 | Belts broken while fitment | null | closed | Replaced V belts
2021-04-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Yamunji Cold Storage | Mumbai | KCX4 | 3384K2427 | 2570424829 | 2021-03-27 | 257042 | 2021-03-27 | oil carry over | 2019-12-20 | 2020-03-02 | 1 | Inhouse | cold storage | 3 | Piston rings replaced | null | closed | Replaced Piston ring set
2021-04-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Areis Color Chem Pvt Ltd | Gujrat | KCX9 | 3404K157 | 2568504824 | 2021-03-25 | 256850 | 2021-03-25 | oil carry over | 2020-10-13 | 2020-10-23 | 3000 | Inhouse | ice plant | 1 | Replaced cylinder head cover and side cover gaskets | null | closed | Replaced cylinder head cover abd side cover gaskets
2021-04-19 | Parag Marketing Services | null | D | Gherade Agro Foods Pvt Ltd | Solapur | KCX51 | 3454K149 | 2567604834 | 2021-03-30 | 256760 | 2021-03-25 | delivery valve leakage | 2020-02-29 | 2021-03-26 | 6 | null | food processing | 13 | Delivery valve found leakage 02 nos. | null | closed | Delivery valve found leakage 02 nos.
2021-04-19 | Trade Links | null | D | Lnsk Greenhouse Agro Products | Andhra Pradesh | KCX3 | 3374K2413 | 2575124855 | 2021-04-07 | 257512 | 2021-04-07 | oil carryover piston crack | 2020-11-03 | 2021-02-04 | 862 | null | ice plant | 3 | Piston crack-2 nos | null | closed | Piston crack2 nos
2021-04-19 | Shree Engineering Services | null | D | Raj Ice Factory | Raipur, Chhatisgarh | PCX2 | 3106K0013 | 2569704852 | 2021-04-06 | 255970 | 2021-04-06 | stop valve leakage | 2019-11-05 | 2020-02-04 | 4300 | null | ice plant | 2 | Stop valve leakage and oil carryover problem | null | closed | Replaced stop valve
2021-04-19 | Fridge House | null | D | United Breweries Ltd | Karnataka | KCX6 | 3394K1433 | 2574904854 | 2021-01-06 | 257490 | 2021-04-09 | flywheel wobbling | 2019-11-19 | 2020-12-24 | 17 | null | chemical / pharma | 13 | Key replaced due to one side free fitting and another side tightened | null | closed | Replaced key
2021-04-19 | Multivista Global Pvt Ltd | null | D | Tcp Ltd Tamilnadu | null | KCX3 | 3374K2462 | 2573044844 | 2021-04-03 | 257304 | 2021-04-03 | kcx oil pump element tang broken | 2020-12-31 | 2021-01-23 | 1634 | null | chemical / pharma | 1 | KCX oil pump element tang broken | null | closed | Replaced KCX oil pump element
2021-04-20 | Kirloskar Pneumatic Co Ltd | Lucknow | D | Prakash Ice Factory | Uttar Pradesh | KC3 | 337K4793 | 2573924848 | 2021-04-05 | 257392 | 2021-04-05 | hour meter not working | 2020-01-31 | 2021-04-05 | 5 | null | ice plant | 4 | Replaced hour meter | null | closed | Hour meter
2021-04-20 | Trade Links | null | D | Sri Divya Joythi Ice & Cold Storage | Andhra Pradesh | KCX6 | 3394K1404 | 2565664803 | 2021-03-17 | 256566 | 2021-03-17 | oil carry over | 2019-09-29 | 2019-11-30 | 7175 | null | ice plant | 2 | Piston ring close gap incrased above 1.5mm,replaced cylinder liner-2 and piston ring sets-3 | null | closed | Piston ring sets and cylinder liner
2021-04-20 | Kirloskar Pneumatic Co Ltd | Lucknow | D | Prakash Ice Factory | Uttar Pradesh | KC3 | 337K4792 | 2574584849 | 2021-04-05 | 257458 | 2021-04-05 | pressure gauge not working | 2020-01-31 | 2021-04-05 | 5 | null | ice plant | 4 | Replaced pressure gauge | null | closed | Pressure gauge
2021-04-20 | Trade Links | null | D | Agrisol India Pvt Ltd | Andhra Pradesh | KCX9 | 3404K178 | 2571804856 | 2021-04-08 | 257180 | 2021-04-07 | retaining plate nut welding damaged | 2020-12-30 | 2021-04-07 | 6 | null | chemical / pharma | 4 | Retaining plate replaced due to nut welding broken | null | closed | Retaining plate
2021-04-30 | Cool Comfort Private Limited | West Bengal | D | S D Cold Sttorage | West Bengal | KCX4 | 3384K2661 | 2579184876 | 2021-04-19 | 257918 | 2021-04-19 | cylinder overheating | 2020-12-23 | 2021-03-12 | 630 | null | cold storage | 3 | Delivery valve kit broken | null | closed | Delivery valve kit
2021-04-30 | Trade Links | Goa | D | Nestle India Ltd | Goa | KCX6 | 3394K1465 | 2577284868 | 2021-04-15 | 257728 | 2021-04-14 | cylinder overheating | 2019-12-25 | 2021-01-02 | 2413 | null | food processing | 13 | Replaced delivery valve assly | null | closed | delivery valve assly
2021-04-30 | Trade Links | Secunderabad | D | Arman Ice Factory | null | KCX6 | 3394K1533 | null | null | null | 2021-04-30 | crank case leak near foot and shell joint due to crack | 2020-05-01 | 2020-11-06 | 2379 | null | ice plant | 6 | Crank case leak near foot and shell joint due to crack | null | closed | null
2021-04-30 | Geekay Pneumatic Pvt Ltd | null | D | Four Star Enterprises | Kerala | KC3 | 3374K4797 | 2577404870 | 2021-04-16 | 257740 | 2021-04-16 | oil carry over | 2020-06-26 | 2021-01-19 | 498 | null | ice plant | 7 | Replaced Piston ring set & VLD Orings | null | closed | Piston ring set & VLD Orings
2021-04-30 | Geekay Pneumatic Pvt Ltd | null | D | Carmaly Chilling Plant | Kerala | KCX2 | 3364K2071 | 2580364882 | 2021-04-22 | 258036 | 2021-04-22 | pressure gauge out | 2021-01-17 | 2021-04-22 | 4 | null | ice plant | 3 | Replaced Pressure gauge- 16 KG/Cm2 | null | closed | Pressure gauge 16 KG/Cm2
2021-04-30 | Trade Links | Secunderabad | D | Alladin Ice | Telangana | KCX2 | 3364K2067 | 2575824859 | 2021-04-09 | 257582 | 2021-04-09 | shaft seal leakage | 2021-01-10 | 2021-04-05 | 37 | null | ice plant | 3 | Oil leakage from shaft seal drain pipe,Freon gas application | null | closed | Shaft seal assly
2021-04-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kiri Industries | Vadodara , Gujarat | KCX9 | 3404K151 | 2574864850 | 2021-04-05 | 257486 | 2021-04-05 | cylinder overheating | 2020-02-29 | 2021-03-19 | 250 | null | chemical / pharma | 11 | Delivery valve found leakage , replaced valve kit | null | closed | Delivery valve kit
2021-04-30 | Fridge House | null | D | Basf India Ltd | Karnataka | KCX42 | 3444K228 | 2578984874 | 2021-04-19 | 257898 | 2021-04-17 | oil carry over | 2020-09-11 | 2021-01-05 | 915 | null | chemical / pharma | 4 | Piston ring set replaced -4 Nos. | null | closed | Piston ring set replaced 4 Nos.
2021-04-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2038 | 2572904841 | 2021-04-02 | 257290 | 2021-04-02 | oil pressure not buildup | 2020-11-03 | 2021-02-01 | 1275 | LDK | chemical / pharma | 4 | Oil pump tang broken | null | closed | Pump element
2021-04-30 | Geekay Pneumatic Pvt Ltd | null | D | Hindustan Organic Chemicals Limited | Kerala | KCX4 | 3384K2444 | 2572464866 | 2021-04-13 | 257246 | 2021-04-16 | solenoid valve not working | 2019-12-31 | 2020-07-13 | 980 | null | chemical / pharma | 7 | Replaced sol valve | null | closed | Sol valve
2021-04-30 | UAE | null | E | Natural Ice Factory | Uae | KCX6 | 3394K1416 | null | null | null | 2021-04-22 | piston crack | 2019-10-01 | null | null | Supplier | null | null | Pistons from cylinder numbers 1,2,4 & 5 had cracked | null | closed | null
2021-05-25 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Sk Cold Storage | Uttar Pradesh | KCX6 | 3394K1703 | 2584304909 | 2021-05-06 | 258430 | 2021-05-04 | compressor overheating | 2020-12-16 | 2021-03-18 | 323 | Inhouse | cold storage | 3 | Delivery valve leakage | null | closed | Discharge valve assembly1
2021-05-25 | Cool Comfort Private Limited | West Bengal | D | Dhupguri Cold Storage Ltd | West Bengal | KCX6 | 3394K1691 | 2582824898 | 2021-05-03 | 258282 | 2021-03-06 | abnormal noise from drive set | 2020-12-04 | 2021-03-24 | 115 | Supplier | cold storage | 3 | Flywheel side belt abnormal sound. | null | closed | V Belt 6 nos.
2021-05-25 | Cool Comfort Private Limited | West Bengal | D | Hemanta Cold Storage Ltd | West Bengal | KCX4 | 3384K2336 | 2586104919 | 2021-05-13 | 258610 | 2021-05-13 | high oil consumption | 2020-11-30 | 2021-02-19 | 727 | Inhouse | cold storage | 3 | Breather assly replaced | null | closed | Breather assly replaced
2021-05-25 | Cool Comfort Private Limited | West Bengal | D | Hemanta Cold Storage Ltd | West Bengal | KCX4 | 3384K2336 | 2580924885 | 2021-04-26 | 258092 | 2021-05-05 | high oil consumption | 2020-11-30 | 2021-02-19 | 695 | Inhouse | cold storage | 3 | Piston , liner & piston rings damaged. | null | closed | Piston 2, Liner1, Piston Rings 4 Gudgeon pin1 Bush1
2021-05-25 | Kalp Marketing | Gujrat | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3364K106 | 2583704925 | 2021-05-17 | 258370 | 2021-05-17 | high oil consumption | 2021-01-12 | 2021-03-31 | 170 | Supplier | dairy / ice cream | 3 | Replaced Piston ring set - 4 & ORV-2 | null | closed | Piston ring set4 & ORV2
2021-05-25 | Model Pneumatic Co | Punjab | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3364K107 | 2583724926 | 2021-05-17 | 258372 | 2021-05-17 | high oil consumption | 2021-01-12 | 2021-03-31 | 383 | Supplier | dairy / ice cream | 3 | Suction valve spring is broken , So replaced Piston ring set 7 . | null | closed | Piston ring set7 & Suction valve rings2
2021-05-25 | Parag Marketing Services | null | D | Dorle Dudh Sankalan Kendra | Maharashtra | KCX2 | 3364K2090 | 2579964897 | 2021-05-03 | 257996 | 2021-04-24 | op pressure switch malfunctioning | 2021-02-16 | 2021-04-24 | 10 | Supplier | dairy / ice cream | 2 | OP Pressure switch not working | null | closed | OP pressure switch
2021-05-25 | Multivista Global Pvt Ltd | null | D | Rvpp Ice Plant And Cold Storage | Tamil Nadu | KCX2 | 3364K2013 | 2580264886 | 2021-04-26 | 258026 | 2021-04-26 | high oil consumption | 2020-09-26 | 2020-11-15 | 2059 | Supplier | ice plant | 2 | Piston ring worn out | null | closed | Piston ring set2
2021-05-25 | Model Pneumatic Co | Punjab | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3364K103 | 2583744927 | 2021-05-17 | 258374 | 2021-05-17 | high oil consumption | 2021-01-12 | 2021-03-31 | 602 | Supplier | ice plant | 3 | Suction valve spring is broken , So replaced Piston ring set 3 . | null | closed | Piston ring set3 & Suction valve rings1
2021-05-25 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K388 | 2582904895 | 2021-05-02 | 258290 | 2021-05-02 | high oil consumption | 2020-07-12 | 2020-12-18 | 1746 | Supplier | meat/fish process | 5 | Open oil throw from all 9 cylinders. | null | closed | Piston ring set9
2021-05-25 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K382 | 2582664896 | 2021-05-02 | 258266 | 2021-04-29 | high oil consumption | 2020-06-20 | 2020-11-22 | 1756 | Supplier | meat/fish process | 5 | High oil consumption. Cyl no. 1,4,6&9 Piston rings replaced. | null | closed | Piston ring set5
2021-05-25 | Kalp Marketing | Gujrat | D | Msn Intermidaites Pvt LtdNaroda | Gujrat | KCX3 | 3374K2416 | 2587064928 | 2021-05-10 | 258706 | 2021-05-18 | high oil consumption piston crack | 2020-11-06 | 2020-11-20 | 831 | Supplier | chemical / pharma | 1 | Piston crack - 2 | null | closed | Piston crack 2
2021-05-29 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K2435 | Service email | 2021-05-29 | 258864 | 2021-05-24 | high oil consumption | 2021-02-01 | 2021-02-17 | PC | Inhouse | cold storage | 3 | Replaced VLD orings and ORV | null | closed | Replaced VLD orings and ORV
2021-05-29 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX42 | 3444K249 | 2588184939 | 2021-05-21 | 258818 | 2021-05-21 | high oil consumption | 2020-11-22 | 2021-05-03 | 854 | Supplier | meat/fish process | 1 | Replaced breather | null | closed | Breather assly replaced
2021-06-19 | Multivista Global Pvt Ltd | null | D | Hpmc | New Delhi | KC6 | 339K3607 | 2586564922 | 2021-05-15 | 258656 | 2021-05-14 | pressure gauge not working | 2020-12-30 | 2021-03-03 | 9 | Supplier | cold storage | 3 | Replaced pressure gauge 16 KG/CM2 | null | closed | pressure gauge
2021-06-19 | Kalp Marketing | Gujrat | D | Shree Gatral Dairy Food | Gujrat | KCX2 | 3364K2025 | 2587664936 | 2021-05-21 | 258766 | 2021-05-20 | solenoid valve not working | 2020-10-12 | 2021-04-28 | 11 | Supplier | dairy / ice cream | 6 | Replaced Sol valve | null | closed | Replaced Sol valve
2021-06-19 | Kalp Marketing | Gujrat | D | Shree Gatral Dairy Food | Gujrat | KCX2 | 3364K2023 | 2587644935 | 2021-05-21 | 258764 | 2021-05-20 | solenoid valve not working | 2020-10-12 | 2021-04-27 | 9 | Supplier | dairy / ice cream | 6 | Repalced Solenoid valve | null | closed | Solenoid valve
2021-06-19 | Kalp Marketing | Gujrat | D | Sahyog Ice Fatory | Gujrat | KCX4 | 3384K2585 | 2587184937 | 2021-05-21 | 258718 | 2021-05-20 | oil pressure not buildup | 2020-09-27 | 2020-10-24 | 888 | Supplier | ice plant | 1 | Replaced KCX oil pump element,gasket, O ring for OPR,Gasket for oil pump cover. | null | closed | KCX oil pump element,gasket, O ring for OPR,Gasket for oil pump cover.
2021-06-19 | Kalp Marketing | Gujrat | D | Sahyog Ice Fatory | Gujrat | KCX4 | 3384K2585 | 2588804949 | 2021-05-27 | 258880 | 2021-05-26 | overheatingpiston crack | 2020-09-27 | 2020-10-24 | 924 | Supplier | ice plant | 1 | Replaced piston,piston ring set,kit delivery valve,buffer spring. | null | closed | Replaced piston,piston ring set,kit delivery valve,buffer spring.
2021-06-19 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K387 | 2589064958 | 2021-05-30 | 258906 | 2021-06-04 | high oil carryover | 2020-07-06 | 2020-11-13 | 1966 | Supplier | meat/fish process | 4 | Replaced Piston ring set-9 nos | null | closed | Replaced piston ring sets9nos.
2021-06-19 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K384 | 2591904968 | 2021-06-05 | 259190 | 2021-06-07 | high oil carryover | 2020-06-30 | 2020-11-22 | 2246 | Supplier | meat/fish process | 5 | Replaced piston ring sets-9 nos. | null | closed | Replaced piston ring sets9nos.
2021-06-21 | Thailand | null | E | Ying Charoen Ice Co Ltd | null | KCX12 | 3415K0013 | 6 | 2021-06-12 | 6 | 2021-06-12 | kcx oil pump tang broken | 2020-09-16 | 2020-09-20 | 2900 | Supplier | ice plant | 1 | Replaced oil pump,paper filter,O ring,gasket. | null | closed | Replaced oil pump,paper filter,O ring,gasket.
2021-06-21 | Trade Links | null | D | Nifty Labs | Telangana | KCX2 | 3364K2054 | 2582744907 | 2021-05-06 | 258274 | 2021-05-05 | kcx low oil pressure | 2020-11-30 | 2021-05-05 | 8 | Supplier | chemical / pharma | 5 | Replaced oil pressure regulators | null | closed | Replaced oil pressure regulators
2021-06-21 | Trade Links | null | D | Ceyone Life Science Pvt Ltd | Andhra Pradesh | KCX6 | 3394K1656 | 2590464997 | 2021-06-18 | 259046 | 2021-01-18 | shaft seal leakage | 2020-10-26 | 2021-06-18 | 3 | Supplier | chemical / pharma | 8 | Replaced shaft seal assly due to leakage/ R22 gas application | null | closed | Replaced shaft seal assly
2021-06-22 | Parag Marketing Services | null | D | Wageshwari Milk Agro Products Services | Pune | KCX1 | 3354K155 | 2593824985 | 2021-06-12 | 259382 | 2021-06-11 | oil carry over | 2020-06-07 | 2021-04-28 | 488 | Supplier | dairy / ice cream | 10 | 2.5 Lit oil carryover within 63 Hrs. Piston rings wornout | null | closed | Replaced Piston ring set
2021-06-22 | Parag Marketing Services | null | D | Eco Farm Agro Products | Walse | KCX3 | 3374K2129 | 2552564905 | 2021-05-06 | 255256 | 2021-05-03 | knocking / abnormal sound | 2019-06-21 | 2020-01-14 | 3158 | Supplier | food processing | 6 | Replaced Cylinder liner , piston,del valve assly, buffer spring, | null | closed | Replaced Cylinder liner , piston,del valve assly, buffer spring,
2021-06-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K387 | 2594844990 | 2021-06-14 | 259484 | 2021-06-14 | abnormal noise | 2020-07-06 | 2020-11-13 | 2561 | Supplier | meat/fish process | 4 | Blank FSR | null | closed | Replaced Cylinder liner , piston, piston rings , gudgeon pin & bearings
2021-06-22 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Hma Agro Industries Ltd | Uttar Pradesh | KCX72 | 3474K383 | 2594804989 | 2021-06-14 | 259480 | 2021-06-14 | abnormal noise | 2020-06-20 | 2020-11-25 | 2191 | Supplier | meat/fish process | 5 | Blank FSR | null | closed | Replaced Cylinder liner , piston, piston rings , gudgeon pin & bearings
2021-06-23 | Multivista Global Pvt Ltd | null | D | Caharanjeet Ice Factory | Haryana | KCX4 | 3384K2614 | 2593604988 | 2021-06-14 | 259360 | 2021-06-16 | cylinder overheating | 2020-11-07 | 2021-03-20 | 314 | Supplier | ice plant | 4 | Delivery valve Spring broken | null | closed | Replaced valve kit
2021-06-29 | Kalp Marketing | Gujrat | D | Sahyog Ice Fatory | Gujrat | KCX4 | 3384K2585 | 2590224961 | 2021-06-02 | 259022 | 2021-06-01 | cylinder overheating | 2020-09-27 | 2020-10-24 | 929 | Supplier | ice plant | 1 | Delivery valve replaced due to valve seat damaged | null | closed | Replaced Del.Valve assly
2021-06-29 | Multivista Global Pvt Ltd | null | D | Swami Chickens | Tamil Nadu | KCX2 | 3364K1979 | 2596085009 | 2021-06-24 | 259608 | 2020-07-22 | tah8 valve and adaptor not supplied | 2020-07-22 | 2021-07-24 | 1 | Inhouse | meat/fish process | 12 | TAH8 valve and adaptor not supplied & control panel switch damaged | null | closed | Fitted TAH8 valve
2021-06-29 | Multivista Global Pvt Ltd | null | D | Swami Chickens | Tamil Nadu | KCX6 | 3394K1582 | 2596125010 | 2021-06-24 | 259612 | 2021-06-22 | tah8 valve and adaptor not supplied | 2020-07-22 | 2021-07-24 | 2 | Inhouse | meat/fish process | 12 | TAH8 valve and adaptor not supplied | null | closed | Fitted TAH8 valve
2021-06-29 | Gargi Engineering Enterprices Pvt Ltd | null | D | Gujarat Dyestuff Industries | Baruch,Gujarat | KCX4 | 3384K2707 | 2596445002 | 2021-06-21 | 259644 | 2021-06-28 | kcx oil pump tang broken | 2021-02-13 | 2021-06-05 | 2 | Supplier | chemical / pharma | 3 | KCX oil pump element tang broken | null | closed | Replaced KCX oil pump element
2021-06-30 | Model Pneumatic Co | Punjab | D | Shiva Cold Storage | Punjab | KCX3 | 3374K2410 | 2573145003 | 2021-06-21 | 257314 | 2021-04-03 | delivery valve leakage | 2020-10-30 | 2021-01-08 | 537 | Supplier | cold storage | 2 | Delivery valve leak,piston and piston ring damaged-liquid entry | null | closed | Delivery valve leak,piston and piston ring damagedliquid entry
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jkc General Trading Co | Mumbai | KCX3 | 3374K2168 | 2587704954 | 2021-05-30 | 258770 | 2021-05-19 | kcx oil pump tang broken | 2019-09-30 | 2021-05-19 | 9 | Supplier | cold storage | 19 | KCX Oil Pump tang broken & Pressure gauge not working | null | closed | Replaced Pump element & Pressure gauge 025Kg/cm2
2021-06-30 | Multivista Global Pvt Ltd | null | D | Bhawani Cold Storage Pvt Ltd | Uttar Pradesh | KCX3 | 3374K2494 | 2599905017 | 2021-06-28 | 259990 | 2021-06-30 | kcx oil pump tang broken | 2021-02-03 | 2021-03-02 | 1302 | Supplier | cold storage | 1 | Replaced KCX oil pump assly | null | closed | KCX oil pump assly
2021-06-30 | Trade Links | Secunderabad | D | Sai Sankar Cold Storage | Andhra Pradesh | KCX2 | 3364K2101 | 2586264917 | 2021-05-11 | 258626 | 2021-05-11 | pump air purging problem | 2021-02-28 | 2021-05-11 | 5 | Supplier | cold storage | 3 | Air purging problem , both regulators changed but problem not resolved. | null | closed | Replaced Pump assly & Both regulators
2021-06-30 | Kalp Marketing | Gujrat | D | Shree Gatral Dairy Food | Gujrat | KCX2 | 3364K2023 | 2595645001 | 2021-06-21 | 259564 | 2021-06-20 | kcx oil pump purging | 2020-10-12 | 2021-04-27 | PC | Supplier | dairy / ice cream | 6 | oil pump replaced due to purging | null | closed | KCX oil pump assly
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX72 | 3474K448 | 2587104982 | 2021-06-11 | 258710 | 2021-06-11 | krms panel issue | 2021-02-25 | 2021-05-02 | 550 | Supplier | food processing | 3 | Problem details not mentioned In FRR/FSR | null | closed | Replaced controller board.
2021-06-30 | Trade Links | Secunderabad | D | Veera Lakshami Krishna Ice Factory | Andhra Pradesh | KCX4 | 3384K2703 | 2583224908 | 2021-05-06 | 258322 | 2021-05-03 | error in pressure gauge | 2021-02-06 | 2021-05-03 | 5 | Supplier | ice plant | 3 | Error in suction pressure gauge | null | closed | Replaced pressure gauge 016Kg/cm2.
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Neotrend Chemical Pvt Ltd | Thane | KCX3 | 3374K2390 | 2580684955 | 2021-05-30 | 258068 | 2021-04-28 | piston crack | 2020-09-23 | 2020-10-17 | 2500 | Supplier | ice plant | 1 | Piston Crack & high oil carryover | null | closed | Replaced Piston 1
2021-06-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Asvini Fisheries Pvt Ltd | Tamil Nadu | KCX42 | 3444K271 | 2577384972 | 2021-06-07 | 257738 | 2021-06-06 | high oil carryover | 2021-02-27 | 2021-04-01 | 285 | Supplier | meat/fish process | 2 | Open oil throw from cylinders . | null | closed | Replaced piston ring sets 3 nos
2021-06-30 | Kirloskar Pneumatic Co Ltd | Uttar Pradesh | D | Hma Agro Industries | Uttar Pradesh | KCX72 | 3474K383 | 2590784963 | 2021-06-03 | 259078 | 2021-06-04 | high oil carryover | 2020-06-20 | 2020-11-22 | 2299 | Supplier | meat/fish process | 6 | Oil carryover problem | null | closed | Replaced All Piston ring sets
2021-06-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Tuticorin Alkali Chemicals & Fertilizers Ltd | Tamil Nadu | KCX12 | 3415K030 | 2586744933 | 2021-05-21 | 258674 | 2021-05-21 | cylinder overheating | 2021-03-17 | 2021-04-16 | 308 | Inhouse | chemical / pharma | 1 | Cylinder no.4 overheat due to delivary valve leakage. | null | closed | Replaced DV Assly
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Net Matrix Crop Care Limited | Gujrat | KCX6 | 3394K1602 | 2589424957 | 2021-05-30 | 258942 | 2021-05-28 | high oil carryover | 2020-07-08 | 2020-12-14 | 4500 | Supplier | chemical / pharma | 6 | One piston hair line crack & Oil throw | null | closed | Replaced Piston 1 & Piston ring set 1
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2037 | 2592244983 | 2021-06-11 | 259224 | 2021-06-23 | high oil consumptionpiston crack | 2020-11-03 | 2021-01-12 | 3070 | Supplier | chemical / pharma | 3 | Piston crack | null | closed | Replaced Piston1& DV Kit1
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2038 | 2587284940 | 2021-05-24 | 258728 | 2021-05-28 | high oil consumptionpiston crack | 2020-11-03 | 2021-02-01 | 2297 | Supplier | chemical / pharma | 3 | Piston crack | null | closed | Replaced Piston2
2021-06-30 | Trade Links | Secunderabad | D | Suven Life Seience Ltd | Vishakhapatanam | KCX2 | 3364K2109 | 2590944980 | 2021-06-10 | 259094 | 2021-06-04 | hour meter not working | 2021-03-08 | 2021-06-04 | 1 | Supplier | chemical / pharma | 3 | Hour meter not working | null | closed | Replaced Hour meter
2021-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Astec Life Science Ltd | Raigad | KCX42 | 3444K215 | 2589124956 | 2021-05-30 | 258912 | 2021-05-29 | kcx oil pump lp pressure not developed | 2020-07-26 | 2021-05-29 | 5 | Inhouse | chemical / pharma | 10 | LP Pressure not developed. Only HP Pressure develop up to 20 Kg/cm2... After field return pump analysis done found HP Regulatory rusty from inside & jammed. | null | closed | Replaced Pump assly
2021-07-17 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K2435 | 2588645046 | 2021-07-10 | 258864 | 2021-05-24 | high oil consumption | 2020-11-30 | 2021-02-17 | 1367 | Inhouse | cold storage | 3 | ORV leakage replaced | null | closed | Replaced ORV
2021-07-17 | Cool Comfort Private Limited | West Bengal | D | S D Cold Storage | West Bengal | KCX6 | 3394K1709 | 2605625051 | 2021-07-12 | 260562 | 2021-07-11 | kcx oil pump tang broken | 2020-12-22 | 2021-03-13 | 1548 | Supplier | cold storage | 3 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2021-07-17 | Trade Links | null | D | Aquatic Frozen Foods Global Private Ltd | Andhra Pradesh | KCX51 | 3454K180 | 2593564998 | 2021-06-19 | 259356 | 2021-06-20 | kcx oil pump tang broken | 2021-02-19 | 2021-04-17 | 445 | Supplier | cold storage | 2 | Replaced KCX oil pump element-1 | null | closed | Replaced KCX oil pump element1
2021-07-17 | Trade Links | null | D | Sneha Cold Strorage | Telangana | KCX3 | 3374K2473 | 2598045011 | 2021-06-25 | 259804 | 2021-06-24 | loading unloading problemsolenoid valve malfunctioning | 2021-01-16 | 2021-02-22 | 930 | Supplier | cold storage | 1 | Replaced solenoid valve-1 | null | closed | Replace solenoid valve1
2021-07-17 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K2434 | 2591704966 | 2021-06-04 | 259170 | 2021-06-04 | shaft seal leakage | 2020-11-30 | 2021-02-17 | 1263 | Inhouse | cold storage | 3 | Shaft seal leak due to heavy scoring on stationary sealing ring | null | closed | Replaced shaft seal assly
2021-07-17 | Trade Links | null | D | Vishnu Priya Ice Factory | Andhra Pradesh | KCX6 | 3394K1779 | 2596025004 | 2021-06-22 | 259602 | 2021-06-21 | high oil consumptionpiston ring set and liner worn out | 2021-03-19 | 2021-04-04 | 1584 | Inhouse | ice plant | 1 | Piston ring set and cylinder liner worn out | null | closed | Replaced piston and piston ring set
2021-07-17 | Trade Links | null | D | Sri Sai Indira Ice Factory | Telangana | KCX4 | 3384K2575 | 2592724995 | 2021-06-18 | 259272 | 2021-06-14 | high oil consumptionpiston crack | 2020-09-08 | 2020-09-19 | 5155 | Supplier | ice plant | 1 | Replaced piston-2,piston ring set-2 | null | closed | Replaced piston2,piston ring set2
2021-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Shree Jalaram Tube Ice | Gujrat | KCX4 | 3384K2587 | 2594205026 | 2021-07-03 | 259420 | 2021-06-23 | high oil consumptionpiston crack | 2020-09-29 | 2020-10-20 | 4450 | Supplier | ice plant | 1 | Replaced piston-1 piston ring set-1 | null | closed | Replaced piston1 piston ring set1
2021-07-17 | Cool Comfort Private Limited | West Bengal | D | Digha Sea Foods | West Bengal | KCX72 | 3474K379 | 2597285007 | 2021-06-24 | 259728 | 2021-06-22 | high oil consumption | 2020-06-16 | 2021-05-31 | 199 | Inhouse | meat/fish process | 1 | Replaced breather assly | null | closed | Replaced breather assly
2021-07-17 | Trade Links | null | D | S R Drugs & Intermidiates P Ltd | Telangana | KCX3 | 3374K2557 | 2607305061 | 2021-07-14 | 260730 | 2021-07-14 | shaft seal leakage | 2021-04-20 | 2021-06-10 | 738 | Supplier | chemical / pharma | 2 | Shaft seal leakage,Freon gas application | null | closed | Replaced Shaft seal assly1
2021-07-17 | Trade Links | null | D | Ceyone Life Science Pvt Ltd | Andhra Pradesh | KCX6 | 3394K1656 | 2590464997 | 2021-06-01 | 259046 | 2021-06-18 | shaft seal leakage | 2020-10-26 | 2021-06-18 | 3 | Supplier | chemical / pharma | 8 | Replaced shaft seal assly leakage while commissioning freon gas-1 | null | closed | Replaced shaft seal assly1
2021-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jay Chemicals | Vapi, Gujarat | KCX3 | 3374K2137 | 2597065027 | 2021-07-03 | 259706 | 2021-06-28 | cylinder overheatingpiston crack | 2019-06-30 | 2020-02-11 | 4600 | Supplier | chemical / pharma | 8 | Replaced piston-1,piston ring set-1 | null | closed | Replaced piston1,piston ring set1
2021-07-17 | Trade Links | null | D | Valentis Laboratories Pvt Ltd | Telangana | KCX6 | 3394K1630 | 2596685021 | 2021-07-01 | 259668 | 2021-06-30 | tah8 valve and adaptor not supplied | 2020-08-29 | 2021-06-30 | 2 | Supplier | chemical / pharma | 10 | TAH8 valve not received | null | closed | null
2021-07-17 | Gargi Engineering Enterprices Pvt Ltd | null | D | Transpek Silox Inductries Pvt Ltd | Gujrat | KCX4 | 3384K2542 | 2600325022 | 2021-07-01 | 260032 | 2021-07-01 | high oil consumptionpiston crack | 2020-07-14 | 2020-09-25 | 214 | Supplier | chemical / pharma | 2 | Piston crack-1no.,piston ring set-4 replaced | null | closed | Piston crack1no.,piston ring set4 replaced
2021-07-26 | Hss Solution Pvt Ltd | null | D | Shree Maruti Chilling Udyaog | Rajastan | KCX2 | 3364K2139 | 2595845070 | 2021-07-17 | 259584 | 2021-06-17 | cylinder overheating | 2021-04-27 | 2021-05-29 | 173 | Inhouse | dairy / ice cream | 1 | Replaced piston,piston ring set, delivery valve assly,suction valve ring and spring,bush con rod. | null | closed | Replaced piston,piston ring set, delivery valve assly,suction valve ring and spring,bush con rod.
2021-07-26 | Hss Solution Pvt Ltd | null | D | Ssm Chilling Plant | Rajastan | KCX2 | 3364K2094 | 2597605076 | 2021-07-19 | 259760 | 2021-07-06 | ip toggle switch malfunctioning | 2021-02-24 | 2021-02-24 | 2 | Supplier | dairy / ice cream | 5 | IP toggle switch not working properly. | null | closed | Replaced IP toggle switch
2021-07-26 | Model Pneumatic Co | Punjab | D | Choice Agros Pvt Ltd | Punjab | KCX1 | 3354K205 | 2606105053 | 2021-07-12 | 260610 | 2021-07-12 | shaft seal leakage | 2021-05-29 | 2021-06-21 | 24 | Supplier | food processing | 1 | Shaft seal leakage R22 application | null | closed | Replaced Shaft seal assly
2021-07-26 | Trade Links | null | D | Sri Ayyappa Ice Factory | Andhra Pradesh | KCX4 | 3384K2772 | 2596865013 | 2021-06-28 | 259686 | 2021-06-24 | abnormal noise | 2021-05-12 | 2021-05-21 | 681 | Inhouse | ice plant | 1 | Replaced cylinder liner,piston,piston ring set, gudgeon pin,bush con rod, del valve assly. | null | closed | Replaced cylinder liner,piston,piston ring set, gudgeon pin,bush con rod, del valve assly.
2021-07-26 | Kalp Marketing | Gujrat | D | Natraj Industries | Gujrat | KCX6 | 3394K1785 | 2609025077 | 2021-07-20 | 260902 | 2021-07-19 | cylinder overheating | 2021-03-26 | 2021-07-10 | 139 | Inhouse | ice plant | 3 | Replaced delivery valve assly | null | closed | Replaced delivery valve assly
2021-07-26 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX6 | 3394K1518 | 2599485014 | 2021-06-28 | 259948 | 2021-06-28 | kcx oil pump tang broken | 2020-02-29 | 2020-07-13 | 3292 | Supplier | ice plant | 4 | Replaced pump element | null | closed | Replaced pump element
2021-07-26 | Trade Links | null | D | Avanti Frozen Foods Pvt Ltd | Andhra Pradesh | KCX63 | 3464K108 | 2604045042 | 2021-07-08 | 260404 | 2021-07-08 | kcx oil pump tang broken | 2021-01-13 | 2021-06-21 | 99 | Supplier | ice plant | 5 | Replaced pump element | null | closed | Replaced pump element
2021-07-26 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX42 | 3444K233 | 2605325048 | 2021-07-10 | 260532 | 2021-07-10 | cylinder overheating | 2020-09-20 | 2021-01-14 | 1706 | Inhouse | meat/fish process | 3 | Cylinder overheating and high oil consumption replaced delivery valve kit,piston,liner,piston ring set. | null | closed | Cylinder overheating and high oil consumption replaced delivery valve kit,piston,liner,piston ring set.
2021-07-26 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX42 | 3444K249 | 2608365066 | 2021-07-17 | 260836 | 2021-07-16 | cylinder overheatingpiston crack | 2020-11-22 | 2021-05-03 | 2096 | Supplier | meat/fish process | 6 | Replaced piston,piston ring set,gudgeon pin-1 | null | closed | Replaced piston,piston ring set,gudgeon pin1
2021-08-02 | Kalp Marketing | Gujrat | D | Mahaveer Agri Cold | Gujrat | KCX2 | 3364K2046 | 2609825084 | 2021-07-22 | 260982 | 2021-07-21 | abnormal noise | 2020-11-24 | 2021-03-09 | 2187 | Supplier | cold storage | 4 | Piston ring set & liner wornout | null | closed | Replaced Liner1 & Piston ring set1
2021-08-02 | Model Pneumatic Co | Punjab | D | Kochar Cold Storage | Punjab | KCX3 | 3374K2577 | 2611385090 | 2021-07-26 | 261138 | 2021-07-24 | delivery valve leakage | 2021-06-15 | 2021-07-15 | 99.2 | Inhouse | cold storage | 1 | Delivery valve leakage & Ring springs broken. | null | closed | Replaced DV assly
2021-08-02 | Kalp Marketing | Gujrat | D | Kitchen Express Overseas Limited | Gujrat | KCX42 | 3444K257 | 2601245024 | 2021-07-02 | 260124 | 2021-07-02 | pressure gauge malfunctioning | 2020-12-25 | 2021-06-28 | 5 | Supplier | food processing | 6 | Discharge pressure gauge 0-25Kg/cm2 stuck & 0 not matching. | null | closed | Replaced discharge pressure gauge 025Kg/cm2
2021-08-02 | Trade Links | Secunderabad | D | Dhanalakshmi Ice Factory | Andhra Pradesh | KCX4 | 3384K2760 | 2608645069 | 2021-07-17 | 260864 | 2021-07-17 | abnormal noise delivery valve leakage | 2021-03-31 | 2021-06-29 | 365 | Inhouse | ice plant | 3 | Abnormal sound . Piston seized . Delivery valve back leakage & Small ring broken. | null | closed | Replaced Liner , Piston , Piston ring set , Delivery valve etc
2021-08-02 | Multivista Global Pvt Ltd | null | D | Murugan Ice Factory | Tamil Nadu | KCX2 | 3364K2095 | 2605285082 | 2021-07-21 | 260528 | 2021-07-10 | kcx oil pump purging | 2021-02-24 | 2021-04-23 | 602 | Supplier DE DE1339A21 | ice plant | 3 | Oil pump purging issue | null | closed | Replaced pump assly
2021-08-02 | Trade Links | Secunderabad | D | Sathvi Ice Industries | Andhra Pradesh | KCX2 | 3364K2111 | 2605665065 | 2021-07-17 | 260566 | 2021-07-16 | kcx oil purging problem | 2021-03-10 | 2021-06-26 | 414 | SupplierLC | ice plant | 3 | Air purging problem | null | closed | Replaced pump assembly
2021-08-02 | Kalp Marketing | Gujrat | D | Balaji Industries | Gujrat | KCX3 | 3374K2195 | 2609845085 | 2021-07-22 | 260984 | 2021-07-22 | knocking soundpiston crack | 2019-11-22 | 2020-01-20 | 6717 | Supplier | chemical / pharma | 2 | Replaced piston-1 | null | closed | Replaced Piston1
2021-08-02 | Model Pneumatic Co | Punjab | D | Cadchem Laboratories | Punjab | KCX3 | 3374K2482 | 2608465067 | 2021-07-17 | 260846 | 2021-07-16 | shaft seal leakage | 2021-01-20 | 2021-07-13 | 5 | Supplier | chemical / pharma | 7 | Shaft seal leakage . Site analysis missing. Gas R22 | null | closed | Replaced shaft seal assly
2021-08-25 | Cool Comfort Private Limited | West Bengal | D | Kundu Cold Storage | null | KCX6 | 3394K1727 | 2617305109 | 2021-08-07 | 261730 | 2021-08-06 | discharge valve leakvalve kit broken | 2021-01-13 | 2021-03-18 | 2402 | Inhouse | cold storage | 3 | Replaced valve kit due to broken | null | closed | Replaced valve kit due to broken
2021-08-25 | Kalp Marketing | Gujrat | D | Jay Ambe Himghar Pvt Ltd | Gujrat | KCX4 | 3384K2691 | 2606325073 | 2021-07-19 | 260632 | 2021-07-17 | high oil consumption | 2021-01-24 | 2021-02-19 | 1448 | Inhouse | cold storage | 1 | Replaced cylinder liner & Piston ring sets | null | closed | Replaced cylinder liner & Piston ring sets
2021-08-25 | Multivista Global Pvt Ltd | null | D | Shree Jee Food Products | Haryana | KCX4 | 3384K2553 | 2616925107 | 2021-08-05 | 261692 | 2021-08-05 | pressure gauge not working | 2020-08-08 | 2021-02-27 | 212 | Supplier | cold storage | 7 | Replaced pressure gauge | null | closed | Replaced pressure gauge
2021-08-25 | Trade Links | Secunderabad | D | Kurnool Dist Milk Producers Mutually Aided Co-Op Union Ltd | Andhra Pradesh | KCX2 | 3364K2114 | 2615725105 | 2021-08-05 | 261572 | 2021-08-04 | kcx oil pump purging | 2021-03-12 | 2021-06-23 | 480 | Supplier | dairy / ice cream | 3 | Replaced KCX oil pump assly | null | closed | Replaced KCX oil pump assly
2021-08-25 | Kalp Marketing | Gujrat | D | Shree Yadav Milk | Madhya Pradesh | KCX2 | 3364K1976 | 2612505096 | 2021-07-29 | 261250 | 2021-07-29 | kcx oil pump tang broken | 2020-07-05 | 2020-10-13 | 732 | SupplierM/S LDK | dairy / ice cream | 3 | KCX oil punp tang broken | null | closed | Replaced KCX oil pump element
2021-08-25 | Trade Links | Secunderabad | D | Nestle India Ltd | Goa | KCX6 | 3394K1465 | 2612765103 | 2021-08-02 | 261276 | 2021-07-29 | oil carry over | 2019-12-25 | 2021-01-02 | 4553 | Inhouse | food processing | 13 | Replaced ORV,VLD Orings. | null | closed | Replaced ORV,VLD Orings.
2021-08-25 | Trade Links | Secunderabad | D | Lnsk Greenhouse Agro Products | Andhra Pradesh | KCX3 | 3374K2413 | 2605765058 | 2021-07-13 | 260576 | 2021-07-13 | piston crack | 2020-11-03 | 2021-02-04 | 2604 | Supplier | ice plant | 3 | Replaced Piston-1 and piston ring sets-3 | null | closed | Replaced Piston1 and piston ring sets3
2021-08-25 | Kalp Marketing | Gujrat | D | Ramdev Enterprises | null | KCX4 | 3384K2794 | 2621385141 | 2021-08-19 | 262138 | 2021-08-18 | suction strainer element damaged. | 2021-06-23 | 2021-08-18 | 3 | Inhouse | ice plant | 2 | Suction strainer element fitted | null | closed | Suction strainer element fitted
2021-08-25 | Kalp Marketing | Gujrat | D | M G Exports | Gujrat | KCX93 | 3485K088 | 2624285151 | 2021-08-21 | 262428 | 2021-08-21 | control panel leakage | 2020-07-18 | 2021-07-27 | 2 | Supplier | meat/fish process | 12 | Replaced control panel box | null | closed | Replaced control panel box
2021-08-25 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Al Halal International Pvt Ltd | Uttar Pradesh | KCX72 | 3474K381 | 2609405124 | 2021-08-13 | 260940 | 2021-08-12 | oil carry over | 2020-06-17 | 2020-08-21 | 4669 | Inhouse | meat/fish process | 3 | Replaced piston ting sets-9 Nos. | null | closed | Replaced piston ting sets9 Nos.
2021-08-25 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX3 | 3374K2423 | 2620705127 | 2021-08-13 | 262070 | 2021-08-13 | piston crack | 2020-11-22 | 2021-06-25 | 870 | SupplierLubricare | meat/fish process | 7 | Piston crack | null | closed | Replaced Piston1No
2021-08-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Elpee Chemicals Pvt LtdRaigad | Maharashtra | KCX2 | 3364K2133 | 2597505028 | 2021-07-03 | 259750 | 2021-06-29 | oil pressure switch problem | 2021-04-17 | 2021-06-13 | 16 | Supplier | chemical / pharma | 2 | Replaced OP Pressure switch | null | closed | OP Pressure switch
2021-08-25 | Trade Links | Secunderabad | D | S R Drugs & Intermidiates P Ltd | Telangana | KCX3 | 3374K2557 | 2593285030 | 2021-07-03 | 259328 | 2021-06-10 | pressure gauge not working | 2021-04-20 | 2021-06-10 | 19 | Supplier | chemical / pharma | 2 | Replaced pressure gauge | null | closed | Replaced pressure gauge
2021-08-31 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K2435 | 2590884969 | 2021-06-05 | 259088 | 2021-06-05 | abnormal noise | 2020-11-30 | 2021-02-17 | 1481 | Inhouse | cold storage | 3 | Replaced cylinder liner and piston ring set due to wornout | null | closed | Replaced cylinder liner and piston ring set due to wornout
2021-08-31 | Multivista Global Pvt Ltd | null | D | Gupta Industries | Uttar Pradesh | KCX51 | 3454K170 | 2596845005 | 2021-06-22 | 259684 | 2021-06-24 | abnormal noise | 2020-12-30 | 2021-03-20 | 866 | Inhouse | dairy / ice cream | 3 | Replaced cylinder liner & piston ring set due to wornout | null | closed | Replaced cylinder liner & piston ring set due to wornout
2021-08-31 | Model Pneumatic Co | Punjab | D | Asianlak Health Foods Ltd | Punjab | KCX31 | 3434K0150 | 2588704943 | 2021-05-24 | 258870 | 2021-05-24 | delivery valve leakage | 2019-06-30 | 2020-05-14 | 2023 | Inhouse | food processing | 11 | Replaced delivery valve kit | null | closed | Replaced delivery valve kit
2021-08-31 | Trade Links | Secunderabad | D | Ananda Fisheries | Andhra Pradesh | KCX6 | 3394K1634 | 2618885130 | 2021-08-14 | 261888 | 2021-08-14 | oil carry over | 2020-09-15 | 2020-12-17 | 4720 | Inhouse | ice plant | 3 | Replaced piston-4,piston ring sets,VLD orings | null | closed | Replaced piston4,piston ring sets,VLD orings
2021-08-31 | Cool Comfort Private Limited | West Bengal | D | Digha Sea Foods | West Bengal | KCX72 | 3474K379 | Service email | 2021-09-01 | null | 2021-09-01 | rms device not working | 2020-06-16 | 2021-05-31 | 250 | Supplier | ice plant | 12 | Device called back for repair and return. | null | null | Device called back for repair FROM SUPPLIER and return.
2021-08-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Satish Ice Factory | Gujrat | KCX6 | 3394K1651 | 2605225047 | 2021-08-10 | 260522 | 2021-08-17 | solenoid valve malfuctioning | 2020-10-06 | 2020-12-25 | 2777 | Supplier | ice plant | 2 | Replaced 2 solenoid valves . Teflon was broken & spring free in plunger. | null | closed | Replaced 2 plungers
2021-08-31 | Cool Comfort Private Limited | West Bengal | D | Sadaf Sea Foods | West Bengal | KCX72 | 3474K348 | 2611665093 | 2021-07-27 | 261166 | 2021-07-27 | abnormal noise | 2019-12-28 | 2021-06-10 | 2304 | Inhouse | meat/fish process | 8 | Replaced piston ring set,liner,piston due to wornout. | null | closed | Replaced piston ring set,liner,piston due to wornout.
2021-08-31 | Kalp Marketing | Gujrat | D | M G Exports | Gujrat | KCX93 | 3485K089 | 2617645116 | 2021-08-09 | 261764 | 2021-08-08 | delivery valve leakage | 2021-07-11 | 2021-07-29 | 2 | Inhouse | meat/fish process | 1 | Replaced delivery valve kit and pressure gauge | null | closed | Replaced delivery valve kit and pressure gauge
2021-08-31 | Cool Comfort Private Limited | West Bengal | D | Digha Sea Foods | West Bengal | KCX72 | 3474K379 | 2818625117 | 2021-08-10 | 281862 | 2021-08-09 | high oil carryover | 2020-06-16 | 2021-05-31 | 290 | Inhouse | meat/fish process | 11 | Replaced breather assly-3Nos. | null | closed | Replaced breather assly3Nos.
2021-08-31 | Robin Refrigeration Works | Odisha | D | Orchid Marine Exports Pvt Ltd | Odisha | KCX51 | 3454K164 | 2605805062 | 2021-07-15 | 260580 | 2021-07-15 | shaft seal leakage | 2020-10-19 | 2021-06-13 | 55 | Inhouse | meat/fish process | 8 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2021-09-19 | Multivista Global Pvt Ltd | null | D | Baba Cold Storage | Uttar Pradesh | KC6 | 339K3595 | 2624445169 | 2021-08-28 | 262444 | 2021-08-24 | oil pump issue | 2020-02-29 | null | 149 | Supplier | cold storage | null | Complaint details not mentioned in FRR & FSR. As per FSR , this compressor is out of warranty & oil pump replaced on goodwill basis . | null | closed | Replaced pump assly
2021-09-19 | Multivista Global Pvt Ltd | null | D | Sharma Enterprises | Uttar Pradesh | KCX3 | 3374K2533 | 2627465175 | 2021-08-30 | 262746 | 2021-09-01 | cylinder overheating | 2021-03-12 | 2021-04-24 | 375 | Supplier | dairy / ice cream | 1 | Delivery valve assembly leakage. | null | closed | Replaced delivery valve assly
2021-09-19 | Geekay Pneumatic Pvt Ltd | null | D | Jeevodaya Milk Products | Kerala | KCX2 | 3364K2147 | 2624545153 | 2021-08-24 | 262454 | 2021-08-22 | cylinder overheating & abnormal sound | 2021-06-02 | 2021-08-09 | 42 | Supplier | dairy / ice cream | 2 | Delivery valve assembly leakage , stroke limitor wornout | null | closed | Replaced delivery valve assly
2021-09-19 | Kalp Marketing | Gujrat | D | Nestle India Ltd | Gujrat | KCX4 | 3384K2634 | 2624245159 | 2021-08-25 | 262424 | 2021-08-24 | oil carry over | 2020-12-11 | 2021-07-17 | 391 | Inhouse | food processing | 7 | Cylinder no. 2& 4 ORV found chocked | null | closed | Replaced ORV
2021-09-19 | Trade Links | null | D | Vishwanandha Ice Factory | Andhra Pradesh | KCX4 | 3384K2627 | 2618785122 | 2021-08-12 | 261878 | 2021-08-12 | abnormal noise | 2020-11-29 | 2021-01-08 | 2875 | Inhouse | ice plant | 3 | Found 1 & 3 Pistons in seized condition due to delivery valve leakages. | null | closed | Replaced cylinder assly
2021-09-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K324 | 2633085222 | 2021-09-13 | 263308 | 2021-09-11 | krms issue no link showing in display | 2019-09-23 | 2021-01-01 | 1199 | Supplier | ice plant | 16 | Controller card was not working. Replaced & working ok | null | closed | Replaced controller board.
2021-09-19 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX6 | 3394K1518 | 2617185115 | 2021-08-09 | 261718 | 2021-08-07 | oil carry over | 2020-02-29 | 2020-07-13 | 992 | Inhouse | ice plant | 5 | Piston rings wornout & VLD Orings shape changed | null | closed | Replaced Piston ring set2 & VLD Orings 6
2021-09-19 | Trade Links | null | D | Ind Union Foods Ltd | Andhra Pradesh | KCX6 | 3394K1706 | 2630345197 | 2021-09-06 | 263034 | 2021-09-04 | oil carry over | 2020-12-30 | 2021-04-09 | 2710 | Inhouse | ice plant | 4 | Cyl no. 2 & 3 delivery valve back leakage resulted to cylinder seized. | null | closed | Replaced cylinder assly
2021-09-19 | Kalp Marketing | Gujrat | D | Gold Fish Ice Factory | Daman & Diu | KCX6 | 3394K1812 | 2626765172 | 2021-08-28 | 262676 | 2021-08-28 | oil pressure not buildup | 2021-07-07 | 2021-08-18 | 2 | Supplier | ice plant | 1 | Pump element broken within 2 hours. | null | closed | Replaced pump element
2021-09-19 | Geekay Pneumatic Pvt Ltd | null | D | Petropill Ice Products | Kerala | KCX3 | 3374K2493 | 2611745100 | 2021-07-30 | 261174 | 2021-07-30 | suction pressure gauge out & glass bulge | 2021-02-02 | 2021-07-30 | 1 | Supplier | ice plant | 5 | Suction gauge out & glass bulge - Old complaint July complaint registered in Sep. Also as per FRR Remark piercing not done. | null | closed | Replaced suction pressure gauge.
2021-09-19 | Cool Comfort Private Limited | West Bengal | D | Shimpo ExportsPvt Ltd | West Bengal | KCX72 | 3474K338 | 2628425177 | 2021-08-31 | 262842 | 2021-08-31 | abnormal noise | 2019-12-21 | 2020-06-13 | 3689 | Inhouse | meat/fish process | 6 | Cylinder no.4 liner cut marks & piston rings wornout | null | closed | Replaced liner1 & Piston ring set2
2021-09-19 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX42 | 3444K233 | 2625505157 | 2021-08-24 | 262550 | 2021-08-24 | oil carry over | 2020-09-20 | 2021-01-14 | 2882 | Inhouse | meat/fish process | 4 | Complaint analysis not mentioned in FSR. Breather assembly changed | null | closed | Replaced breather assly.
2021-09-19 | Geekay Pneumatic Pvt Ltd | null | D | Nas Fisheries Pvt Ltd | Kerala | KCX72 | 3474K372 | 2622145146 | 2021-08-20 | 262214 | 2021-08-19 | oil carry over | 2020-03-13 | 2020-12-19 | 2157 | Supplier | meat/fish process | 3 | Open oil throw observed & Piston rings wornout | null | closed | Replaced Piston ring set4
2021-09-19 | Kalp Marketing | Gujrat | D | Crystal Quinone Pvt Ltd | Gujrat | KCX4 | 3384K2365 | 2627265171 | 2021-08-28 | 262726 | 2021-08-28 | cylinder overheating | 2019-10-19 | 2020-09-24 | 557 | Inhouse | chemical / pharma | 11 | Cylinder no. 2 delivery valve leakage resulted to cylinder overheating. | null | closed | Replaced DV Kit
2021-09-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Hari Orgo Chem Pvt Ltd | Gujrat | KCX6 | 3394K1633 | 2629745186 | 2021-09-03 | 262974 | 2021-09-02 | oil carry over piston crack | 2020-09-07 | 2020-11-10 | PC | Inhouse | chemical / pharma | 2 | Cylinder no.3 found piston crack & Piston rings wornout | null | closed | Replaced piston & Piston ring set1
2021-09-24 | Shree Engineering Services | null | D | BRCold Storage Pvt Ltd | Chhattisgarh | KCX4 | 3384K2648 | 2598745182 | 2021-09-01 | 259874 | 2021-09-01 | oil carry over | 2020-12-11 | 2021-01-13 | 618 | Inhouse | cold storage | 1 | Replaced piston ring set-2 nos. | null | closed | Replaced piston ring set2 nos.
2021-09-24 | Shree Engineering Services | null | D | Jagganath Herbal And Foods Pvt Ltd | Raipur, Chhatisgarh | KCX4 | 3384K2481 | 2593505164 | 2021-08-26 | 259350 | 2021-06-10 | oil carry over | 2020-02-07 | 2021-05-11 | 358 | Inhouse | cold storage | 15 | Piston rings , vld orings and orv changed | null | closed | Piston rings , vld orings and orv changed
2021-09-24 | Robin Refrigeration Works | Odisha | D | Sree Radhe Keshav Cold Storage | Odisha | KCX3 | 3374K2500 | 2622885137 | 2021-08-18 | 262288 | 2021-08-18 | shaft seal leakage | 2021-02-05 | 2021-04-06 | 902 | Supplier | cold storage | 2 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2021-09-24 | Kalp Marketing | Gujrat | D | Jay Shree Gayatri Food Products | Madhya Pradesh | KCX51 | 3454K162 | 2631805224 | 2021-09-13 | 263180 | 2021-09-12 | kcx oil pump tang broken | 2020-10-16 | 2021-07-14 | 240 | Supplier | dairy / ice cream | 9 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2021-09-24 | Multivista Global Pvt Ltd | null | D | Kvg Agro Pvt Ltd | Haryana | KCX2 | 3364K2092 | 2633545214 | 2021-09-09 | 263354 | 2021-09-02 | kcx oil pump tang broken | 2021-02-20 | 2021-08-29 | 63 | Inhouse | dairy / ice cream | 6 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2021-09-24 | Model Pneumatic Co | Punjab | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3464K107 | 2633105217 | 2021-09-10 | 263310 | 2021-09-09 | oil carry over | 2021-01-17 | 2021-03-31 | 1666 | Inhouse | dairy / ice cream | 2 | Replaced piston, liner,piston ring set | null | closed | Replaced piston, liner,piston ring set
2021-09-24 | Parag Marketing Services | null | D | Manegrow Agrow Products | Maval, Maharashtra | KCX12 | 3415K021 | 2600025160 | 2021-08-25 | 260002 | 2021-07-05 | kcx oil pump tang broken | 2021-02-12 | 2021-05-26 | 563 | Supplier | food processing | 3 | Replaced oil pump element | null | closed | Replaced oil pump element
2021-09-24 | Kalp Marketing | Gujrat | D | Hari Om Ice And Cs | Gujrat | KCX6 | 3394K1807 | 2629845200 | 2021-09-06 | 262984 | 2021-09-06 | hp pressure gauge not working | 2021-06-25 | 2021-08-28 | 77 | Supplier | ice plant | 2 | Replaced pressure gauge 25 kg/ cm2 | null | closed | Replaced pressure gauge 25 kg/ cm2
2021-09-24 | Kalp Marketing | Gujrat | D | Jay Sadguru Ice Factory | Gujrat | KCX4 | 3384K2820 | 2632185204 | 2021-09-07 | 263218 | 2021-09-06 | kcx oil pump tang broken | 2021-07-24 | 2021-09-01 | 45 | Supplier | ice plant | 2 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2021-09-24 | Geekay Pneumatic Pvt Ltd | null | D | Marain Ice Factory | Kerala | KCX4 | 3384K2504 | 2626465166 | 2021-08-27 | 262646 | 2021-08-26 | oil carry over | 2020-02-25 | 2020-06-16 | 5206 | Inhouse | ice plant | 4 | Replaced piston,liner,piston ring set. | null | closed | Replaced piston,liner,piston ring set.
2021-09-24 | Kalp Marketing | Gujrat | D | Ocean Aquatech Product | Gujrat | KCX72 | 3374K456 | 2628705198 | 2021-09-06 | 262870 | 2021-09-05 | op pressure switch malfunctioning | 2021-03-27 | 2021-09-05 | 2 | Supplier | meat/fish process | 6 | Replaced OP Pressure switch | null | closed | Replaced OP pressure switch
2021-09-24 | Trade Links | null | D | DrReaddy Laboratory | Andhra Pradesh | KCX63 | 3464K083 | 2624685155 | 2021-08-24 | 262468 | 2021-08-22 | kcx oil pump tang broken | 2020-08-11 | 2021-04-12 | 2899 | Supplier | chemical / pharma | 8 | Replaced oil pump element | null | closed | Replaced oil pump element
2021-09-30 | Multivista Global Pvt Ltd | Gurgaon | D | Sundar Cold Storage | Uttar Pradesh | KCX6 | 3394K1758 | 2623705220 | 2021-09-13 | 262370 | 2021-09-10 | oil carry over | 2021-02-26 | 2021-05-04 | 1254 | Inhouse | cold storage | 3 | Cylinder no. 1,2,4&5 observed liner cut marks & cyl no. 3&6 Piston rings wornout. | null | closed | Replaced Cylinder liner 4 , Piston 4 & Piston ring set 6
2021-09-30 | Model Pneumatic Co | Punjab | D | Rai Poultries | Punjab | KCX31 | 3434K0141 | 2634625216 | 2021-09-10 | 263462 | 2021-09-10 | oil pressure not buildup | 2020-08-28 | 2021-06-18 | 292 | Supplier LC | cold storage | 10 | LP Oil pressure not develop due to drive shaft & bearing jammed. | null | closed | Replaced pump assly LC 04 21 12
2021-09-30 | Trade Links | Secunderabad | D | The Krishna District Milk Co-Operative Union | Andhra Pradesh | KCX9 | 3404K148 | Service email | 2021-10-01 | 263794 | 2021-09-17 | oil carry over | 2019-12-10 | 2020-08-10 | 2201 | null | dairy / ice cream | 8 | Breather assly changed | null | closed | Breather assly changed
2021-09-30 | Model Pneumatic Co | Himachal Pradesh | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3464K106 | 2629365218 | 2021-09-10 | 262936 | 2021-09-09 | oil carry over & overheating | 2021-01-12 | 2021-03-31 | 1369 | null | dairy / ice cream | 3 | Safety valve bypass , cylinder no. 5&6 overheating . | null | closed | Replaced Liner 3 , Piston3 , Piston ring set 3 , Spring SV , Gudgeon pin 2 , Bearings etc.
2021-09-30 | Kalp Marketing | Gujrat | D | Nestle India Ltd | Gujrat | KCX4 | 3384K2634 | 2629465203 | 2021-09-07 | 262946 | 2021-09-06 | high oil consumption | 2020-12-11 | 2021-07-17 | 347 | Inhouse | food processing | 7 | Cylinder no. 2&4 observed open oil throw. Piston rings slightly wornout. | null | closed | Replaced Piston ring sets2
2021-09-30 | Kalp Marketing | Gujrat | D | Anjani Putra Marketing | Veraval, Gujarat | KCX4 | 3384K2551 | 2637005253 | 2021-09-23 | 263700 | 2021-09-20 | high oil consumption | 2020-08-02 | 2020-11-27 | 2619 | Inhouse | ice plant | 3 | Cylinder no.3 ORV Blocked, All VLD Orings found flatened . | null | closed | Replaced ORV & Orings.
2021-09-30 | Robin Refrigeration Works | Odisha | D | B-One Buisness House Pvt Ltd | Bhubaneswar Orissa | KCX6 | 3394K1617 | 2628005221 | 2021-09-13 | 262800 | 2021-09-20 | oil carry over piston crack | 2020-08-07 | 2020-12-26 | 1200 | Inhouse | ice plant | 4 | All 6 piston found crack . | null | closed | Replaced Piston , Piston rings & Liner 6 nos each
2021-09-30 | Trade Links | Secunderabad | D | Dhanalakshmi Ice Factory | Andhra Pradesh | KCX4 | 3384K2760 | 2635465233 | 2021-09-16 | 263546 | 2021-09-16 | stop valve problem | 2021-03-31 | 2021-06-29 | 1345 | Supplier | ice plant | 3 | Discharge stop valve TAL50 stucked/jammed | null | closed | Replaced TAL50
2021-09-30 | Kalp Marketing | Gujrat | D | J M Sea Foods | Gujrat | KCX72 | 3474K375 | 2630125199 | 2021-09-06 | 263012 | 2021-09-05 | discharge valve leakage | 2020-05-30 | 2020-09-24 | 1684 | Inhouse | meat/fish process | 4 | Cylinder no. 4 overheated , found delivery valve leakage due to damage of stroke limitor & valve ring/sprins. | null | closed | Replaced DV assly
2021-09-30 | Trade Links | Secunderabad | D | Dwaraka Sea Foods | Andhra Pradesh | KCX12 | 3415K012 | 2632905211 | 2021-09-08 | 263290 | 2021-09-08 | over heating | 2020-02-28 | 2020-10-20 | 2907 | Inhouse | meat/fish process | 8 | Cylinder no. 10 discharge valve leakage & liner , piston rings wornout. | null | closed | Replaced liner , piston rings & valve kit.
2021-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Premier Marine Foods | Kerala | KCX72 | 3474K408 | 2629765213 | 2021-09-09 | 262976 | 2021-09-15 | pressure gauge out | 2020-10-14 | 2021-09-15 | 8 | Supplier | meat/fish process | 12 | Pressure gauge 25Kg/cm2 Out , Piercing already done . | null | closed | Replaced pressure gauge 25Kg/cm2
2021-09-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Bostec Cryogenic Gases | Daman & Diu | KCX93 | 3485K095 | 2635285239 | 2021-09-18 | 263528 | 2021-09-17 | oil carry over piston crack | 2020-11-30 | 2021-03-05 | 2580 | Inhouse | others | 4 | Cylinder no. 1&4 found piston crack | null | closed | Replaced piston 2
2021-10-16 | Trade Links | Secunderabad | D | Foster Cold Storage Pvt Ltd | Telangana | KCX3 | 3374K2293 | 2639985249 | 2021-09-22 | 263998 | 2021-09-21 | loading problemsolenoid valve malfunctioning | 2020-02-12 | 2020-05-19 | 1940 | Inhouse | cold storage | 4 | Replaced sol valve 2 nos. | null | closed | Replaced sol valve 2 nos.
2021-10-16 | Trade Links | Secunderabad | D | Vallabha Milk Products | Telangana | KCX21 | 3424K105 | 2631825209 | 2021-09-07 | 263182 | 2021-09-07 | kcx oil pump tang broken | 2020-05-22 | 2020-06-24 | 172 | M/S LDK | dairy / ice cream | 1 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2021-10-16 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Bhushan Oil And Fats Pvt Ltd | Haryana | KCX42 | 3444K186 | 2636265240 | 2021-09-18 | 263626 | 2021-09-17 | delivery valve leakage | 2019-10-26 | 2021-09-17 | 4.5 | Inhouse | food processing | 23 | Replaced discharge valve assly-1No. Due to leak and rusty | null | closed | Del. Valve assly
2021-10-16 | Trade Links | Secunderabad | D | Avanti Frozen Foods Pvt Ltd | Andhra Pradesh | KCX63 | 3464K108 | 2639985249 | 2021-09-22 | 263998 | 2021-09-21 | oil lifting | 2021-01-13 | 2021-06-21 | 1079 | Inhouse | ice plant | 6 | Replaced piston ring sets | null | closed | Replaced piston ring sets
2021-10-16 | Kalp Marketing | Gujrat | D | Natraj Industries | Gujrat | KCX6 | 3394K1785 | 2642865264 | 2021-09-28 | 264286 | 2021-09-27 | over heating | 2021-03-26 | 2021-07-10 | 1254 | Inhouse | ice plant | 3 | Replaced del valve assly-3nos. | null | closed | Replaced del valve assly3nos.
2021-10-16 | Kalp Marketing | Gujrat | D | Kailash Ice Factory | Gujrat | KCX2 | 3364K2163 | 2646025287 | 2021-10-04 | 264602 | 2021-10-02 | over heating | 2021-07-05 | 2021-09-11 | 200 | Inhouse | ice plant | 2 | Replaced del valve kit due to leakage | null | closed | Replaced delivery valve kit
2021-10-16 | Kalp Marketing | Gujrat | D | Real Export | Gujrat | KCX72 | 3474K469 | 2643445286 | 2021-10-04 | 264344 | 2021-10-02 | high oil consumption | 2021-05-30 | 2021-08-13 | 459 | Inhouse | meat/fish process | 2 | Delivery valve kit replaced due to leakage | null | closed | Replaced delivery valve kit
2021-10-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Evergreen Exports | Kerala | KCX2 | 3364K1898 | 2602905108 | 2021-08-06 | 260290 | 2021-09-22 | op pressure switch malfunctioning | 2019-12-29 | 2021-09-22 | 1 | M/S Danfoss | meat/fish process | 19 | Replaced OP Pressure switch | null | closed | Replaced OP Pressure switch
2021-10-16 | Kalp Marketing | Gujrat | D | Atulya Life Science Llp | Gujrat | KCX31 | 3434K0123 | 2642205280 | 2021-10-01 | 264220 | 2021-09-19 | delivery valve leakage | 2019-12-29 | 2021-03-26 | 48 | Inhouse | chemical / pharma | 15 | Delivery valve repaired at site and piston rong set replaced due to damaged in overheating | null | closed | Delivery valve repaired at site and piston ring set replaced due to damaged in overheating
2021-10-16 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Organic Industries Pvt Ltd | Gujrat | KCX9 | 3404K192 | 2612705250 | 2021-09-22 | 261270 | 2021-08-13 | flywheel groove depth oversize | 2021-05-15 | 2021-08-13 | 4 | M/S Jineshwar | chemical / pharma | 3 | Replaced Flywheel due to belt loosened in groove no.5&6 | null | closed | Replaced flywheel
2021-10-16 | Trade Links | Secunderabad | D | Arch Pharma Labls Ltd | Telangana | KCX63 | 3464K075 | 2627005184 | 2021-09-02 | 262700 | 2021-09-01 | oil lifting | 2020-06-01 | 2020-09-27 | 4800 | Inhouse | chemical / pharma | 4 | Replaced piston ring set and cylinder liner | null | closed | Replaced piston ring set and cylinder liner
2021-10-18 | Parag Marketing Services | null | D | Acr Engineering | null | KCX4 | 3384K2875 & 2878 | Email | 2021-10-18 | null | 2021-10-01 | paint peel off | 2021-08-10 | null | ZH | Inhouse | null | null | Paint peel off near VLD housing flange of crank case | null | closed | Paint peel off
2021-10-18 | Multivista Global Pvt Ltd | Uttar Pradesh | D | Shri Radhey Radhey Cold Storage | Hathras ,Uttar Pradesh | KCX4 | 3384K2676 | 2641245254 | 2021-09-23 | 264124 | 2021-09-23 | oil lifting | 2021-01-13 | 2021-02-22 | 1131 | Inhouse | cold storage | 1 | 3 ORV Partially leakage. | null | closed | Replaced 3 ORV.
2021-10-18 | Multivista Global Pvt Ltd | Gurgaon | D | DJ Exports Pvt Ltd | New Delhi | PCX2 | 3106K0076 | 2650165306 | 2021-10-11 | 265016 | 2021-10-11 | suction filter assly leakage | 2021-02-09 | 2021-08-16 | 36 | Inhouse | cold storage | 6 | Suction filter assly welding leakage | null | closed | Replaced Suction filter assly
2021-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | CSIce Land | Kerala | KCX3 | 3374K2162 | 2628325179 | 2021-08-31 | 262832 | 2021-08-21 | oil carry over piston crack | 2019-09-24 | 2020-08-24 | 3969 | Inhouse | ice plant | 11 | 3 Pistons found crack | null | closed | Replaced 3 Pistons & piston ring sets.
2021-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Vasai Machimar S S S Ltd | Thane | KCX6 | 3394K1675 | 2640285260 | 2021-09-27 | 264028 | 2021-09-25 | oil carry over piston crack | 2020-11-11 | 2020-11-17 | 3001 | Inhouse | ice plant | 1 | Piston crack issue for 4 pistons | null | closed | Replaced 4 pistons, Piston ring sets & 1 delivery valve.
2021-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | Nas Fisheries Pvt Ltd | Kerala | KCX72 | 3474K372 | 2649585312 | 2021-10-13 | 264958 | 2021-10-12 | high oil consumption | 2020-03-13 | 2020-12-19 | 2740 | Inhouse | meat/fish process | 9 | Cylinder liner - 2 & Piston ring sets 4 nos.wornout | null | closed | Replaced Cylinder liner 2 & Piston ring sets 4
2021-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | Al Marine Products India Pvt Ltd | Kerala | KCX72 | 3474K366 | 2635885297 | 2021-10-07 | 263588 | 2021-10-07 | pressure gauge out | 2020-02-25 | 2021-10-07 | 17 | Supplier | meat/fish process | 20 | Pressure gauge 16 Kg/cm2 found out. | null | closed | Replaced PG
2021-10-26 | Kalp Marketing | Gujrat | D | Ambika Ice Factory | Gujrat | KCX4 | 3384K2624 | 2644785323 | 2021-10-18 | 264478 | 2021-10-18 | kcx oil pump tang broken | 2020-11-27 | 2021-03-13 | 2236 | M/S LDK | ice plant | 4 | Replaced oil pump element | null | closed | KCX oil pump element
2021-10-26 | Kalp Marketing | Gujrat | D | Sumra Exports | Gujrat | KCX51 | 3454K190 | 2652525324 | 2021-10-18 | 265252 | 2021-10-18 | over heating | 2021-05-30 | 2021-09-11 | 82 | Inhouse | meat/fish process | 4 | Delivery valve replaced | null | closed | Delivery valve replaced
2021-10-26 | Trade Links | Secunderabad | D | Arene Life Science Pvt Ltd | Telangana | KCX6 | 3394K1710 | 2641825282 | 2021-10-02 | 264182 | 2021-10-01 | delivery valve leakage | 2020-12-28 | 2021-07-24 | 236 | Inhouse | chemical / pharma | 7 | Replaced Delivery valve-2,Piston-1,Cylinder liner-1,piston ring set-1,Kit del valve-1 | null | closed | Replaced Delivery valve2,Piston1,Cylinder liner1,piston ring set1,Kit del valve1
2021-10-31 | Trade Links | Secunderabad | D | Foster Cold Storage Pvt Ltd | Telangana | KCX3 | 3374K2296 | 2651645320 | 2021-10-14 | 265164 | 2021-10-14 | high oil consumption | 2020-02-12 | 2020-05-19 | 1308 | Inhouse | cold storage | 3 | Replaced ORV-1 | null | closed | Replaced ORV1
2021-10-31 | Trade Links | Secunderabad | D | Foster Cold Storage Pvt Ltd | Telangana | KCX3 | 3374K2296 | 2654605345 | 2021-10-25 | 265460 | 2021-10-22 | kcx oil pump purging | 2020-02-12 | 2020-05-19 | 1355 | M/S DE | cold storage | 3 | Replaced KCX oil pump-1 | null | closed | Replaced KCX oil pump1
2021-10-31 | Trade Links | Secunderabad | D | Foster Cold Storage Pvt Ltd | Telangana | KCX3 | 3374K2297 | 2651385322 | 2021-10-18 | 265138 | 2021-10-21 | kcx oil pump purging | 2020-02-12 | 2020-05-19 | 1981 | M/S Lubicare | cold storage | 3 | Replaced KCX oil pump-1 | null | closed | Replaced KCX oil pump1
2021-10-31 | Kalp Marketing | Gujrat | D | Nestle India Ltd | Gujrat | KCX4 | 3384K2630 | Service email | 2021-11-01 | 263348 | 2021-10-25 | oil carry over | 2021-12-11 | 2021-07-17 | 1272.6 | Inhouse | food processing | 7 | Piston ring set wornout . | null | closed | Replaced piston ring set
2021-10-31 | Trade Links | Secunderabad | D | Ind Union Foods Ltd | Andhra Pradesh | KCX6 | 3394K1706 | 2642345289 | 2021-10-05 | 264234 | 2021-10-04 | kcx oil pump tang broken | 2020-12-30 | 2021-04-09 | 2879 | M/S LDK | ice plant | 4 | Replaced KCX oil pump kit | null | closed | Replaced KCX oil pump kit
2021-10-31 | Trade Links | Secunderabad | D | Avanti Frozen Foods Pvt Ltd | Andhra Pradesh | KCX63 | 3464K108 | 2636605236 | 2021-09-17 | 263660 | 2021-09-16 | oil lifting | 2021-01-13 | 2021-06-21 | 1079 | Inhouse | ice plant | 5 | Replaced piston ring set 3 nos. | null | closed | Replaced piston ring set 3 nos.
2021-10-31 | Trade Links | Secunderabad | D | Vijay Laxmi Ice And Cold Storage | null | KCX3 | 3374K2420 | 2656165350 | 2021-10-27 | 265616 | 2021-10-26 | oil liftingpiston crack | 2020-11-12 | 2021-02-03 | 4865 | M/S Paramount pistons | ice plant | 2 | Replaced piston-1 and piston ring set-1 | null | closed | Replaced piston1 and piston ring set1
2021-10-31 | Geekay Pneumatic Pvt Ltd | Kerala | D | Thottakam Ice Plant | null | KCX3 | 3374K2361 | 2652785331 | 2021-10-19 | 265278 | 2021-10-19 | shaft seal leakage | 2020-08-11 | 2021-04-09 | 2503 | Inhouse | ice plant | 8 | Replaced shaft seal assly R22 application | null | closed | Replaced shaft seal assly
2021-10-31 | Trade Links | Secunderabad | D | Arene Life Science Pvt Ltd | Telangana | KCX6 | 3394K1784 | 2644865283 | 2021-10-02 | 264486 | 2021-10-04 | delivery valve leakage | 2021-03-26 | 2021-10-04 | 4 | Inhouse | chemical / pharma | 7 | Replaced delivery valve and stop valve teflon | null | closed | Replaced delivery valve and stop valve teflon
2021-11-20 | Kalp Marketing | Gujrat | D | Vinayak Cold Storage | Gujrat | KCX4 | 3384K2867 | 2658565361 | 2021-11-01 | 265856 | 2021-11-01 | pressure gauge malfunctioning | 2021-08-25 | 2021-11-01 | 2 | Supplier | cold storage | 2 | HP Pressure gauge not shwoing pr more than 7 kg/cm2. Replaced pressure gauge | null | closed | Replaced pressure gauge
2021-11-20 | Robin Refrigeration Works | Odisha | D | B-One Buisness House Pvt Ltd | Bhubaneswar Orissa | KCX6 | 3394K1617 | 2658185383 | 2021-11-15 | 265818 | 2021-11-11 | abnormal noisecylinder liner & piston ring set worn out | 2020-08-07 | 2020-12-26 | 1375 | Inhouse | ice plant | 4 | Replaced piston ring set, cylinder liner and curtian spring | null | closed | Replaced piston ring set
2021-11-20 | Cool Comfort Private Limited | West Bengal | D | Shimpo ExportsPvt Ltd | West Bengal | KCX72 | 3474K338 | 2659265362 | 2021-11-01 | 265926 | 2021-11-16 | abnormal noise & oil lifting | 2019-12-21 | 2020-01-13 | 3967 | Inhouse | meat/fish process | 6 | Site observations not mentioned in FRR & FSR. | null | closed | Replaced Liner , Piston , Piston ring set , Gudgeon pin & Connecting rod2 nos each.
2021-11-21 | Trade Links | Secunderabad | D | The Kurnool DistMilk Producers Mutually Aided Co-Op Union Ltd | Andhra Pradesh | KCX6 | 3394K1790 | 2656365353 | 2021-11-29 | 265636 | 2021-11-28 | pressure gauge malfunctioning | 2021-03-31 | 2021-11-28 | 3 | Supplier | dairy / ice cream | 7 | OP Pressure gauge having positive error. | null | closed | Replaced OP Pr gauge
2021-11-21 | Trade Links | Secunderabad | D | Dhanalakshmi Ice Factory | Andhra Pradesh | KCX4 | 3384K2760 | 2652685327 | 2021-11-19 | 265268 | 2021-11-18 | discharge stop valve problem. | 2021-03-31 | 2021-06-29 | 2082 | Supplier | ice plant | 3 | Repeatative type FRR - Wrong part number entered while raised first FRR Tal-50 INSTEAD OF TAL70/80. | null | closed | null
2021-11-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Three Star Indistries | Kerala | KCX3 | 3374K2177 | 2648625349 | 2021-11-26 | 264862 | 2021-11-26 | high oil consumption | 2019-11-15 | 2020-06-02 | 5128 | Inhouse | ice plant | 7 | All 3 liners & piston ring sets were wornout | null | closed | Liners & Piston ring sets replaced.
2021-11-21 | Robin Refrigeration Works | Odisha | D | Orchid Marine Exports Pvt Ltd | Odisha | KCX93 | 3485K091 | 2658645367 | 2021-11-01 | 265864 | 2021-11-01 | oil pressure not buildup | 2020-11-19 | 2021-06-09 | 4 | Inhouse | meat/fish process | 7 | Oil pump tang broken | null | closed | Oil pump elementLDK
2021-11-27 | Trade Links | Secunderabad | D | Cofoods Processing Pvt Ltd | Andhra Pradesh | KCX6 | 3394K1880 | 2753305410 | 2021-11-24 | 275330 | 2021-11-24 | krms problemswiring connector broken | 2021-09-29 | 2021-11-24 | 0 | Supplier | ice plant | 2 | Replaced control panel | null | closed | Replaced control panel
2021-11-27 | Geekay Pneumatic Pvt Ltd | Kerala | D | C S Ice Land | Kerala | KCX3 | 3374K2162 | 2628325179 | 2021-08-31 | 262832 | 2021-08-31 | oil carryover piston crack | 2019-09-24 | 2020-08-24 | 3969 | Inhouse | ice plant | 11 | Cylinder no 03 pistons found crack | null | closed | Replaced piston, piston ring set.
2021-11-27 | Geekay Pneumatic Pvt Ltd | Kerala | D | Nas Fisheries Pvt Ltd | Kerala | KCX72 | 3474K372 | 2649585312 | 2021-10-13 | 264958 | 2021-10-12 | high oil carryover | 2020-03-13 | 2020-12-19 | 2740 | Inhouse | meat/fish process | 9 | Replaced piston ring set-4nos and cylinder liner-2 nos. | null | closed | Replaced piston ring set4nos and cylinder liner2 nos.
2021-11-27 | Kalp Marketing | Gujrat | D | Ascent Fine Chem PvtLtd | Gujrat | KCX4 | 3384K2870 | 2711465394 | 2021-11-18 | 271146 | 2021-11-18 | discharge stop valve leakage | 2021-08-25 | 2021-11-12 | 100 | Supplier | chemical / pharma | 3 | discharge stop valve found welding leakage | null | closed | Replaced Discharge stop valve TAL 70/80 inlet
2021-11-30 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX4 | 3384K2720 | 2666825381 | 2021-11-15 | 266682 | 2021-11-20 | kcx oil pump tang broken | 2021-02-27 | 2021-11-20 | 5 | Supplier H21 049 LDK | food processing | 9 | Oil pump driving shaft tang broken | null | closed | Pump assly replaced
2021-11-30 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX6 | 3394K1762 | 2668825399 | 2021-11-20 | 266882 | 2021-11-20 | wrong pressure switch kp5 | 2021-02-27 | 2021-11-20 | 5 | Inhouse | food processing | 9 | KP5 Cutout replaced with KP1 as this compressor is used in LP side due to booster system. | null | closed | KP5 Cutout replaced with KP1 due to booster system. OK Cutout
2021-11-30 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX6 | 3394K1761 | 2668785400 | 2021-11-20 | 266878 | 2021-11-20 | wrong pressure switch kp5 | 2021-02-27 | 2021-11-20 | 5 | Inhouse | food processing | 9 | KP5 Cutout replaced with KP1 as this compressor is used in LP side due to booster system. | null | closed | KP5 Cutout replaced with KP1 due to booster system. OK Cutout
2021-11-30 | Kalp Marketing | Gujrat | D | Laakoonaa Reaction | Gujrat | KCX4 | 3384K2793 | 2666485392 | 2021-11-18 | 266648 | 2021-11-17 | pressure gauge malfunctioning | 2021-06-23 | 2021-11-17 | 4 | Supplier | ice plant | 6 | Replaced pressure gauge 25 kg/cm2 | null | closed | Replaced pressure gauge 25 kg/cm2
2021-12-20 | Parag Marketing Services | null | D | Shree Industrial Suppliers & Contractors | Pune | KCX4 | 3384K2768 | 2650905311 | 2021-10-12 | 265090 | 2021-10-14 | female run tee leakage | 2021-05-03 | 2021-10-14 | 4 | Inhouse | cold storage | 6 | Female run tee leakage | null | closed | Replaced Female run tee
2021-12-20 | Shree Engineering Services | Chhattisgarh | D | BRCold Storage Pvt Ltd | Chhattisgarh | KCX4 | 3384K2648 | 2630445313 | 2021-10-13 | 263044 | 2021-10-14 | high oil consumption | 2020-12-11 | 2021-01-13 | 780 | Inhouse | cold storage | 1 | Cyl.No. 3 & 4 found open oil throw & one ORV stuck | null | closed | Replaced Piston ring set 2 & ORV1
2021-12-20 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX6 | 3394K1760 | 2668765433 | 2021-11-29 | 266876 | 2021-12-03 | booster system hp pressure switch replaced | 2021-02-27 | 2021-12-03 | 3 | mkt | food processing | 10 | HP Cutout replaced with KP1 Cutout due to booster system. | null | closed | HP Cutout replaced with KP1 Cutout due to booster system.
2021-12-20 | Parag Marketing Services | null | D | Royal Foodtuffs Pvt Ltd | Karad | KCX72 | 3474K411 | 2640725371 | 2021-11-02 | 264072 | 2021-11-02 | high oil consumption | 2020-10-20 | 2021-01-20 | 4099 | Inhouse | food processing | 3 | Piston rings wornout, ORV chock & bearings wornout. | null | closed | Replaced piston ring set 10 , ORV7, Bearing 1.
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Cherukattu Industries | Kerala | KCX3 | 3374K2617 | 2659245372 | 2021-11-10 | 265924 | 2021-11-03 | cylinder overheating | 2021-07-28 | 2021-09-09 | 778 | Inhouse | ice plant | 2 | Discharge valve leakage , high discharge pressure , no insulation , no liquid controller & high vibrations at site. | null | closed | Replaced DV
2021-12-20 | Robin Refrigeration Works | Odisha | D | Subrana Ice Factory | Odisha | KCX4 | 3384K2782 | 2658665368 | 2021-11-01 | 265866 | 2021-11-01 | cylinder overheating | 2021-05-31 | 2021-07-15 | 298 | Customer site issue | ice plant | 2 | Compressor cylinder block colour changed. One delivery valve found leakage due to dirt entry. | null | closed | Replaced Cylinder liner , Piston , Piston ring set , Gudgen pin , Kit delivery valve , ORV.
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Freezing Point | Kerala | KCX3 | 3374K2628 | 2716625421 | 2021-11-27 | 271662 | 2021-11-30 | cylinder overheating & abnormal sound | 2021-08-14 | 2021-09-30 | 671 | Supplier | ice plant | 1 | Delivery valve leakage & step at suction stroke limitor . | null | closed | Replaced suction , delivery stroke limitor & valve kit1
2021-12-20 | Parag Marketing Services | null | D | Mv9 Hospitality | Pune | PCX2 | 3106K0080 | 2628365338 | 2021-10-21 | 262836 | 2021-10-21 | high oil consumption | 2021-02-28 | 2021-03-30 | 19 | Inhouse | ice plant | 1 | Oil throw from both cylinders & ORV plate missing - 1 | null | closed | Replaced piston ring set2 & ORV1
2021-12-20 | Parag Marketing Services | null | D | Mv9 Hospitality | Pune | PCX2 | 3106K0079 | 2628385339 | 2021-10-21 | 262838 | 2021-10-21 | high oil consumption | 2021-02-28 | 2021-03-30 | 65 | Inhouse | ice plant | 1 | Oil throw from both cylinders , liner & piston 1 wornout , piston ring gap 0.83mm & ORV plate missing - 1 | null | closed | Replaced liner1piston1,piston ring set2 & ORV1
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Marine Ice Factory | Kerala | KCX4 | 3384K2504 | 2664305409 | 2021-11-24 | 266430 | 2021-12-08 | high oil consumption | 2020-02-25 | 2020-06-16 | 6411 | Inhouse | ice plant | 4 | Liner no. 1 & 3 found step & all piston ring sets wornout. Shaft seal leakage | null | closed | Replaced Liner 2 , Piston ring sets 4 & shaft seal 1
2021-12-20 | Pragya Industrial Supply | Karnataka | D | Samudra Ice Plant Unit-2 | Karnataka | KCX4 | 3384K2757 | 2689305387 | 2021-11-16 | 268930 | 2021-11-15 | high oil consumption | 2021-03-30 | 2021-09-02 | 1654 | Inhouse | ice plant | 5 | Liner cut mark -1 & 3 piston ring sets wornout. | null | closed | Liner cut mark 1 & 3 piston ring sets wornout.
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Crystal Ice Plant | Kerala | KCX3 | 3374K2310 | 2656705354 | 2021-10-29 | 265670 | 2021-11-01 | high oil consumption piston crack | 2020-02-25 | 2021-04-01 | 2506 | Inhouse | ice plant | 2 | Cylinder no. 2 & 3 Piston hair line crack & piston rings wornout. | null | closed | Replaced Piston & Piston ring sets
2021-12-20 | Trade Links | Secunderabad | D | Naga Hanuman Ice Industry | Andhra Pradesh | KCX4 | 3384K2831 | 2664225377 | 2021-11-11 | 266422 | 2021-11-11 | oil pressure not buildup | 2021-07-28 | 2021-10-26 | 135 | Inhouse | ice plant | 3 | Oil pressure not develop due to tang broken & DV leakage. | null | closed | Replaced pump assly & DV assly
2021-12-20 | Parag Marketing Services | null | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX72 | 3474K460 | 2653305332 | 2021-11-19 | 265330 | 2021-11-19 | air purging problem | 2020-12-29 | 2021-04-28 | 2058 | Supplier | meat/fish process | 4 | KCX Oil pump air purging problem , after vaccume oil pressure not develop. | null | closed | KCX Oil pump air purging problem , after vaccume oil pressure not develop.
2021-12-20 | Kalp Marketing | Gujrat | D | Real Export | Gujrat | KCX72 | 3474K469 | 2714145425 | 2021-11-27 | 271414 | 2021-11-27 | high oil consumption | 2021-05-30 | 2021-08-13 | 1395 | Inhouse | meat/fish process | 2 | Piston ring set 3 Nos gap increased & one discharge valve leakage | null | closed | Replaced 3 piston ring sets & one valve kit.
2021-12-20 | Kalp Marketing | Gujrat | D | Sun International | Gujrat | KCX72 | 3474K424 | 2714125424 | 2021-11-27 | 271412 | 2021-11-27 | high oil consumption | 2020-11-30 | 2021-03-04 | 1027 | Inhouse | meat/fish process | 4 | Piston ring set no. 3 , 6 & 9 found light leakage & gap increased. | null | closed | Replaced piston ring set 3 nos.
2021-12-20 | Kalp Marketing | Gujrat | D | Sagar Food | Gujrat | KCX72 | 3474K474 | 2714105423 | 2021-11-27 | 271410 | 2021-11-27 | high oil consumption | 2021-07-28 | 2021-10-05 | 370 | Inhouse | meat/fish process | 3 | All VLD Orings replaced due to flatned | null | closed | All VLD Orings replaced due to flatned
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Premier Marine Foods | Kerala | KCX72 | 3474K408 | 2686925408 | 2021-11-24 | 268692 | 2021-11-30 | high oil consumption | 2020-10-14 | 2021-09-15 | 583 | Supplier | meat/fish process | 11 | One piston damaged , 5 piston rings wornout & 2 delivery valve leakage due to step at stroke limitor. | null | closed | Replaced piston1, piston ring sets 5 & dv2
2021-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Geo Sea Foods | Kerala | KCX4 | 3384K2905 | 2664365374 | 2021-11-11 | 266436 | 2021-11-30 | pressure gauge malfunctioning | 2021-10-05 | 2021-11-30 | 1 | supplier | meat/fish process | 1 | Pressure gauge 16Kg/cm2 found out. | null | closed | Replaced Pr 16Kg/cm2.
2021-12-20 | Kirloskar Pneumatic Co Ltd | Uttar Pradesh | D | Bharakam Carbonic | Uttar Pradesh | KCX63 | 3464K094 | 2655505376 | 2021-11-11 | 265550 | 2021-11-11 | abnormal noise | 2020-11-10 | 2021-03-01 | 4056 | Customer site issue | others | 4 | Cylinder no.4 Piston crack & Cylinder no.2 liner cut mark due to liquid stroke. | null | closed | Replaced Piston4, Liner2 & Piston ring set4
2021-12-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Odyssey Oranganics Pvt Ltd | Raigad | KCX2 | 3364K2032 | 2646625348 | 2021-10-26 | 264662 | 2021-10-21 | op pressure switch malfunctioning | 2020-10-26 | 2021-10-21 | 3 | Supplier | ice plant | 12 | Microswitch plate not released automatically when oil pressure was dropped. No tripping issue. | null | closed | Replaced OP Switch
2021-12-21 | Kalp Marketing | Gujrat | D | Sumra Exports | Gujrat | KCX51 | 3454K189 | 2789085477 | 2021-12-14 | 278908 | 2021-12-14 | cylinder overheating | 2021-05-30 | 2021-09-11 | 464 | Inhouse | meat/fish process | 4 | Delivery valve leakage due to kit overheated. | null | closed | Replaced kit DV
2021-12-27 | Trade Links | Secunderabad | D | Hatsun Agro Products Ltd | Tamil Nadu | KCX4 | 3384K2724 | 2807745495 | 2021-12-21 | 280774 | 2021-12-21 | krms problemcontroller not working | 2021-02-28 | 2021-09-03 | 133 | Supplier | dairy / ice cream | 7 | KRMS Controller Panel malfunctioning | null | closed | KRMS controller board
2021-12-27 | Trade Links | Secunderabad | D | Lnsk Greenhouse Agro Products | Andhra Pradesh | KCX3 | 3374K2413 | 2787125470 | 2021-12-13 | 278712 | 2021-12-11 | oil liftingpiston crack | 2020-11-03 | 2021-02-04 | 5159 | Inhouse | ice plant | 3 | Piston crack issue | null | closed | Piston, cylinder liner,piston ring sets
2021-12-31 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Aries Color Chem Pvt Ltd | Gujrat | KCX72 | 3474K418 | 2615525150 | 2021-08-21 | 261552 | 2021-08-20 | delivery valve leakage | 2020-10-31 | 2021-08-20 | 3 | Inhouse | chemical | 10 | Delivery valve kit & piston ring set replaced | null | closed | Delivery valve kit & piston ring set replaced
2021-12-31 | Robin Refrigeration Works | Odisha | D | Bhimraj Exports Private Limited Badapokharia | Odisha | KCX93 | 3485K097 | Email | 2021-12-31 | null | 2021-12-31 | burr found in cylinder no 5 | 2021-01-17 | 2021-12-25 | ZH | Inhouse | cold storage | 11 | Burr found in cylinder no 05 | null | closed | null
2021-12-31 | Robin Refrigeration Works | Odisha | D | Bhimraj Exports Private Limited Badapokharia | Odisha | KCX63 | 3464K0109 | Email | 2021-12-31 | null | 2021-12-31 | burr found in cylinder no 7 | 2021-01-17 | 2021-12-25 | ZH | Inhouse | cold storage | 11 | Burr found in cylinder no 07 | null | closed | null
2021-12-31 | Trade Links | Secunderabad | D | Subbu Milk Products | Andhra Pradesh | KCX1 | 3354K219 | 2766425456 | 2021-12-08 | 276642 | 2021-12-08 | key loose in c.shaft keyway | 2021-09-20 | 2021-12-08 | 6 | Inhouse | dairy / ice cream | 3 | Replaced key | null | closed | Key
2021-12-31 | Trade Links | Secunderabad | D | Subbu Milk Products | Andhra Pradesh | KCX1 | 3354K220 | 2766445457 | 2021-12-08 | 276644 | 2021-12-08 | key loose in c.shaft keyway | 2021-09-20 | 2021-12-08 | 13 | Inhouse | dairy / ice cream | 3 | Replaced key | null | closed | Key
2021-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Choice Trading Cooperation Pvt Ltd | Kerala | KCX72 | 3474K455 | 2799585484 | 2021-12-16 | 279958 | 2021-12-15 | cylinder overheating | 2021-03-28 | 2021-07-25 | 2491 | Inhouse | food processing | 4 | Replaced Delivery valve assly | null | closed | Replaced Delivery valve assly
2021-12-31 | Trade Links | Secunderabad | D | Lakshmi Ganapthi Ice Factory | Andhra Pradesh | KCX4 | 3384K2835 | 2797745488 | 2021-12-18 | 279774 | 2021-12-17 | bearings worn out | 2021-07-31 | 2021-10-19 | 174 | Inhouse | ice plant | 3 | Replaced main bearing bush FW & PE , thrust ring | null | closed | Replaced main bearing bush FW & PE , thrust ring
2021-12-31 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Amit Ice Factory | Gujrat | KCX3 | 3374K2572 | 2799405482 | 2021-12-15 | 279940 | 2021-12-15 | delivery valve leakage | 2021-05-26 | 2021-07-29 | 1 | Inhouse | ice plant | 2 | Replaced delivery valve and piston ring set | null | closed | Replaced delivery valve and piston ring set
2021-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Sea Food Innovations | Kerala | KCX3 | 3374K2685 | 2801405486 | 2021-12-17 | 280140 | 2021-12-16 | high oil carryover | 2021-10-29 | 2021-11-30 | 616 | Inhouse | ice plant | 1 | Replaced piston ring set and thrust ring | null | closed | Replaced piston ring set and thrust ring
2021-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Crystal Ice & Cold Storage | Ratnagiri | KCX4 | 3384K2722 | 2807885497 | 2021-12-21 | 280788 | 2021-12-21 | pressure gauges out | 2021-02-28 | 2021-12-21 | 2 | Supplier | ice plant | 10 | Discharge and oil pressure gauge out | null | closed | Replaced pressure gauge 16 & 25 Kg/cm2
2021-12-31 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Astik Dyestuff Pvt Ltd | Vadodara , Gujarat | KCX63 | 3464K063 | 2609285145 | 2021-08-19 | 260928 | 2021-08-19 | suction valve spring broken | 2019-09-09 | 2021-08-19 | 11 | Inhouse | ice plant | 23 | Suction valve spring broken | null | closed | Suction valve spring broken
2021-12-31 | Trade Links | Secunderabad | D | Akshay Food Impex | Andhra Pradesh | KCX72 | 3474K392 | 2657265358 | 2021-10-30 | 265726 | 2021-10-29 | cylinder overheating | 2020-08-29 | 2020-09-20 | 1827 | Inhouse | meat/fish process | 1 | Replaced piston,liner,del valve,buffer spring, piston ring set,suction valve spring | null | closed | Replaced piston,liner,del valve,buffer spring, piston ring set,suction valve spring
2021-12-31 | Kalp Marketing | Gujrat | D | Raunak Ice & Cold Storage | Gujrat | KCX72 | 3474K468 | 2818005509 | 2021-12-25 | 281800 | 2021-12-24 | cylinder overheating | 2021-05-26 | 2021-09-07 | 1619 | Inhouse | meat/fish process | 4 | Replaced Delivery valve assly-2 nos. | null | closed | Replaced Delivery valve assly2 nos.
2021-12-31 | Kalp Marketing | Gujrat | D | Sun International | Gujrat | KCX72 | 3474K424 | 2804865508 | 2021-12-25 | 280486 | 2021-12-24 | high oil consumption | 2020-11-30 | 2021-03-01 | 1355 | Inhouse | meat/fish process | 4 | Replaced piston ring set and VLD orings | null | closed | Replaced piston ring set and VLD orings
2021-12-31 | Kalp Marketing | Gujrat | D | Real Export | Gujrat | KCX72 | 3474K469 | 2797445505 | 2021-12-24 | 279744 | 2021-12-23 | high oil consumption | 2021-05-30 | 2021-08-13 | 1723 | Inhouse | meat/fish process | 2 | Delivery valve seat damaged & piston ring close gap incresed | null | closed | Replaced Del.valve assly and piston ring sets
2022-01-15 | S. B. Refrigeration Services | Bihar | D | Pristin Mega Food Park Pvt Ltd | Bihar | KCX4 | 3384K2721 | 2825925520 | 2021-12-30 | 282592 | 2021-12-31 | high oil consumption | 2021-02-27 | 2021-05-18 | 1550 | Inhouse | cold storage | 3 | Replaced piston ring set 4 nos. | null | closed | Replaced piston ring set 4 nos.
2022-01-15 | Multivista Global Pvt Ltd | Gurgaon | D | Natures Betow | Uttarakhand | KCX6 | 3394K1469 | 2697305535 | 2022-01-07 | 269730 | 2021-12-09 | oil lifting | 2019-12-31 | 2020-07-29 | 2761 | Inhouse | cold storage | 7 | Replaced cylinder liner and piston ring set due to wornout | null | closed | Cylinder liner & piston ring sets
2022-01-15 | Cool Comfort Private Limited | West Bengal | D | Aquatech Feed & Sea Foods Pvt Ltd | West Bengal | KCX4 | 3384K2659 | 2847425549 | 2022-01-12 | 284742 | 2022-01-12 | krmscontroller board not working | 2020-12-31 | 2021-11-19 | 4 | Supplier | meat/fish process | 11 | Replaced KRMS conroller | null | closed | Replaced KRMS conroller
2022-01-15 | Trade Links | Secunderabad | D | V J Sai Chem | Telangana | KCX63 | 3464K138 | 2821025519 | 2021-12-30 | 282102 | 2021-12-29 | key loose in c.shaft keyway | 2021-10-20 | 2021-12-29 | 7 | Inhouse | chemical / pharma | 2 | Replaced key | null | closed | Key
2022-01-15 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Spectrum Dyes & Chemicals Pvt Ltd | Gujrat | KCX2 | 3364K2037 | 2826545523 | 2022-01-01 | 282654 | 2022-01-12 | oil carry over | 2020-11-03 | 2021-01-12 | 8024 | Inhouse | chemical / pharma | 3 | Piston crack | null | closed | Replaced piston1 & piston ring set
2022-01-23 | Parag Marketing Services | null | D | Godhan Agro Farms | Rahuri | KCX1 | 3354K160 | 2669005460 | 2021-12-09 | 266900 | 2021-12-07 | oil carry over | 2020-08-22 | 2021-03-20 | 1727 | Inhouse | dairy / ice cream | 7 | Replaced piston,liner and piston ring set-1 | null | closed | Replaced piston,liner and piston ring set1
2022-01-23 | Parag Marketing Services | null | D | Bhoomi Agro Bio Foods | Pune | KCX51 | 3454K184 | 2782165450 | 2021-12-07 | 278216 | 2021-12-07 | oil carry over | 2021-03-17 | 2021-08-17 | 1663 | Inhouse | food processing | 5 | Replaced piston ring sets | null | closed | Replaced piston ring sets
2022-01-23 | Geekay Pneumatic Pvt Ltd | Kerala | D | Al Marine Products India Pvt Ltd | Kerala | KCX72 | 3474K367 | 2639505299 | 2021-10-08 | 263950 | 2021-10-07 | toggle switch not working | 2020-02-25 | 2021-10-07 | 10 | Inhouse | meat/fish process | 19 | Replaced toggle switch | null | closed | Replaced toggle switch
2022-01-24 | Trade Links | Goa | D | Nestle India Ltd | Goa | KCX6 | 3394K1466 | 2797385499 | 2021-12-22 | 279738 | 2021-12-15 | overheatingdelivery valve leak | 2019-12-25 | 2021-01-02 | 5126 | Supplier | food processing | 13 | Replaced piston,cylindr liner, piston ring set, delivery valve | null | closed | Replaced piston,cylindr liner, piston ring set, delivery valve
2022-01-24 | Kalp Marketing | Gujrat | D | Aries Dye Chem Industries | Gujrat | KCX6 | 3394K1828 | 2852945574 | 2022-01-21 | 285294 | 2022-01-21 | cylinder overheatingdelivery valve leak | 2021-07-28 | 2021-10-30 | 949 | Supplier | ice plant | 3 | Replaced delivery valve assly-1 | null | closed | Replaced delivery valve assly1
2022-01-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Ava Ice And Cold Storage | Kerala | KCX3 | 3374K2384 | 2839005539 | 2022-01-10 | 283900 | 2022-01-08 | high oil carryoverpiston crack | 2020-09-19 | 2020-11-05 | 4730 | Supplier | ice plant | 2 | Replaced piston-1,piston ring set-2 | null | closed | Replaced piston1,piston ring set2
2022-01-24 | Pragya Industrial Supply | Karnataka | D | Ideal Ice Cream | Mangalore, Karnataka | KCX63 | 3464K0063 | 2850625557 | 2022-01-14 | 285062 | 2022-01-14 | shaft seal leakage | 2020-01-22 | 2021-04-29 | 1325 | Supplier | ice plant | 14 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2022-01-24 | Trade Links | Secunderabad | D | Dwarka Sea Foods | Andhra Pradesh | KCX72 | 3474K458 | 2832905526 | 2022-01-04 | 283290 | 2022-01-03 | abnormal noisedelivery valve leak | 2021-03-29 | 2021-04-29 | 3211 | Supplier | meat/fish process | 1 | Replaced Delivery valve assly-2 nos. | null | closed | Replaced Delivery valve assly2 nos.
2022-01-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Ai Marine Products India Pvt Ltd | Kerala | KCX72 | 3474K368 | 2833665531 | 2022-01-06 | 283366 | 2022-01-06 | high oil carryover | 2020-02-25 | 2021-10-07 | 245 | Supplier | meat/fish process | 20 | Replaced piston,piston ring set. | null | closed | Replaced piston,piston ring set.
2022-01-24 | Kalp Marketing | Gujrat | D | Ss International | Gujrat | KCX93 | 3485K096 | 2851325565 | 2022-01-19 | 285132 | 2022-01-18 | piston crack | 2021-01-11 | 2021-08-15 | 2667 | Supplier | meat/fish process | 7 | Replaced piston | null | closed | Replaced oring kit
2022-01-24 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3454K191 | 2851345569 | 2022-01-20 | 285134 | 2022-01-20 | shaft seal leakage | 2021-06-23 | 2021-08-25 | 1203 | Supplier | meat/fish process | 2 | Replaced Shaft seal assly | null | closed | Replaced Shaft seal assly
2022-01-24 | Kalp Marketing | Gujrat | D | Ss International | Gujrat | KCX93 | 3485K096 | 2851325565 | 2022-01-19 | 285132 | 2022-01-18 | shaft seal leakage | 2021-01-11 | 2021-08-15 | 2667 | Supplier | meat/fish process | 7 | Replaced oring kit | null | closed | Replaced oring kit
2022-01-24 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KCX42 | 3444K205 | 2641925301 | 2021-10-08 | 264192 | 2021-10-08 | abnormal noisedelivery valve leak | 2020-03-13 | 2020-11-12 | 6500 | Inhouse | chemical / pharma | 8 | Replaced cylinder liner,piston ring set, del. Valve assly | null | closed | Replaced cylinder liner,piston ring set, del. Valve assly
2022-01-30 | Cool Comfort Private Limited | West Bengal | D | Aether Breweries | Arunachal Pradesh | KCX9 | 3404K164 | 2849965558 | 2022-01-14 | 284996 | 2022-01-14 | shaft seal leakage | 2020-11-28 | 2021-11-03 | 60 | Supplier | beverage / breweries | 12 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2022-01-30 | Parag Marketing Services | null | D | Graviss Food Pvt Ltd | null | KCX102 | 3495K002 | Email | 2022-01-30 | null | 2022-01-30 | base frame problem0.4 to 1.2 mm gap between compressor foot and base frame pad | 2021-10-04 | 2022-01-30 | 0 | Supplier | dairy / ice cream | 3 | Replaced base frame | null | closed | Replaced base frame
2022-01-30 | Kalp Marketing | Gujrat | D | Jay Shree Gayatri Food Products | Madhya Pradesh | KCX6 | 3394K1776 | 2863385584 | 2022-01-28 | 286338 | 2022-01-28 | kcx oil pump tang broken | 2021-03-12 | 2021-08-28 | 2965 | Supplier | dairy / ice cream | 5 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2022-01-30 | Parag Marketing Services | null | D | Godhan Agro Farms | Rahuri | KCX1 | 3354K167 | 2669025462 | 2021-12-10 | 266902 | 2021-12-07 | oil carry over | 2020-10-07 | 2021-04-12 | 1918 | Supplier | dairy / ice cream | 6 | Replaced piston ring set | null | closed | Replaced piston ring set
2022-01-30 | Cool Comfort Private Limited | West Bengal | D | Shankha Deep Exports Pvt Ltd | West Bengal | KCX93 | 3485K104 | 2857925578 | 2022-01-24 | 285792 | 2022-01-24 | heater socket inclinedc.case problem | 2021-03-24 | 2022-01-24 | ZH | Supplier | meat/fish process | 10 | Rectified at site | null | closed | null
2022-02-16 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Aries Color Chem Pvt Ltd | Gujrat | KCX72 | 3474K396 | 2880305631 | 2022-02-10 | 288030 | 2022-02-10 | kcx oil pump tang broken | 2020-09-20 | 2021-08-20 | 6 | Supplier | chemical | 11 | Replaced KCX oil pump element | null | closed | Replaced KCX oil pump element
2022-02-16 | Model Pneumatic Co | Punjab | D | Sai All Season Fruits And Vegetables | Himachal Pradesh | KCX72 | 3474K513 | 2892125623 | 2022-02-09 | 289212 | 2021-11-30 | discharge temprature sensor not working | 2021-11-30 | 2022-01-24 | 57 | Supplier | cold storage | 2 | Replaced Discharge Temparature sensor | null | closed | Replaced Discharge Temparature sensor
2022-02-16 | Model Pneumatic Co | Punjab | D | Sai All Season Fruits And Vegetables | Himachal Pradesh | KCX72 | 3474K513 | 2892125623 | 2022-02-09 | 289212 | 2021-11-30 | discharge temprature sensor not working | 2021-11-30 | 2022-01-24 | 2 | Supplier | cold storage | 2 | Replaced Discharge Temparature sensor | null | closed | Replaced Discharge Temparature sensor
2022-02-16 | Hss Solution Pvt Ltd | Rajasthan | D | Jai Gurudev Agro Industries | Rajastan | KCX2 | 3364K2115 | 2641485256 | 2021-09-24 | 264148 | 2021-09-23 | discharge valve leakage | 2021-03-14 | 2021-07-12 | 276 | Inhouse | dairy / ice cream | 4 | Replaced Discharge valve assly | null | closed | Replaced Discharge valve assly
2022-02-16 | Hss Solution Pvt Ltd | Rajasthan | D | Kuber Dairy | Rajastan | KCX3 | 3374K2564 | 2873645600 | 2022-02-01 | 287364 | 2022-02-01 | kcx manifold threading worn out due to excessive tightening at field | 2021-04-27 | 2021-05-15 | 2377 | Inhouse | dairy / ice cream | 1 | Replaced KCX manifold | null | closed | Replaced KCX manifold
2022-02-16 | Hss Solution Pvt Ltd | Rajasthan | D | Paschimi Rajasthan Dudh Utpadak Sangh | Rajastan | KCX6 | 3394K1817 | 2879805614 | 2022-02-05 | 287980 | 2022-02-05 | shaft seal leakage | 2021-07-19 | 2022-01-07 | 190 | Supplier | dairy / ice cream | 6 | Replaced Shaft seal assly | null | closed | Replaced Shaft seal assly
2022-02-16 | Model Pneumatic Co | Punjab | D | Voctory Foods | Punjab | KCX2 | 3364K2136 | 2882985619 | 2022-02-07 | 288298 | 2022-02-06 | kcx oil pump tang broken | 2021-04-21 | 2021-12-30 | 8 | Supplier | food processing | 8 | Replaced oil pump element | null | closed | Replaced KCX oil pump element
2022-02-16 | Multivista Global Pvt Ltd | Gurgaon | D | Ehsas Frozen Foods | Uttarakhand | KC63 | 346K290 | 2873945612 | 2022-02-04 | 287394 | 2022-02-04 | knocking soundcylinder liner and piston ring set worn out | 2021-10-01 | 2021-12-16 | 151 | Inhouse | food processing | 3 | Replaced cylinder liner,piston,piston ring set,Needle roller bearing,HP suction strainer assly | null | closed | Replaced cylinder liner,piston,piston ring set,Needle roller bearing,HP suction strainer assly
2022-02-16 | Model Pneumatic Co | Punjab | D | Sai All Season Fruits And Vegetables | Himachal Pradesh | KCX31 | 3434K0121 | 2850985310 | 2021-10-12 | 265098 | 2021-10-12 | piston crack | 2019-12-23 | 2021-01-06 | 2148 | Supplier | food processing | 12 | Piston crack 1 no. | null | closed | Replaced piston 1 no.
2022-02-16 | Hss Solution Pvt Ltd | Rajasthan | D | A S Agro Foods | Rajastan | KCX1 | 3354K226 | 2724845419 | 2021-11-26 | 272484 | 2021-11-25 | leakage from 6 mm tubing from discharge to gauge board | 2021-10-18 | 2021-11-16 | 23 | Supplier | ice plant | 1 | Replaced 6 mm tubing | null | closed | Replaced 6 mm tubing
2022-02-16 | Hss Solution Pvt Ltd | Rajasthan | D | Maruti Chilling Udyog | Rajastan | KCX2 | 3364K1926 | 2772165441 | 2021-12-03 | 277216 | 2021-12-03 | oil carry over | 2020-02-12 | 2020-06-02 | 2970 | Inhouse | ice plant | 5 | Replaced ORV -2 Nos. | null | closed | Replaced ORV 2 Nos.
2022-02-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Petropill Ice Products | Kerala | KCX3 | 3374K2493 | 2879185610 | 2022-02-04 | 287918 | 2022-02-04 | oil carry over | 2021-02-02 | 2021-07-30 | 3801 | Inhouse | ice plant | 5 | Piston ring set replaced 2 nos. | null | closed | Piston ring set replaced 2 nos.
2022-02-16 | Multivista Global Pvt Ltd | New Delhi | D | Ay Enterprises | Rajastan | KCX3 | 3374K2657 | 2804305530 | 2022-01-05 | 280430 | 2021-12-24 | pressure gauge out | 2021-08-28 | 2021-12-21 | 4 | Supplier | ice plant | 4 | Replaced Pressure gauge 16.0 kg/cm2 | null | closed | Replaced Pressure gauge 16.0 kg/cm2
2022-02-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Iceberg Ice Plant | Kerala | KCX3 | 3374K2623 | 2873745598 | 2022-02-01 | 287374 | 2022-01-31 | delivery valve leakagestroke limitor step mark | 2021-08-01 | 2021-11-30 | 531 | Supplier | ice plant | 4 | Replaced delivery valve assly | null | closed | Replaced delivery valve assly
2022-02-21 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Sajjan India Limited | Gujrat | KCX93 | 3485K069 | Email | 2022-02-07 | null | 2022-02-07 | piston crack | 2019-12-10 | 2020-11-02 | Out of warranty | Supplier | chemical | 11 | Replaced Piston 4 nos. | null | closed | Replaced Piston 4 nos.
2022-02-21 | Iran | null | E | Mashhad Project | Iran | KCX6 | null | Email | 2022-01-02 | null | 2022-01-02 | oil carry over | null | null | null | Inhouse | cold storage | null | Replaced Piston,piston ring set,liner,delivery valve | null | closed | Replaced Piston,piston ring set,liner,delivery valve
2022-02-23 | Trade Links | Goa | D | The Coutband Fishries Co Operative Society | Goa | KCX3 | 3374K2345 | 2869525593 | 2022-01-29 | 286952 | 2022-01-29 | cylinder overheating & knocking sound | 2020-07-18 | 2020-08-26 | 6846 | Supplier | ice plant | 1 | Replaced Safety valve spring | null | closed | Replaced Safety valve spring
2022-02-23 | Parag Marketing Services | null | D | Walwa Shirala Co Op Dairy Ltd | Sangli | KCX1 | 3354K223 | 2890305625 | 2022-02-09 | 289030 | 2022-02-09 | oil pump air purging problem | 2021-09-29 | 2021-11-25 | 478 | Inhouse | ice plant | 3 | Oil pump air purging problem | null | closed | Replaced oil pump assly
2022-02-23 | Kalp Marketing | Gujrat | D | Bhopal Glues & Chemical Pvt Ltd | Madhya Pradesh | KCX3 | 3374K2574 | 2879545644 | 2022-02-15 | 287954 | 2022-02-05 | over heating | 2021-06-11 | 2021-09-30 | 215 | Inhouse | chemical / pharma | 4 | Delivery valve leakage | null | closed | Replaced Delivery valve 1 no.
2022-02-23 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX6 | 3394K1742 | 2833905545 | 2022-01-11 | 283390 | 2022-01-10 | over heating | 2021-01-29 | 2021-07-07 | 1950 | Inhouse | chemical / pharma | 7 | Cyl no. overheating due to delivery valve leakage | null | closed | Replaced Delivery valve 1 no.
2022-02-28 | Model Pneumatic Co | Punjab | D | Sai All Season Fruits And Vegetables | Himachal Pradesh | KCX72 | 3474K513 | 2857485579 | 2022-01-24 | 285748 | 2022-01-24 | discharge temprature sensor not working | 2021-11-30 | 2022-01-24 | 2 | Supplier | cold storage | 2 | Replaced Discharge Temparature sensor | null | closed | Replaced Discharge Temparature sensor
2022-02-28 | Multivista Global Pvt Ltd | null | D | Sk Logistic | New Delhi | KCX21 | 3424K125 | 2901525647 | 2022-02-16 | 290152 | 2022-02-15 | discharge valve leakage | 2021-05-29 | 2021-08-20 | 2087 | Inhouse | cold storage | 3 | Replaced discharge valve assly | null | closed | Replaced discharge valve assly
2022-02-28 | Geekay Pneumatic Pvt Ltd | Kerala | D | Gt George Ice Plant | Kerala | KCX2 | 3364K2083 | 2852285571 | 2022-01-21 | 285228 | 2022-01-20 | high oil carryover | 2021-02-08 | 2021-10-09 | 1021 | Inhouse | ice plant | 8 | Replaced piston ring set-2nos. | null | closed | Replaced piston ring set2nos.
2022-02-28 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX4 | 3384K2898 | 2906585652 | 2022-02-19 | 290658 | 2022-02-19 | discharge valve leakage | 2021-09-06 | 2022-01-05 | 800 | Inhouse | chemical / pharma | 3 | Replaced discharge valve assly | null | closed | Replaced discharge valve assly
2022-02-28 | Multivista Global Pvt Ltd | null | D | Jay Emm Gases Pvt Ltd | Uttar Pradesh | KC93 | 348K0159 | 2900985660 | 2022-02-21 | 290098 | 2022-02-25 | kc oil pressure problem | 2021-06-30 | 2021-12-30 | 880 | Inhouse | chemical / pharma | 6 | Kc oil pump low oil pressure | null | closed | Replaced oil pump assly
2022-03-08 | Trade Links | Secunderabad | D | Kala Agro Cold Storage | Andhra Pradesh | KCX3 | 3374K2484 | 2913685685 | 2022-03-01 | 291368 | 2022-03-01 | kcx oil pump purging | 2021-01-22 | 2021-02-15 | 3678 | Supplier | cold storage | 1 | Replaced oil pump | null | closed | Replaced oil pump
2022-03-08 | Kalp Marketing | Gujrat | D | Jay Shree Ambe Cold Storage | Gujrat | KCX3 | 3374K2550 | 2879425673 | 2022-02-21 | 287942 | 2022-02-21 | paper filter placed at suction filter housisng instead of wire filter in compressor. | 2021-08-28 | 2022-02-21 | 2 | Inhouse | cold storage | 6 | Replaced paper filter | null | closed | Replaced paper filter
2022-03-08 | Geekay Pneumatic Pvt Ltd | Kerala | D | Choice Trading Cooperation Pvt Ltd | Kerala | KCX72 | 3474K455 | 2906525663 | 2022-02-22 | 290652 | 2022-02-21 | high oil carryover | 2021-03-28 | 2021-07-25 | 3689 | Inhouse | food processing | 4 | Replaced piston ring set-9,piston-1,cylinder liner-1 | null | closed | Replaced piston ring set9,piston1,cylinder liner1
2022-03-08 | Trade Links | Secunderabad | D | V J Sai Chem | Telangana | KCX63 | 3464K138 | 2890665668 | 2022-02-23 | 289066 | 2022-02-10 | high oil carryover | 2021-10-20 | 2021-12-29 | 492 | Inhouse | chemical / pharma | 2 | Replaced piston ring sets-5nos. | null | closed | Replaced piston ring sets5nos.
2022-03-16 | Multivista Global Pvt Ltd | Gurgaon | D | Arkayee Agrotech & Cold Storage Pvt Ltd | Haryana | KCX3 | 3374K2649 | 2927465715 | 2022-03-10 | 292746 | 2022-03-10 | cylinder overheatingdischarge valve leakage | 2021-08-27 | 2021-11-18 | 484 | Inhouse | cold storage | 3 | Replaced discharge valve assly | null | closed | Discharge valve assembly1
2022-03-16 | Multivista Global Pvt Ltd | Gurgaon | D | Hargovind Das Agro Farms | Uttar Pradesh | KC4 | 338K5763 | 2912145688 | 2022-03-02 | 291214 | 2022-03-02 | kit thermowell assly not received at site | 2021-12-28 | 2022-03-02 | 4 | Inhouse | cold storage | 3 | Kit thermowell assly not received at field | null | closed | null
2022-03-16 | Cool Comfort Private Limited | West Bengal | D | Maa Jharbhoni Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K1894 | 2919625696 | 2022-03-04 | 291962 | null | pressure gauge not working | 2021-12-10 | 2021-03-04 | 0 | Supplier | cold storage | 3 | Replaced 16.0 kg/cm presure gauge | null | closed | Pressure gauge 16.0 kg/cm2
2022-03-16 | Multivista Global Pvt Ltd | Gurgaon | D | M K Proteins Ltd | Haryana | KCX3 | 3374K2584 | 2911465676 | 2022-02-25 | 291146 | 2022-02-24 | cylinder overheatingdischarge valve leakage | 2021-06-30 | 2021-10-11 | 593 | Inhouse | food processing | 4 | Replaced Del valve kit | null | closed | Del Valve kit
2022-03-16 | Model Pneumatic Co | Punjab | D | Perfect Poultry Products Pvt Ltd | null | KCX3 | 3374K2589 | 2910665695 | 2022-03-04 | 291066 | 2022-02-23 | discharge valve leakage | 2021-06-30 | 2022-01-26 | 250 | Inhouse | food processing | 7 | Replaced del valve kit due to leakage | null | closed | Replaced del valve kit.
2022-03-16 | Hss Solution Pvt Ltd | Rajasthan | D | ASAgro Foods | Rajastan | KCX1 | 3354K226 | 2920485707 | 2022-03-09 | 292048 | 2022-03-07 | discharge valve leakvalve kit broken | 2021-10-18 | 2021-11-16 | 436 | Supplier | ice plant | 1 | Replaced del valve kit | null | closed | Replaced del valve kit
2022-03-16 | Geekay Pneumatic Pvt Ltd | Kerala | D | Thottakam Ice Plant | Kerala | KCX3 | 3374K2361 | 2906285651 | 2022-02-19 | 290628 | 2022-02-18 | shaft seal leakage | 2020-08-11 | 2021-04-09 | 4276 | Supplier | ice plant | 8 | Replaced shaft seal assly | null | closed | Shaft seal assly
2022-03-16 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Aarti Drugs Limited | Boisar,Maharashtra | KCX3 | 3374K2660 | 2863365621 | 2022-02-08 | 286336 | 2022-01-28 | oil carry over | 2021-08-29 | 2021-10-12 | 3565 | Supplier | chemical / pharma | 1 | Replaced piston ring sets and VLD orings-3 | null | closed | Piston ring sets and VLD Orings3
2022-03-22 | Kalp Marketing | Gujrat | D | Natraj Cold Storage | Deesa | KCX4 | 3384K2977 | Email | 2022-03-10 | null | 2022-03-10 | flywheel paint peel off | 2022-01-18 | 2022-02-17 | 0 | Inhouse | cold storage | 1 | Paint rectified at site | null | closed | null
2022-03-22 | Trade Links | Secunderabad | D | Raithana Cold Storage | Andhra Pradesh | KCX3 | 3374K2724 | 2925045719 | null | 292506 | 2022-03-12 | key loose in c.shaft keyway | 2021-12-19 | 2022-03-12 | 20 | Inhouse | cold storage | 3 | Replace key | null | closed | Key
2022-03-22 | Trade Links | Secunderabad | D | Raithana Cold Storage | Andhra Pradesh | KCX3 | 3374K2725 | 2925065720 | 2022-03-14 | 292504 | 2022-03-12 | key loose in c.shaft keyway | 2021-12-19 | 2022-03-12 | 8 | Inhouse | cold storage | 3 | Replaced key | null | closed | Key
2022-03-22 | Kirloskar South East Asia Co Ltd | Thailand | E | Ksea | Thailand | KCX9 | 3404K0219 | Email | 2022-03-04 | null | 2022-03-04 | stop valve leakage | 2021-11-01 | 2022-03-04 | 0 | Supplier | cold storage | 5 | Replaced stop valve TAL100, FLANGE 125NB Both Side (Part no.: 085.09.700.50) | null | closed | Replaced stop valve TAL100, Part no.: 085.09.700.50
2022-03-28 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Aqua | Ratnagiri | KCX31 | 3434K0175 | email | 2022-03-25 | null | 2022-03-25 | paint peel off | 2021-10-20 | 2022-03-20 | 0 | Inhouse | cold storage | 5 | Painting done at field | null | closed | null
2022-03-28 | Multivista Global Pvt Ltd | Gurgaon | D | Kisanputra Cold Storage Agritech Pvt Ltd | Uttar Pradesh | KC3 | 337K4811 | 2912285725 | 2022-03-15 | 291228 | 2022-03-14 | solenoid valve coil burnt | 2022-01-09 | 2022-03-14 | 2 | Supplier | cold storage | 2 | Replaced sol valve coil | null | closed | Replaced sol valve coil
2022-03-28 | Multivista Global Pvt Ltd | Gurgaon | D | Ehsas Frozen Foods | Uttarakhand | KC63 | 346K290 | 2940085741 | 2022-03-22 | 294008 | 2022-03-21 | kc oil pressure problem | 2022-10-01 | 2021-12-16 | 581 | Supplier | food processing | 2 | Replaced KC oil pump | null | closed | Replaced KC oil pump
2022-03-28 | Kalp Marketing | Gujrat | D | Alps Exim Pvt Ltd | Gujrat | KCX72 | 3474K413 | 2920085716 | 2022-03-10 | 292008 | 2022-03-10 | shaft seal leakage | 2020-10-23 | 2021-01-23 | 2771 | Supplier | food processing | 3 | Replaced shaft seal oring kit | null | closed | Replaced shaft seal oring kit
2022-03-28 | Kalp Marketing | Gujrat | D | Shabir Ice Factory | Gujrat | KCX3 | 3374K2417 | 2910385672 | 2022-02-24 | 291038 | 2022-02-23 | shaft seal leakage | 2020-11-06 | 2021-04-28 | 2047 | Supplier | ice plant | 6 | Replaced shaft seal oring kit | null | closed | Replaced shaft seal oring kit
2022-03-28 | Kalp Marketing | Gujrat | D | Sagar Food | Gujrat | KCX72 | 3474K474 | 2896145714 | 2022-03-10 | 289614 | 2022-03-10 | high oil consumption | 2021-07-28 | 2021-10-05 | 772 | Inhouse | meat/fish process | 3 | Replaced piston ring sets-5 & VLD oring -9 | null | closed | Replaced piston tring sets5 & VLD oring 9
2022-03-28 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX63 | 3364K121 | 2923985709 | 2022-03-09 | 292398 | 2022-03-08 | shaft seal leakage | 2021-03-26 | 2021-11-26 | 496 | Supplier | chemical / pharma | 8 | Replaced shaft seal oring kit | null | closed | Replaced shaft seal oring kit
2022-03-30 | Multivista Global Pvt Ltd | Gurgaon | D | Madan Cold Storage | Uttar Pradesh | KC6 | 339K3637 | 2940525744 | 2022-03-23 | 294052 | 2021-03-22 | kc oil pump tang broken | 2022-01-29 | 2022-03-14 | 60 | Supplier | cold storage | 1 | Replaced KC gear kit | null | closed | Replaced KC oil pump gear kit with cvoer
2022-03-30 | Parag Marketing Services | null | D | Sanjog Cold Sorage | Satara | KCX42 | 3444K269 | 2909185657 | 2022-02-21 | 290918 | 2022-02-21 | shaft seal leakage | 2021-02-20 | 2021-07-23 | 2198 | Supplier | cold storage | 4 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2022-03-30 | Multivista Global Pvt Ltd | Gurgaon | D | Huma Cold Storage | Uttar Pradesh | KC6 | 339K3631 | 2925025711 | 2022-03-09 | 292502 | 2022-03-09 | solenoid valve not working | 2021-12-19 | 2022-03-07 | 2 | Supplier | cold storage | 1 | Replaced sol valve assly | null | closed | Replaced sol valve assly
2022-03-30 | Parag Marketing Services | null | D | Mauli Fresh Agro | Ahmed Nagar | KCX4 | 3384K2503 | 2905565721 | 2022-03-14 | 290556 | 2022-02-17 | overheating problem | 2020-02-23 | 2021-07-15 | 1514 | Inhouse | dairy / ice cream | 17 | Replaced Piston,liner,piston ring set replaced | null | closed | Replaced Piston,liner,piston ring set replaced
2022-03-30 | Multivista Global Pvt Ltd | Gurgaon | D | M K Proteins Ltd | Haryana | KCX3 | 3374K2584 | 2918985693 | 2022-03-04 | 291898 | 2022-03-04 | cylinder overheating | 2021-06-30 | 2021-10-11 | 648 | Inhouse | food processing | 4 | Replaced discharge valve assly | null | closed | Replaced discharge valve assly
2022-03-30 | Pragya Industrial Supply | Karnataka | D | Abhimanya Ice Plant | Karnataka | KCX4 | 3384K2817 | 2867365595 | 2022-01-30 | 286736 | 2022-01-29 | cylinder overheating | 2021-07-19 | 2021-11-27 | 335 | Inhouse | ice plant | 3 | Replaced discharge valve,piston,piston ring set-1 | null | closed | Replaced discharge valve,piston,piston ring set1
2022-03-30 | Trade Links | Secunderabad | D | Cofoods Processing Pvt Ltd | Andhra Pradesh | KCX6 | 3394K1880 | 2933285733 | 2022-03-17 | 293328 | 2022-03-17 | krms panel issue | 2021-09-29 | 2021-12-21 | 432 | Supplier | ice plant | 3 | Replaced Controller board | null | closed | Replaced Controller board
2022-03-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Jaylakshmi Ice Plant | Tamil Nadu | KCX4 | 3384K2845 | 286445544 | 2022-01-11 | 284644 | 2022-01-10 | stop valve leakage | 2021-08-06 | 2022-01-08 | 22 | Supplier | ice plant | 5 | Replaced stop valve | null | closed | Replaced stop valve TAL 70/80 Inlet
2022-03-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Swami Chickens | Tamil Nadu | KCX6 | 3394K1582 | 2940105743 | 2022-03-22 | 294010 | 2022-03-22 | krms panel issue | 2020-07-22 | 2021-10-26 | 100 | Supplier | meat/fish process | 15 | Replaced controller | null | closed | Replaced controller
2022-03-30 | Kalp Marketing | Gujrat | D | Shyam Marine Foods | Veraval, Gujarat | KCX72 | 3474K465 | 2918965708 | 2022-03-09 | 291896 | 2022-03-08 | oil carry over | 2021-04-26 | 2021-11-01 | 876 | Inhouse | meat/fish process | 7 | Replaced piston ring set & VLD orings | null | closed | Replaced piston ring set & VLD orings
2022-03-30 | Trade Links | Secunderabad | D | Ceyone Life Science Pvt Ltd | Andhra Pradesh | KCX6 | 3394K1856 | 2940565745 | 2022-03-23 | 294056 | 2022-03-22 | kcx oil pump tang broken | 2020-10-26 | 2021-06-18 | 326 | Supplier | chemical / pharma | 8 | Replaced KCX oil pump assly | null | closed | Repalced KCX oil pump assly1
2022-04-19 | Cool Comfort Private Limited | West Bengal | D | Bengal Beverage Pvt Ltd | West Bengal | KCX6 | 3394K1809 | 2941465748 | 2022-03-24 | 294146 | 2022-03-23 | hr meter & tdv damaged | 2021-06-29 | 2022-01-19 | 0 | null | beverage / breweries | 7 | Hr meter & TDV damaged. Low suction, | null | closed | Replaced Hr meter & TDV
2022-04-19 | Trade Links | Secunderabad | D | Foster Cold Storage Pvt Ltd | Telangana | KCX42 | 3444K320 | 2943525754 | 2022-03-28 | 294352 | 2022-03-26 | cylinder overheating | 2021-12-29 | 2022-03-19 | 86 | null | cold storage | 3 | Delivery valve leakage , piston , piston ring , liner , buffer spring , gudgen pin damaged. | null | closed | Replaced Delivery valve leakage , piston , piston ring , liner , buffer spring , gudgen pin
2022-04-19 | Cool Comfort Private Limited | West Bengal | D | Gour Netai Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K1930 | 2950465758 | 2022-03-30 | 295046 | 2022-03-29 | cylinder overheating | 2021-12-31 | 2022-03-14 | 389 | null | cold storage | 3 | Cylinder seized , damaged piston , piston rings & liner , DV etc. | null | closed | Replaced Liner , piston , piston ring set , delivery valve , gudeon pin , bush con rod etc.
2022-04-19 | Model Pneumatic Co | Punjab | D | Shri Ram Farm And Cold Storage | Punjab | KCX4 | 3384K2995 | 2931845757 | 2022-03-30 | 293184 | 2022-03-29 | krms sensor problem | 2022-01-28 | 2022-03-29 | 0 | Supplier | cold storage | 1 | Disch & suction pressure sensor not working & CCSV2 Coil malfuctioning. | null | closed | Replaced Disch & suction pressure sensor & CCSV2 Coil.
2022-04-19 | Multivista Global Pvt Ltd | Gurgaon | D | Bahubali Cold Storage | Uttar Pradesh | KC4 | 338K5751 | 2876985654 | 2022-02-21 | 287698 | 2022-02-19 | pressure gauge not working | 2021-08-30 | 2022-02-19 | 1 | null | cold storage | 6 | Pressure gauge 16.00kg/cm2 not working | null | closed | Replaced Pressure gauge 16.00kg/cm2
2022-04-19 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Durga Cold Storage & Ice Factory | Uttar Pradesh | KCX3 | 3374K2784 | 2932705730 | 2022-03-16 | 293270 | 2022-03-15 | pressure gauge not working | 2022-02-07 | 2022-03-15 | 6 | null | cold storage | 1 | Pressure gauge 16.00kg/cm2 not working | null | closed | Replaced Pressure gauge 16.00kg/cm2
2022-04-19 | Multivista Global Pvt Ltd | Gurgaon | D | Shiv Foods | Uttar Pradesh | KC4 | 338K5762 | 2920825742 | 2022-03-22 | 292082 | 2022-03-22 | pressure gauge not working | 2021-12-25 | 2022-03-22 | 30 | null | cold storage | 3 | Discharge pressure gauge not working | null | closed | Replaced discharge pressure gauge 025Kg/cm2
2022-04-19 | Multivista Global Pvt Ltd | Gurgaon | D | DJ Exports Pvt Ltd | New Delhi | PCX2 | 3106K0075 | 2933345751 | 2022-03-25 | 293334 | 2022-03-25 | shaft seal leakage | 2021-02-09 | 2021-08-16 | 1762 | null | cold storage | 6 | Shaft seal leakage (R22 Gas) | null | closed | Replaced Oring set
2022-04-19 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX4 | 3384K2720 | 2942865752 | 2022-03-28 | 294286 | 2022-03-26 | oil pressure problem | 2021-02-27 | 2021-11-20 | 735 | null | food processing | 9 | Drive shaft jammed & broken | null | closed | Replaced pump assembly
2022-04-19 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Yogeshwar Ice And Cold Storage | Gujrat | KCX3 | 3374K2696 | 2931625727 | 2022-03-15 | 293162 | 2022-03-15 | loading unloading problemsolenoid valve malfunctioning | 2021-11-16 | 2021-12-11 | 2 | null | ice plant | 1 | Solenoid valve not working | null | closed | Replaced NC Solenoid valve assly
2022-04-19 | Trade Links | Secunderabad | D | Sri Karthikeya Ice Plant | Andhra Pradesh | KCX4 | 3384K2909 | 2924385768 | 2022-04-04 | 292438 | 2022-04-01 | oil pump tang broken | 2021-10-29 | 2022-04-01 | 4 | Supplier H21 059 LDK | ice plant | 6 | Oil pump tang broken witin 1 hr | null | closed | Replaced KCX pump assly
2022-04-19 | Multivista Global Pvt Ltd | Gurgaon | D | Al Naved Agro Foods Industries Pvt Ltd | Haryana | KCX72 | 3474K428 | 2950765760 | 2022-03-31 | 295076 | 2022-03-29 | oil carry over | 2020-12-14 | 2022-01-23 | 845 | null | meat/fish process | 12 | OP Cutout and Pressure gauge not working/defective. | null | closed | Replaced OP Cutout & Pressure gauge 16 Kg/cm2
2022-04-30 | Cool Comfort Private Limited | West Bengal | D | Pioneer Himudyog Pvt Ltd | West Bengal | KCX4 | 3384K3009 | 2986325793 | 2022-04-15 | 298632 | 2022-04-14 | abnormal noise | 2022-02-09 | 2022-03-16 | 190 | null | cold storage | 1 | Replaced Delivery valve kit | null | closed | null
2022-04-30 | Kalp Marketing | Gujrat | D | Nestle India Ltd | Gujrat | KCX4 | 3384K2639 | 2995145805 | 2022-04-20 | 299514 | 2022-04-20 | kcx oil pump assly purging | 2020-12-11 | 2021-08-13 | 2453 | null | food processing | 8 | Replaced oil pump assly | null | closed | Replaced oil pump assly
2022-04-30 | Kalp Marketing | Gujrat | D | Nestle India Ltd | Gujrat | KCX4 | 3384K2638 | 2995165806 | 2022-04-20 | 299516 | 2022-04-20 | oil pressure problemoil pump assly | 2020-12-11 | 2021-08-13 | 2237 | null | food processing | 8 | Replaced oil pump assly | null | closed | Replaced oil pump assly
2022-04-30 | Parag Marketing Services | null | D | Graviss Food Pvt Ltd | Satara | KCX3 | 3374K2695 | Email | 2022-04-29 | null | 2022-04-29 | paint peel off at cylinder no.3 | 2021-11-30 | 2022-04-27 | 6 | null | food processing | 5 | Paint peel off at cylinder no 03 | null | open | Paint to be sent for rectification
2022-04-30 | Kalp Marketing | Gujrat | D | Rameshwar Ice & Cold Storage | Jafrabad | KCX4 | 3384K2819 | Email | 2022-04-08 | null | 2022-04-08 | c.case foot welding leakage/crack | 2021-07-24 | 2022-01-17 | 368 | null | ice plant | 6 | Compressor foot crack - compressor sent back to KPCL for rectification | null | closed | null
2022-04-30 | Trade Links | Goa | D | Mandovi Ice Plant | Goa | KCX3 | 3374K2569 | 2931285747 | 2022-03-23 | 293128 | 2022-03-14 | cylinder overheating | 2021-05-09 | 2021-08-07 | 4386 | null | ice plant | 3 | Delivery valve leakage | null | closed | Replaced del valve assly
2022-04-30 | Trade Links | Goa | D | Niranjan Industries | Goa | KCX4 | 3384K2765 | 293125746 | 2022-03-23 | 293212 | 2022-03-17 | oil carry over | 2021-04-30 | 2021-08-02 | 48135 | null | ice plant | 4 | Replaced piston ring set-4nos | null | closed | Replaced piston ring set4nos
2022-04-30 | Parag Marketing Services | null | D | Kabir Ice Factory Bharuch Gujarat | null | KCX4 | 3384K2873 | Email | 2022-04-29 | null | 2022-04-29 | paint peel of at vld housing of cylinder no 1 | 2021-08-27 | 2022-04-27 | 16 | null | ice plant | 8 | Paint peel of at VLD housing of cylinder no 1 | null | open | Paint to be sent for rectification
2022-04-30 | Parag Marketing Services | null | D | Mv9 Hospitality | Pune | PCX2 | 3106K0079 | 2833985577 | 2022-01-24 | 283398 | 2022-01-21 | shaft seal leakage r22 | 2021-02-28 | 2021-03-30 | PC | null | ice plant | 1 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2022-04-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vasai Frozen Foods | Bhivandi | KCX42 | 3444K282 | 2950725763 | 2022-03-31 | 295072 | 2022-03-29 | discharge valve assembly | 2021-03-27 | 2021-08-30 | 2339 | null | meat/fish process | 5 | Replaced discharge valve assly | null | closed | Replaced discharge valve assly
2022-04-30 | Cool Comfort Private Limited | West Bengal | D | Aquatech Feed & Sea Foods Pvt Ltd | West Bengal | KCX4 | 3384K2659 | 2997945811 | 2022-04-22 | 299794 | 2022-04-22 | oil pressure problemoil pump assly | 2020-12-31 | 2021-11-19 | 35 | null | meat/fish process | 11 | Replaced oil pump assly | null | closed | Replaced KCX oil pump assly
2022-04-30 | Cool Comfort Private Limited | West Bengal | D | Aquatech Feed & Sea Foods Pvt Ltd | West Bengal | KCX12 | 3415K0026 | 2997885810 | 2022-04-22 | 299788 | 2022-04-22 | oil pressure problemtang broken | 2020-12-31 | 2021-11-18 | 293 | null | meat/fish process | 11 | Replaced oil pump element | null | closed | KCX oil pump element
2022-05-10 | S B Refrigeration | Bihar | D | Varun Beverage Limited | Bihar | KCX9 | 3404K201 | 3024265832 | 2022-05-04 | 302426 | 2022-05-03 | abnormal noise | 2021-08-24 | 2022-01-30 | 217 | null | beverage / breweries | 5 | System problem. Discharge valve leak , liner , piston , piston rring sets , gudgeon pin changed. | null | closed | Replaced kit delivery valve ,liner , piston , piston rring sets , gudgeon pin
2022-05-10 | Multivista Global Pvt Ltd | null | D | D J Exports Pvt Ltd | New Delhi | PCX2 | 3106K0075 | 3006425817 | 2022-04-26 | 300642 | 2022-04-26 | suction filter hsg leakage | 2021-02-09 | 2021-08-16 | 1765 | null | cold storage | 6 | Suction filter hsg leakage | null | closed | Replaced Suction filter hsg
2022-05-10 | Trade Links | null | D | Kurnool Dist Milk Producers Mutually Aided Co-Op Union Ltd | Andhra Pradesh | KCX2 | 3364K2114 | 2999665814 | 2022-04-25 | 299966 | 2022-04-22 | oil lifting | 2021-03-12 | 2021-06-23 | 2333 | null | dairy / ice cream | 3 | ORV leakage replaced | null | closed | ORV leakage 2 nos replaced
2022-05-10 | Gargi Engineering Enterprices Pvt Ltd | null | D | Uma Akash Argro Pvt Ltd | Gujrat | KCX31 | 3434K0160 | 2994665801 | 2022-04-19 | 299466 | 2022-04-21 | over heating | 2021-07-30 | 2021-09-29 | 7 | null | food processing | 2 | Delivery valve leakage due to stroke limitor step marks & Buffer spring shrink due to overheating. | null | closed | Replaced delivery valve assly 2 & Buffer spring 1
2022-05-10 | Geekay Pneumatic Pvt Ltd | Kerala | D | Fathima Ice Industries | Kerala | KCX2 | 3364K2559 | 2994785826 | 2022-04-30 | 299478 | 2022-04-30 | oil carry over | 2022-01-31 | 2022-03-04 | 630 | null | ice plant | 3 | Suction stroke limitor damage & step mark in delivery stroke limitor. | null | closed | Replaced suction stroke limitor , delivery stroke limitor & Kit
2022-05-10 | Multivista Global Pvt Ltd | null | D | Radhika Dairy | Uttar Pradesh | KCX2 | 3364K2160 | 2988605797 | 2022-04-18 | 298860 | 2022-04-17 | oil lifting | 2021-06-30 | 2021-10-31 | 979 | null | ice plant | 4 | ORV leakage replaced | null | closed | ORV leakage 1 no replaced
2022-05-10 | Cool Comfort Private Limited | West Bengal | D | Maa Kali Enterprises | West Bengal | KCX2 | 3364K2077 | 3007565824 | 2022-04-28 | 300756 | 2022-04-26 | overheating piston crack | 2021-01-25 | 2021-06-13 | 2472 | null | ice plant | 5 | Piston crack & Piston ring set wornout 01 no each replaced. | null | closed | Piston crack & Piston ring set wornout 01 no each replaced.
2022-05-10 | Kalp Marketing | Gujrat | D | Godrej Consumer Products Ltd | Madhya Pradesh | KCX3 | 3374K2576 | 3006885820 | 2022-04-27 | 300688 | 2022-04-27 | oil pressure not buildup | 2021-06-14 | 2021-12-08 | 1765 | D20 006 LDK | chemical / pharma | 6 | Element broken | null | closed | Replaced pump element
2022-05-21 | Kalp Marketing | Gujrat | D | Chaudhary Ice & Cold Storage | Madhya Pradesh | KCX4 | 3384K2965 | 3024485856 | 2022-05-16 | 302448 | 2022-05-14 | high oil consumption | 2022-01-11 | 2022-03-28 | 376 | null | cold storage | 2 | Cylinder no.1 & 3 oil throw observed. Liner & Piston wornout. | null | closed | Replaced Piston , Liner & Piston ring set 2 nos
2022-05-21 | Multivista Global Pvt Ltd | Chennai | D | Flex Foods Ltd | Tamil Nadu | KCX42 | 3444K305 | 3037605846 | 2022-05-10 | 303760 | 2022-05-13 | knocking / abnormal sound | 2021-09-28 | 2022-02-07 | 316 | null | cold storage | 5 | System issue - HP Stariner chocked due to heavy system dirt. Strainer filter mesh damaged. | null | closed | Replaced suction strainer filter element.
2022-05-21 | Multivista Global Pvt Ltd | Chennai | D | Flex Foods Ltd | Tamil Nadu | KCX9 | 3404K218 | 3034865845 | 2022-05-09 | 303486 | 2022-05-10 | oil pressure problem | 2021-11-26 | 2022-05-10 | 4 | null | cold storage | 6 | System issue - Liquid entry in compressor & High vibrations | null | closed | Replaced pump element
2022-05-21 | Trade Links | Secunderabad | D | H & S Cold Storage | Andhra Pradesh | KCX3 | 3374K2495 | 3040865852 | 2022-05-13 | 304086 | 2022-05-17 | oil presure issue tang broken | 2021-01-31 | 2022-01-29 | 1593 | null | cold storage | 12 | System issue - Observed liquid ammonia in compressor , pump tang broken. LC 01 21 567 | null | closed | Replaced pump assly
2022-05-21 | Multivista Global Pvt Ltd | Chennai | D | Flex Foods Ltd | Tamil Nadu | KCX9 | 3404K225 | 3034885844 | 2022-05-09 | 303488 | 2022-05-10 | over heating | 2021-11-27 | 2021-05-10 | 5 | null | cold storage | 6 | System issue - Liquid entry in compressor & High vibrations | null | closed | Replaced cylinder assly
2022-05-21 | Cool Comfort Private Limited | West Bengal | D | Shree Modan Mohan Cold Storage | West Bengal | KCX6 | 3394K1887 | 3029805838 | 2022-05-07 | 302980 | 2022-05-08 | overheat & abnormal sound | 2021-10-30 | 2022-03-31 | 357 | null | cold storage | 5 | Cylinder seized , damaged piston , piston rings & liner , DV etc. | null | closed | Replaced Piston . Ring set , liner , suction & discharge valve rings , delivery valve assembly.
2022-05-21 | Multivista Global Pvt Ltd | Gurgaon | D | Prena Cold Storage & Allied Industries | Uttar Pradesh | KCX6 | 3394K1850 | 3030285840 | 2022-05-07 | 303028 | 2022-05-07 | overheating delivery valve leakage | 2021-08-27 | 2022-02-19 | 807 | null | cold storage | 6 | Dischage valve leakage | null | closed | Replaced DV01 No.
2022-05-21 | Multivista Global Pvt Ltd | Gurgaon | D | Kvg Agro Pvt Ltd | Haryana | KCX4 | 3384K2751 | 2956025761 | 2022-03-31 | 295602 | 2022-03-31 | oil carry over | 2021-03-27 | 2021-08-26 | 599 | null | dairy / ice cream | 8 | Piston ring wornout & cut mark in liner | null | closed | Replaced Liner , Piston & Piston ring set
2022-05-21 | Hss Solution Pvt Ltd | Rajasthan | D | Paschimi Rajasthan Dudh Utpadak Sangh | Rajastan | KCX6 | 3394K1817 | 2970665781 | 2022-04-11 | 297066 | 2022-04-09 | oil carry over | 2021-07-19 | 2022-01-07 | 598 | null | dairy / ice cream | 6 | System issue - Low suction pressure , system dirt in suction strainer , 01 delivery valve leakage. | null | closed | Replaced delivery valve assembly.
2022-05-21 | Hss Solution Pvt Ltd | Rajasthan | D | Vighnesh Dairy Plant | Rajastan | KCX4 | 3384K2610 | 2932325732 | 2022-03-16 | 293232 | 2022-03-16 | delivery valve leakage | 2020-11-01 | 2021-02-03 | 960 | null | ice plant | 3 | Cylinder no.1 overheating , disharge valve leakage due to seat wornout | null | closed | Replaced discharge valve assembly 1
2022-05-21 | Trade Links | Secunderabad | D | Arene Life Science Pvt Ltd | Telangana | KCX3 | 3374K2824 | 3038305853 | 2022-05-13 | 303830 | 2022-05-11 | shaft seal leakage | 2022-03-16 | 2022-04-22 | 328 | null | chemical / pharma | 1 | R22 Refrigerant . Shaft seal leakage. | null | closed | Replaced Shaft seal
2022-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Al Nasir Exports Pvt Ltd | Gurgaon | KC42 | 344K1145 | Email | 2022-06-04 | 305742 | 2021-11-11 | kc low oil pressure | 2021-10-03 | 2021-11-11 | WC | Supplier | cold storage | 1 | Cover plate lapping done | null | closed | null
2022-05-31 | Cool Comfort Private Limited | West Bengal | D | Baba Basantroy Cold Storage | West Bengal | KCX6 | 3394K1945 | Email | 2022-06-04 | 304108 | 2022-05-12 | leakage from 22 dia. kcx internal pipe and bearing cover fitting joint | 2022-01-23 | 2022-03-31 | WC | Inhouse | cold storage | 1 | Pipe length reduced | null | closed | null
2022-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Radhey Radhey Storage | Uttar Pradesh | KCX4 | 3384K2673 | 2956485843 | 2022-05-09 | 295648 | 2022-05-12 | oil carry over | 2021-01-09 | 2021-02-22 | 2140 | null | cold storage | 1 | Analysis not mentioned in FSR | null | closed | Replaced piston , piston rings ,liner , oil pump assly
2022-05-31 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Shree Krishna Cold Storage | Gujrat | KCX72 | 3374K2488 | Email | 2022-06-04 | 305984 | 2022-05-25 | oil carry over | 2021-01-25 | 2021-02-22 | WC | null | cold storage | 1 | Equilizing line installed | null | closed | null
2022-05-31 | Kalp Marketing | Gujrat | D | Supreme Construction | Gujrat | KCX3 | 3374K2640 | 3047605858 | 2022-05-17 | 304760 | 2022-05-17 | over heating | 2021-08-26 | 2022-03-25 | 63 | null | ice plant | 7 | Cylinder no.2 - Delivery valve leakage & step mark to stroke limitor. | null | closed | Replaced delivery valve assly
2022-05-31 | Cool Comfort Private Limited | West Bengal | D | Lokenath Ice Plant | West Bengal | KCX2 | 3364K2105 | Email | 2022-06-04 | 305692 | 2021-07-16 | piston crack | 2021-03-05 | 2021-07-16 | WC | Supplier | ice plant | 4 | Piston replaced | null | closed | Piston
2022-05-31 | Hss Solution Pvt Ltd | Rajasthan | D | Bansal Industries | Rajastan | KCX3 | 3374K2639 | 3034925857 | 2022-05-17 | 303492 | 2022-05-09 | pressure switch break kp5a | 2021-08-25 | 2022-05-09 | 4 | null | ice plant | 9 | Pressure switch break. | null | closed | Replaced Pressure switch KP5A.
2022-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Al Naved Agro Foods Industries Pvt Ltd | Haryana | KCX42 | 3444K251 | 2986285836 | 2022-05-05 | 268628 | 2022-05-05 | oil carry over | 2020-12-14 | 2021-11-28 | 966 | null | meat/fish process | 11 | Piston ring problem - 4 sets | null | closed | Replaced piston ring sets 4 nos.
2022-05-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Shree Datt Aquaculture Farms Ltd | Gujrat | KCX72 | 3474K400 | 3029345837 | 2022-05-05 | 302934 | 2022-05-05 | shaft seal leakage | 2020-09-30 | 2021-04-01 | 90 | Confusion in running hrs | meat/fish process | 7 | Shaft seal leakage due to deep scoring. | null | closed | Replaced shaft seal assembly
2022-05-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Alkem Labs Ltd Ankleshwar | Gujrat | KCX63 | 3464K126 | 3049725872 | 2022-05-27 | 304972 | 2022-05-27 | loading unloading problemsolenoid valve malfunctioning | 2021-05-19 | 2021-09-17 | 1670 | null | chemical / pharma | 4 | Improper loading -unloading due to solenoid valve malfuctioning might be resulted in overheating and got damaged entire cylinder . | null | closed | Replaced liner, piston , piston ring , solenoid valve , gudgeon pin , discharge valve , needle roller bearing etc.
2022-05-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Transpek Silox Inductries Pvt Ltd | Gujrat | KCX4 | 3384K2767 | 2990185800 | 2022-04-19 | 299018 | 2022-04-16 | over heating | 2021-04-30 | 2021-12-13 | 8 | null | chemical / pharma | 8 | Delivery valve leakage due to step mark to stroke limitor. | null | closed | Replaced discharge valve assembly
2022-06-18 | Model Pneumatic Co | Punjab | D | Archian Foods Pvt Ltd | Punjab | KCX9 | 3404K236 | 3079245894 | 2022-06-07 | 307924 | 2022-06-07 | pressure gauge not working | 2021-11-30 | 2022-06-07 | 4 | Supplier | beverage / breweries | 6 | Pressure gauge not working | null | closed | Pressure gauge 16.0 kg/cm2
2022-06-18 | Kalp Marketing | Gujrat | D | Mayank Industries | Madhya Pradesh | KCX4 | 3384K2755 | 3067045887 | 2022-06-03 | 306704 | 2022-06-03 | cylinder overheating | 2021-03-28 | 2021-08-19 | 526 | Supplier | cold storage | 5 | Replaced Delivery valve assly | null | closed | Del valve assly
2022-06-18 | Trade Links | Secunderabad | D | Sarwani Cold Storage | Andhra Pradesh | KCX2 | 3364K2275 | 3062665874 | 2022-05-27 | 306266 | 2022-05-27 | key loose in c.shaft keyway | 2022-02-22 | 2022-03-20 | 750 | null | cold storage | 1 | Key replaced | null | closed | Key
2022-06-18 | Kalp Marketing | Gujrat | D | Chaudhary Ice & Cold Storage | Madhya Pradesh | KCX4 | 3384K2965 | 30633365878 | 2022-05-30 | 306336 | 2022-05-30 | oil carry over | 2022-01-11 | 2022-03-28 | 430 | Inhouse | cold storage | 2 | Replaced piston,liner,ring set | null | closed | Replaced piston,liner,ring set
2022-06-18 | Parag Marketing Services | null | D | Kala Biotech Pvt Ltd | Khed, Maharashtra | KCX6 | 3394K1792 | 3093265899 | 2022-06-13 | 309326 | 2022-06-13 | oil separator leakage | 2021-04-20 | 2021-09-12 | 0 | Supplier | cold storage | 1 | Replaced 50D oil separator | null | closed | 50 D oil separator
2022-06-18 | Multivista Global Pvt Ltd | Gurgaon | D | D J Exports Pvt Ltd | New Delhi | PCX2 | 3106K0075 | 3069985889 | 2022-06-04 | 306998 | 2022-06-04 | oil strainer suction assembly welding leakage | 2021-02-09 | 2021-08-19 | 1847 | Inhouse | cold storage | 6 | Replaced oil strainer housing | null | closed | PCX2 oil strainer housing
2022-06-18 | Multivista Global Pvt Ltd | Gurgaon | D | Smc Foods Ltd | Uttar Pradesh | KCX9 | 3404K205 | 3077125891 | 2022-06-07 | 307712 | 2022-06-14 | oil carry over | 2021-09-29 | 2022-05-03 | 658 | null | dairy / ice cream | 8 | Piston ring set replaced | null | closed | Piston ring set
2022-06-18 | Trade Links | Secunderabad | D | Kurnool Dist Milk Producers Mutually Aided Co-Op Union Ltd | Andhra Pradesh | KCX2 | 3364K2114 | 3062345873 | 2022-05-27 | 306234 | 2022-05-26 | oil lifting | 2021-03-12 | 2021-06-23 | 2600 | Supplier | dairy / ice cream | 3 | Replaced Piston ring set | null | closed | Replaced Piston ring set
2022-06-18 | Multivista Global Pvt Ltd | Gurgaon | D | Naturagreen Foods Products | Uttar Pradesh | KCX4 | 3384K2882 | 3037665849 | 2022-05-12 | 303766 | 2022-06-02 | oil carry over | 2021-08-28 | 2022-01-10 | 2162 | Inhouse | food processing | 5 | Replaced Piston ring set | null | closed | Piston ring set
2022-06-18 | Kalp Marketing | Gujrat | D | Laakoonaa Reaction | Gujrat | KCX4 | 3384K2792 | 3059885875 | 2022-05-27 | 305988 | 2022-05-27 | cylinder overheating | 2021-06-23 | 2021-11-17 | 961 | Supplier | ice plant | 5 | Replaced Delivery valve assly,Piston,buffer spring,liner,ORV,piston ring set,Gudgeon pin | null | closed | Replaced Delivery valve assly,Piston,buffer spring,liner,ORV,piston ring set,Gudgeon pin
2022-06-18 | Model Pneumatic Co | Punjab | D | Rich Products & Solutions Pvt Ltd | Himachal Pradesh | KCX63 | 3464K103 | 3089705896 | 2022-07-09 | 308970 | 2022-07-09 | shaft seal leakage | 2021-01-12 | 2021-03-31 | 6406 | Supplier | ice plant | 2 | Replaced shaft seal assly | null | closed | Shaft seal assly
2022-06-18 | Multivista Global Pvt Ltd | Gurgaon | D | Al Naved Agro Foods Industries Pvt Ltd | Haryana | KCX72 | 3474K428 | 3029945842 | 2022-05-09 | 302994 | 2022-05-07 | oil carry over | 2020-12-14 | 2022-01-23 | 1667 | Inhouse | meat/fish process | 1 | Replaced piston ring set replaced | null | closed | Replaced piston ring set replaced
2022-06-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Shakti Bio Science Ltd | Gujrat | KCX6 | 3394K1774 | 2942005892 | 2022-06-07 | 294200 | 2022-03-27 | cylinder overheating | 2021-07-31 | 2022-01-31 | 24 | null | chemical / pharma | 6 | Delivery valve leakage | null | closed | Del.valve,piston liner
2022-06-22 | Cool Comfort Private Limited | West Bengal | D | Matri Bhumi Agritech LLP | West Bengal | KCX4 | 3384K3013 | 3100805906 | 2022-06-18 | 310080 | 2022-06-18 | high oil consumption | 2022-02-12 | 2022-03-12 | 910 | Inhouse | cold storage | 1 | Replaced Cylinder liner,piston, piston ring set | null | closed | Replaced Cylinder liner,piston, piston ring set
2022-06-22 | Geekay Pneumatic Pvt Ltd | Kerala | D | Choice Trading Cooperation Pvt Ltd | Kerala | KCX72 | 3474K455 | 3066845884 | 2022-06-03 | 306684 | 2022-06-02 | cylinder overheating | 2021-03-28 | 2021-07-25 | 5371 | Inhouse | food processing | 4 | Replaced Del valve assly-1 No. | null | closed | Replaced Del valve assly1 No.
2022-06-22 | Cool Comfort Private Limited | West Bengal | D | Nezami Rekha Sea FoodsPvt Ltd | West Bengal | KCX3 | 3374K2433 | 3095785904 | 2022-06-14 | 309578 | 2022-06-14 | high oil consumption | 2020-11-22 | 2021-06-25 | 2239 | Inhouse | meat/fish process | 7 | Replaced piston ring set | null | closed | Replaced piston ring set
2022-07-18 | Kalp Marketing | Gujrat | D | Ocean Aquatech Product | Gujrat | KCX51 | 3454K187 | 3120765969 | 2022-07-08 | 312076 | 2022-07-05 | over heating | 2021-03-27 | 2021-09-03 | 165 | Inhouse | meat/fish process | 6 | Replaced delivery valve kit . | null | closed | Replaced delivery valve kit .
2022-07-18 | Kalp Marketing | Gujrat | D | Sumra Exports | Gujrat | KCX51 | 3454K189 | 3133345966 | 2022-07-06 | 313334 | 2022-07-06 | over heating | 2021-05-30 | 2021-09-11 | 888 | Inhouse | meat/fish process | 4 | Cylinder no. delivery valve leakage | null | closed | Replaced delivery valve assembly.
2022-07-19 | S B Refrigeration | Bihar | D | Varun Beverage Limited | Bihar | KCX6 | 3394K1843 | 3113225934 | 2022-06-27 | 311322 | 2022-06-27 | over heating | 2021-08-24 | 2022-01-30 | 457 | Supplier | beverage / breweries | 5 | Overheating ..observations not mentioned in FSR | null | closed | Replaced Piston,piston ring set , cylinder liner, gudgeon pin , bearings ,delivery valve 1 no each & kit delivery valve 3 nos.
2022-07-19 | S B Refrigeration | Bihar | D | Sai Multi Cold Storage | Bihar | KCX4 | 3384K2560 | 3147585985 | 2022-07-15 | 314758 | 2022-07-15 | oil carry over piston crack | 2020-08-14 | 2021-04-02 | 3712 | Supplier | cold storage | 8 | Piston crack & oil carry over | null | closed | Replaced Piston
2022-07-19 | Multivista Global Pvt Ltd | null | D | Shri Radhey Radhey Cold Storage | Hathras ,Uttar Pradesh | KCX4 | 3384K2673 | 3057645914 | 2022-06-21 | 305764 | 2022-06-21 | oil carry over & abnormal sound | 2021-01-09 | 2021-02-22 | 2314 | Inhouse | cold storage | 1 | oil carry over issue due to liner cut marks | null | closed | Replaced Piston , piston ring sets & Liners 2 nos
2022-07-19 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | S R Agro Pvt Ltd | Nagpur | KCX3 | 3374K2807 | 3063065905 | 2022-06-17 | 303306 | 2022-06-11 | pressure gauge not working | 2022-02-27 | 2022-06-11 | 1 | Supplier | cold storage | 4 | Oil pressure gauge 16 kg/cm2 not working | null | closed | Replaced Pressure gauge 16 Kg/cm2
2022-07-19 | Multivista Global Pvt Ltd | null | D | Smc Foods Ltd | Uttar Pradesh | KCX9 | 3404K205 | 3112965938 | 2022-06-28 | 311296 | 2022-06-26 | oil carry over | 2021-09-29 | 2022-05-03 | 860 | Supplier | dairy / ice cream | 8 | Piston rings , liners wornout | null | closed | Replaced piston ring sets 4 nos.& Liner 2 nos.
2022-07-19 | Trade Links | null | D | Plr Foods Pvt Ltd | Andhra Pradesh | PCX2 | 3106K0155 | 3138665971 | 2022-07-09 | 313866 | 2022-07-09 | pc2 oil pump seized | 2022-03-27 | 2022-07-09 | 6 | Supplier | food processing | 4 | Oil pump seized within 6 hrs. | null | closed | Replaced pump assembly
2022-07-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Kanyalal & Company | Mumbai | KCX3 | 3374K2579 | 3098485909 | 2022-06-18 | 309848 | 2022-06-17 | oil carry over | 2021-06-29 | 2021-07-18 | 5649 | Inhouse | ice plant | 1 | Open oil throw from all cylinders , piston rings wornout , 1 liner found cut marks & piston scraches. | null | closed | Replaced liner & piston 1 no each & 3 Piston ring sets
2022-07-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Guru Nanak Refrigeration Services | Mumbai | KCX6 | 3394K1751 | 3088085908 | 2022-06-18 | 308808 | 2022-06-16 | oil carry over | 2021-02-19 | 2021-08-10 | 4964 | Inhouse | ice plant | 6 | Open oil throw from all cylinders , piston rings wornout , 2 liners found cut marks & piston scraches. | null | closed | Replaced liner,piston 2 nos each & piston ring sets 6 nos.
2022-07-19 | Kalp Marketing | Gujrat | D | Real Export | Gujrat | KCX3 | 3374K2535 | 3121325963 | 2022-07-06 | 312132 | 2022-07-05 | oil carry over | 2021-03-16 | 2021-05-25 | 486 | Inhouse | ice plant | 2 | Excess oil found in VLD ,Replaced VLD Orings. | null | closed | Replaced VLD Orings
2022-07-19 | Trade Links | null | D | Hanuman Ice Links | Andhra Pradesh | KCX4 | 3384K2979 | 3103365912 | null | 310336 | 2022-06-18 | over heating | 2022-01-19 | 2022-02-10 | 2820 | Inhouse | ice plant | 1 | Cylinder no.1 delivery valve leakage, ring spring damaged & cylinder seized. | null | closed | Replaced delivery valve assembly & cylinder assly parts.
2022-07-19 | Trade Links | null | D | Ratna Ice Factory | Andhra Pradesh | KCX4 | 3384K2753 | 3132665964 | 2022-07-06 | 313266 | 2022-07-05 | overheating & abnormal sound | 2021-03-28 | 2021-07-30 | 6035 | Supplier | ice plant | 4 | Cylinder no.2 - Delivery valve leakage & liner/piston seized. | null | closed | Replaced delivery valve assly & cylinder assembly parts.
2022-07-19 | Geekay Pneumatic Pvt Ltd | Kerala | D | Fathima Ice Industries | Kerala | KCX3 | 3374K2668 | 3087785895 | 2022-06-09 | 308778 | 2022-06-08 | pressure gauge error | 2021-08-31 | 2022-06-08 | 8 | Inhouse | ice plant | 10 | Suction pressure gauge error 0.75Kg/cm2 | null | closed | Replaced Pressure gauge 16 Kg/cm2
2022-07-19 | Geekay Pneumatic Pvt Ltd | Kerala | D | Vinayaka Ice Plant | null | KCX1 | 3354K244 | 3100965921 | 2022-06-22 | 310096 | 2022-06-21 | pump opr not working | 2022-05-08 | 2022-06-21 | 5 | Inhouse | ice plant | 1 | LP Regulator ball stuck & pressure gratually decreased. | null | closed | Replaced OPR
2022-07-19 | Gargi Engineering Enterprices Pvt Ltd | null | D | Meghmani Dyes | Gujrat | KCX72 | 3474K495 | 3107305947 | 2022-06-30 | 310730 | 2022-06-30 | delivery valve problem | 2021-11-30 | 2022-04-01 | 178 | Supplier | others | 5 | HP Cylinder no.4 delivery valve leakage due to foregin particles & cylinder seized. Intercoolar compressor. | null | closed | Replaced buffer spring , delivery valve , liner ,piston & piston rings.
2022-07-19 | Pragya Industrial Supply | Karnataka | D | Larson Pharma Pvt Ltd | Karnataka | KCX42 | 3444K349 | null | null | 312120 | 2022-07-03 | knocking sound from hp cylinder | 2022-05-11 | 2022-07-03 | 2 | Inhouse | chemical / pharma | 1 | Knocking sound from HP cylinder due to metal chips observed inside. | null | closed | Knocking sound from HP cylinder due to metal chips observed inside.
2022-07-31 | Cool Comfort Private Limited | West Bengal | D | SMCold Storage | West Bengal | KCX4 | 3384K2692 | 3147165999 | 2022-07-28 | 314716 | 2022-07-28 | oil carry over | 2021-01-31 | 2021-03-16 | 6635 | null | cold storage | 2 | Cylinder liner-2 , Piston rings sets 4, Piston 2 DV -1 wornout. | null | closed | Replaced Cylinder liner2 , Piston rings sets 4, Piston 2 DV 1
2022-07-31 | Kalp Marketing | Gujrat | D | Siddhi Vinayak Cold Storage | Gujrat | KCX3 | 3374K2641 | 3110345928 | 2022-06-24 | 311034 | 2022-06-23 | oil pressure problem | 2021-08-26 | 2022-02-04 | 201 | LDK Before improvement | cold storage | 6 | Oil pressure problem due to tang broken | null | closed | Replaced pump element
2022-07-31 | Trade Links | Secunderabad | D | Tirumala Milk Products Ltd | Andhra Pradesh | KCX2 | 3364K2110 | 3101025907 | 2022-06-18 | 310102 | 2022-06-17 | oil pressure problem | 2021-03-10 | 2021-04-21 | 3570 | null | dairy / ice cream | 1 | Oil pressure problem due to air purging issue & gear wornout | null | closed | Replaced oil pump assembly
2022-07-31 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Sailani Ice Factory | Maharashtra | KCX3 | 3374K2608 | 3062525913 | 2022-06-21 | 306252 | 2022-06-20 | oil carry over | 2021-07-25 | 2021-11-27 | 1535 | null | ice plant | 4 | Piston rings wornout | null | closed | Replaced Piston ring sets3
2022-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Guru Nanak Refrigeration Services | Mumbai | KCX9 | 3404K181 | 3088105932 | 2022-06-27 | 308810 | 2022-06-25 | oil carry over | 2021-02-19 | 2021-08-10 | 6129 | null | ice plant | 7 | Liner step cut marks & piston rings wornout | null | closed | Replaced Liner 3 nos & piston rings 9 sets.
2022-07-31 | Trade Links | Secunderabad | D | Naga Hanuman Ice Industry | Andhra Pradesh | KCX4 | 3384K2831 | 3109845922 | 2022-06-22 | 311050 | 2022-06-24 | oil lifting | 2021-07-28 | 2021-10-26 | 3912 | null | ice plant | 3 | All cylinders piston rings wornout by 1mm | null | closed | Replaced piston ring set4 & valve kit3nos
2022-07-31 | Trade Links | Secunderabad | D | Naga Hanuman Ice Industry | Andhra Pradesh | KCX4 | 3384K2831 | 3110505927 | 2022-06-24 | 311050 | 2022-06-24 | over heating | 2021-07-28 | 2021-10-26 | 3922 | null | ice plant | 3 | Cyl no. delivery valve leakage & overheating | null | closed | Replaced kit & delivery valve assembly
2022-07-31 | Kalp Marketing | Gujrat | D | Devarsons Industries Pvt Ltd | Gujrat | KCX21 | 3424K140 | 3147485994 | 2022-07-23 | 314748 | 2022-07-18 | hour meter not working | 2022-06-21 | 2022-07-18 | 4 | null | chemical / pharma | 1 | Hour meter not working. Improper base frame comminssion remark as per FRR. | null | closed | Hour meter
2022-07-31 | Pragya Industrial Supply | Karnataka | D | Larson Pharma Pvt Ltd | Karnataka | KCX42 | 3444K349 | 3121205955 | 2022-07-04 | 312120 | 2022-07-03 | knocking / abnormal sound | 2022-05-11 | 2022-07-03 | 2 | null | chemical / pharma | 1 | Machining chips found in HP cylinder | null | closed | Replaced Liner , Piston , Piston ring set & delivery valve
2022-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Adroit Pharmachem Pvt Ltd | Gujrat | KCX4 | 3384K2893 | 3107265926 | 2022-06-23 | 310726 | 2022-06-23 | oil carry over | 2021-08-31 | 2022-01-17 | 8 | null | chemical / pharma | 5 | Piston rings wornout | null | closed | Replaced piston ring set 3 nos.
2022-07-31 | Kalp Marketing | Gujrat | D | Pavansut Industries | Gujrat | KCX3 | 3374K2855 | 3148786001 | 2022-07-29 | 314878 | 2022-07-19 | oil pressure not buildup | 2022-04-26 | 2022-06-11 | 50 | null | chemical / pharma | 2 | Low oil level in compressor & pump tang broken | null | closed | Replaced pump element
2022-08-21 | S B Refrigeration | Bihar | D | Varun Beverage Limited | Bihar | KCX9 | 3404K201 | 3183426030 | 2022-08-09 | 318342 | 2022-08-09 | over heating | 2021-08-24 | 2022-01-30 | 342 | null | beverage / breweries | 5 | Cylinder no.-03 delivery valve leakage | null | closed | Discharge valve assembly1
2022-08-21 | Cool Comfort Private Limited | West Bengal | D | Sanjiwani Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3018 | 3183226028 | 2022-08-09 | 318322 | 2022-08-09 | abnormal noise | 2022-02-14 | 2022-03-17 | 1455 | null | cold storage | 1 | Piston and piston ring, liner discharge valve assign gudgeon pin damage ( As per FRR Remark foreign particles observed on DV) | null | closed | Piston 1 no. Cylinder Liner 1 no. Piston ring set 1 no. Gudgeon pin 1 no. Bush connecting rod 1 no. Discharge valve assly 1 no.
2022-08-21 | Multivista Global Pvt Ltd | Tamil Nadu | D | Flex Foods Ltd | Tamil Nadu | KCX72 | 3474K507 | 3167466047 | 2022-08-16 | 316746 | 2022-08-11 | abnormal noise hp cylinder seized | 2021-10-31 | 2022-04-12 | 560 | null | cold storage | 6 | Oil pressure not maintained HP Cyl. Liner, piston and piston rings & crankshaft damaged Connecting rod big end bearing damaged Crankshaft damaged. | null | closed | Crankshaft assly KCX9 1 no. Piston 1 no. Piston rings 2 nos. Liner 2 nos. Lock plate Con rod & Inter. Hsg. Bolt 9 nos. Bearing bush big end Con rod 4 nos. Gudgeon pin 1 no. Safety plate counter weight 4 nos. Needle roller bearing 2 nos. Spacer for needle roller bearing 1 no. Nut Hex Con Rod bolt 2 nos. Bearing Inter. Half 2 nos. Bearing bush plain, Flywheel end 1 no. Bearing bush flange, Pump end 1 no.
2022-08-21 | Parag Marketing Services | Pune | D | Gugale Cold Storage Pvt Ltd | Maharashtra | KCX3 | 3374K2404 | Service email | 2022-08-03 | 311282 | 2022-07-22 | air purging problem | 2020-10-26 | 2020-12-26 | 1406 | null | cold storage | 2 | Air purging problem | null | closed | Oil pump replaced with manual FRR OA 5656851. refer mail dated 09.07.22
2022-08-21 | Multivista Global Pvt Ltd | Tamil Nadu | D | Flex Foods Ltd | Tamil Nadu | KCX42 | 3444K303 | Service email | 2022-08-03 | 316480 | 2022-07-30 | crankcase foot crack | 2021-09-28 | 2022-03-03 | 1671 | null | cold storage | 6 | Crankcase body foot crack and oil leakage (Detail site analysis missing in FSR) | null | closed | Compressor received at KPCL . Crankcase shell to foot welding rectified at supplier end and in pressure testing no leakage found at KPCL
2022-08-21 | Cool Comfort Private Limited | West Bengal | D | SN Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K2884 | 3154326027 | 2022-08-09 | 315432 | 2022-08-09 | high oil consumption | 2021-08-29 | 2022-03-14 | 892 | null | cold storage | 7 | Piston ring and liner bore damaged | null | closed | Piston 2 nos. Cylinder Liner 2 nos. Piston ring set 4 nos. Bearing bush big end Con Rod 2 nos.
2022-08-21 | Model Pneumatic Co | Punjab | D | Shri Ram Farm And Cold Storage | Punjab | KCX4 | 3384K2995 | 2931845757 | 2022-03-30 | 293184 | 2022-03-29 | krms suction & discharge temp sensors nor working. | 2022-01-28 | 2022-03-29 | 0 | null | cold storage | 1 | CCSV 2 coil was not working Suction and Discharge temperature sensor not working | null | closed | Suction temperature sensor 50 to 105 Deg C 1 no. Discharge temperature sensor 50 to 250 Deg C 1 no. Coil for No Solenoid valve 230V, 50Hz with green colour sticker 1 no.
2022-08-21 | Hss Solution Pvt Ltd | Rajasthan | D | Evergreen Cold Storage Rajasthan | null | KCX2 | 3364K2225 | 3178286011 | 2022-08-03 | 317828 | 2022-08-03 | loading unloading problemsolenoid valve malfunctioning | 2021-10-31 | 2022-02-26 | 783 | null | cold storage | 4 | CCSV-1 not working Suction and discharge line vibration found abnormal Suction cloth bag condition very bad. ( As per FRR remark high system dirt evident in photographs attched in oracle) | null | closed | Replaced Solenoid valve (Teflon), 3 Way, 230V, 50 Hz, NC 1 no.
2022-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Hpmc Cold Storage | null | KC6 | 339K3607 | 3178846012 | 2022-08-04 | 317884 | 2022-08-12 | oil pressure problem | 2020-12-30 | 2021-03-03 | 1428 | null | cold storage | 3 | Oil pump housing was cut from inside, due to which pressure is decreasing | null | closed | Oil pump assly 1 no.
2022-08-21 | Parag Marketing Services | Pune | D | Kala Biotech Pvt Ltd | Khed, Maharashtra | KCX6 | 3394K1793 | Service email | 2022-08-03 | 312114 | 2022-07-11 | oil separator leakage | 2021-04-20 | 2021-09-12 | 1102 | null | cold storage | 5 | Welding leakage observed in oil separator | null | closed | Oil separator welding leakage rectified on site by KPCL ( Same welding crack for two os on same site.)
2022-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Robin Cold Storage PvtLtd | Uttar Pradesh | KCX4 | 3384K2682 | 3191466051 | 2022-08-18 | 319146 | 2022-08-17 | over heating | 2021-01-18 | 2022-07-12 | 218 | null | cold storage | 6 | Cyl. No. -03 piston overheat problem Discharge valve was leak | null | closed | Discharge valve assembly1
2022-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Robin Cold Storage PvtLtd | Uttar Pradesh | KCX4 | 3384K2682 | 3178146010 | 2022-08-03 | 317814 | 2022-08-03 | over heating | 2021-01-18 | 2022-07-12 | 162 | null | cold storage | 6 | Cylinder no 3 was overheating . Delivery valve was leakage | null | closed | Kit delivery valve 1 no.
2022-08-21 | Parag Marketing Services | Pune | D | Shree Ganesh Milk Processor | Pune | KCX1 | 3354K181 | 3139386050 | 2022-08-17 | 313938 | 2022-08-17 | oil carry over | 2021-01-04 | 2021-08-12 | 4211 | null | dairy / ice cream | 7 | Analysis not mentioned in FSR | null | open | Replaced Float valve Assly for Oil Separator 1 no. Set of Gasket for KCX1 1 no. Set of O ring for KCX1 1 no. Set of Packing 1 no. Gasket, Square flange 50 NB 2 nos.
2022-08-21 | Multivista Global Pvt Ltd | Tamil Nadu | D | Sivaraj Spinning Mills (Atmos Dairy) | Tamil Nadu | PCX2 | 3106K0066 | 3163946046 | 2022-08-16 | 316394 | 2022-08-13 | oil pressure not develop spares supply | 2020-11-28 | 2021-02-04 | WC | null | dairy / ice cream | 3 | Pump failed due to improper operations at site.Customer purchased new pump and this pump also Oil pressure not developed. | null | closed | Oil pump assly PC2 1 no.
2022-08-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Seafood Innovations | Kerala | KCX3 | 3374K2685 | 3098405915 | 2022-06-21 | 309840 | 2022-06-17 | high oil carryover | 2021-10-29 | 2021-11-30 | 4602 | null | ice plant | 1 | Oil throw from all 3 Cylinders Cyl. No. 1 & 3 Liner worn out Bronze thrust ring worn out and shaft seal leakage | null | closed | Liner 2 nos. Piston ring set 3 nos. Lock plate Con Rod and Inter. Hsg. Bolt 6 nos. Thrust ring pump end bearing cover 1 no. Spring cylinder liner 4 nos. Stud STD Type A M16x2x81L 1 no. Nut Hex, M16 x 2P 1 no.
2022-08-21 | Cool Comfort Private Limited | West Bengal | D | Marcofed Ice Plant | Nagaland | KCX1 | 3354K189 | 3147605990 | 2022-07-20 | 314760 | 2022-07-16 | high oil consumption | 2021-02-20 | 2021-07-10 | 3858 | null | ice plant | 5 | Piston ring 2 top rings not properly seating | null | closed | Piston ring set 1 no. Oil return valve 1 no.
2022-08-21 | Cool Comfort Private Limited | West Bengal | D | Gita Ice Plant | West Bengal | KCX2 | 3364K2293 | 3152005997 | 2022-07-27 | 315200 | 2022-07-21 | high oil consumption | 2022-03-21 | 2022-06-02 | 925 | null | ice plant | 3 | Excessive oil through in cyl. No. 1 & 2 | null | closed | Piston ring set 2 nos.
2022-08-21 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Pure Ice Industries | null | KCX3 | 3374K2781 | 3136605977 | 2022-07-11 | 313660 | 2022-07-11 | oil carry over | 2022-02-05 | 2022-02-12 | 2150 | null | ice plant | 0 | Liner step marks Piston have touch mark of delivery valve assly and piston ring gap was more than 1.9 mm for all Delivery valve and Piston | null | closed | Cylinder liner 1 no. Piston ring set 3 nos.
2022-08-21 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sonia Marine Exports Pvt Ltd | Mumbai | KCX72 | 3474K496 | 3152026021 | 2022-08-06 | 315202 | 2022-08-05 | over heating | 2022-01-18 | 2022-05-21 | 268 | null | meat/fish process | 4 | HP piston delivery valve was leakage | null | closed | Kit delivery valve 1 no.
2022-08-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Frontline Exports Pvt Ltd | Kerala | KCX72 | 3474K459 | 3139605991 | 2022-07-20 | 313960 | 2022-07-12 | pressure gauge malfunctioning | 2021-03-29 | 2022-07-12 | 10 | null | meat/fish process | 15 | Analysis not mentioned in FSR | null | closed | Replaced Ammonia Pressure gauge with bottom entry Range 760 mm of Hg to 16 Kg/cm2 1 No.
2022-08-21 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KCX63 | 3464K141 | 3114025989 | 2022-07-19 | 311402 | 2022-08-02 | cylinder overheating (hp) | 2021-12-15 | 2022-08-02 | 16 | null | chemical / pharma | 8 | Cylinder no.-04 (HP) Delivery valve leakage | null | closed | Discharge valve assembly1
2022-08-21 | Parag Marketing Services | Pune | D | Canpex Chemicals Pvt Ltd | Beed | KCX2 | 3364K2075 | Service email | 2022-08-03 | 313298 | 2022-07-05 | oil pressure problem | 2021-01-20 | 2021-02-09 | 4870 | null | chemical / pharma | 1 | Oil pump element tang broken | null | closed | Oil pump element 1 no.
2022-08-21 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K015 | 3001966015 | 2022-08-05 | 300196 | 2022-04-23 | oil pump purging | 2020-08-16 | 2020-11-10 | 5563 | null | chemical / pharma | 3 | Oil pressure not developed | null | closed | Oil pump assly 1 no.
2022-08-23 | Multivista Global Pvt Ltd | Gurgaon | D | Varun Beverage Limited | Bihar | KCX9 | 3404K198 | 3179726016 | 2022-08-05 | 317972 | 2022-08-05 | coupling disc pack damage | 2021-07-18 | 2021-12-21 | 493 | null | beverage / breweries | 5 | Coupling alignment issue. Disc pack damaged. (Detail site analysis missing in FSR) | null | closed | Replaced disc pack & nylock nut
2022-08-31 | Cool Comfort Private Limited | West Bengal | D | S M Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K2692 | 3229186082 | 2022-08-30 | 322918 | 2022-08-30 | high oil consumption | 2021-01-31 | 2021-03-16 | 6646 | null | cold storage | 2 | Liner , piston , piston rings wornout | null | closed | Replaced liner , Piston & connecting ros 2 nos each & piston ring sets 4 nos.
2022-08-31 | Cool Comfort Private Limited | West Bengal | D | Matri Bhumi Agritech LLP | West Bengal | KCX4 | 3384K3013 | 3226566078 | 2022-08-29 | 322656 | 2022-08-29 | high oil consumption | 2022-02-12 | 2022-03-12 | 1344 | null | cold storage | 1 | Liner , piston , piston rings wornout | null | closed | Replaced liner , Piston & connecting ros 2 nos each & piston ring sets 4 nos.
2022-08-31 | Multivista Global Pvt Ltd | Gurgaon | D | Smc Foods Ltd | Uttar Pradesh | KCX9 | 3404K205 | 3185766026 | 2022-08-09 | 318576 | 2022-08-09 | high oil consumption | 2021-09-29 | 2022-05-03 | 1890 | null | dairy / ice cream | 8 | Liner , piston wornout - 2 nos & Piston ring sets 9 nos | null | closed | Replaced Liner , piston wornout 2 nos & Piston ring sets 9 nos
2022-08-31 | Multivista Global Pvt Ltd | Gurgaon | D | Bveg Foods Private Limited | Haryana | KCX3 | 3374K2823 | 3207786067 | 2022-08-24 | 320778 | 2022-08-24 | oil pressure problem | 2022-03-14 | 2022-08-10 | 2.6 | null | food processing | 5 | Oil pump element broken. | null | closed | Replaced pump assembly
2022-08-31 | Trade Links | Secunderabad | D | Siri Vinayak Aqua Exports Pvt Ltd | Andhra Pradesh | KCX4 | 3384K2825 | 3138766009 | 2022-08-03 | 313876 | 2022-08-02 | delivery valve leakage | 2021-07-26 | 2022-08-02 | 1.5 | null | ice plant | 13 | Cylinder no.3 Delivery valve leakage . This is reapeated case | null | closed | Replaced delivery valve assembly
2022-08-31 | Hss Solution Pvt Ltd | Rajasthan | D | ASAgro Foods | Rajastan | KCX1 | 3354K226 | 3107365995 | 2022-07-25 | 310736 | 2022-07-23 | high oil consumption | 2021-10-18 | 2021-11-16 | 1492 | null | ice plant | 1 | Oil carry over , OS Return line not connected & system related issues observed. | null | closed | Replaced piston ring set
2022-08-31 | Robin Refrigeration Works | Odisha | D | Balmer Lawrie & CoLtd | Odisha | KCX42 | 3444K227 | 3189926052 | 2022-08-18 | 318992 | 2022-08-26 | intermediate bearing bush damaged | 2020-08-30 | 2021-09-28 | 202.9 | null | ice plant | 12 | Crankshaft & Flywheel jammed due to intermediate bearing seized. Possibility of Liquid entry in compressor. | null | closed | Replaced intermediate bearings
2022-08-31 | Trade Links | Secunderabad | D | Sri Ayyappa Ice Factory | Andhra Pradesh | KCX4 | 3384K2772 | 3191266037 | 2022-08-12 | 319126 | 2022-08-11 | over heating | 2021-05-12 | 2021-05-21 | 8726 | null | ice plant | 1 | Cylinder no.3 Delivery valve leakage . This is reapeated case | null | closed | Replaced delivery valve assembly
2022-08-31 | Robin Refrigeration Works | Odisha | D | Orchid Marine Exports Pvt Ltd | Odisha | KCX51 | 3454K164 | 3201106060 | 2022-08-20 | 320110 | 2022-08-27 | high oil consumption | 2020-10-19 | 2021-06-13 | 2169 | null | meat/fish process | 8 | Piston ring set - 2 nos found wornout | null | closed | Replaced Piston ring set 2 nos
2022-08-31 | Multivista Global Pvt Ltd | Gurgaon | D | Federal Agro Industries Pvt Ltd | Uttar Pradesh | KCX42 | 3444K343 | 3211666076 | 2022-08-27 | 321166 | 2022-08-27 | oil pressure problem | 2022-03-25 | 2022-04-01 | 2319 | null | meat/fish process | 1 | Pump pressure gratually drop , checked on another compressor same issue noticed. | null | closed | Replaced Pump Assembly
2022-08-31 | Cool Comfort Private Limited | West Bengal | D | Basu International | West Bengal | KCX72 | 3474K552 | 3196686057 | 2022-08-19 | 319668 | 2022-08-26 | over heating | 2022-06-12 | 2022-07-20 | 303 | null | meat/fish process | 1 | HP Cylinder liner , piston , piston rings , bushing & delivery valve damaged. | null | closed | Replaced HP Cylinder liner , piston , piston rings , bushing & delivery valve damaged.
2022-08-31 | Trade Links | Secunderabad | D | Nichino India PvtLtd | null | KCX6 | 3394K1847 | Service email | 2022-09-02 | 305808 | 2022-08-29 | wobbling of flywheel | 2021-07-31 | 2021-10-31 | 2800 | null | chemical / pharma | 3 | Crankshaft keyway had damaged and resulted to wobbling of flywheel & abnormal sound | null | closed | Replaced crankshaft & flywheel from cutomer stock
2022-09-12 | Multivista Global Pvt Ltd | Gurgaon | D | Varun Beverage Limited | Uttar Pradesh | KCX9 | 3404K196 | 3164246079 | 2022-08-29 | 316424 | 2022-08-29 | low oil pressure | 2021-07-18 | 2021-12-21 | 542 | null | beverage / breweries | 5 | Cylinder seized due to no oil pressure.OP Switch bypass | null | closed | Replaced Piston 4, Ring set9,Bearings , Crankshaft , Pump element, Cylinder liners.
2022-09-12 | Hss Solution Pvt Ltd | Rajasthan | D | Jc Cold Storage | Rajastan | KCX3 | 3374K2697 | 3196246062 | 2022-08-22 | 319624 | 2022-08-21 | oil pressure not buildup | 2021-11-19 | 2022-07-28 | 7.4 | null | cold storage | 8 | Oil pump tang broken | null | closed | Replaced pump assembly 1
2022-09-14 | Cool Comfort Private Limited | West Bengal | D | Bengal Beverage Pvt Ltd | West Bengal | KCX6 | 3394K1810 | 3243806099 | 2022-09-07 | 324380 | 2022-09-09 | oil carryover piston crack | 2021-06-09 | 2021-11-12 | 2379 | null | beverage / breweries | 5 | Cyl.no 01 piston crack,cyl. 1,3,4 disc. Valve spring broken | null | closed | Replaced cylinder liner,piston,piston ring set,kit del valve, disc. Valve assly2
2022-09-14 | Kalp Marketing | Gujrat | D | Chhatarpur Cold Storage | Madhya Pradesh | KCX4 | 3384K2815 | 3195906059 | 2022-08-20 | 319590 | 2022-08-20 | kcx oil pump element tang broken | 2021-07-17 | 2021-09-20 | 2169 | null | cold storage | 2 | Oil pump tang broken | null | closed | Replaced oil pump element
2022-09-14 | Robin Refrigeration Works | Odisha | D | R & M Group Of Company | Odisha | KCX3 | 3374K2748 | 3245906103 | 2022-09-09 | 324590 | 2022-09-09 | abnormal noise | 2022-01-03 | 2022-06-08 | 937 | null | ice plant | 5 | Piston siezed & delivery valve nut found in loose condition. | null | closed | Replaced delivery valve,Piston,piston ring set,cylinder liner,bush con rod.
2022-09-14 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Evergreen Engineering Works | Thane | KCX3 | 3374K2526 | 3196786063 | 2022-08-23 | 319676 | 2022-08-19 | oil carry over | 2021-03-06 | 2021-03-22 | 2612 | null | ice plant | 1 | Piston rings worn out | null | closed | Replaced piston ring set
2022-09-20 | Trade Links | Goa | D | Niranjan Industries | Goa | KCX3 | 3374K2860 | 3208406106 | 2022-09-12 | 320840 | 2022-09-09 | oil carryoverdel valve leak | 2022-05-13 | 2022-07-31 | 4085 | null | ice plant | 3 | Piston and liner siezed | null | closed | Piston,liner,Buffer spring and del.valve assly.
2022-09-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ambarnath Org Pvt Ltd | Thane | KC3 | 337K4827 | 3209026074 | 2022-08-27 | 320902 | 2022-08-27 | pressure switch leakage from connector due to threading damaged | 2022-03-25 | 2022-08-27 | ZH | null | ice plant | 5 | Leakage from connector threading | null | closed | Replaced pressure switches
2022-09-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Pure Ice Industries | null | KCX3 | 3374K2781 | 3214486091 | 2022-09-03 | 321448 | 2022-09-03 | solenoid valve not working | 2022-02-05 | 2022-02-12 | 643 | null | ice plant | 1 | Solenoid valve not working | null | closed | Replaced sol.valve.
2022-09-20 | Trade Links | Secunderabad | D | Kalyan Aqua And Marine Ltd | Andhra Pradesh | KCX72 | 3474K519 | 3164186006 | 2022-08-01 | 316418 | 2022-07-30 | oil lifting | 2022-02-06 | 2022-06-09 | 593 | null | meat/fish process | 4 | Piston rings changed | null | closed | Replaced piston,piston rings and liner
2022-09-20 | Trade Links | Secunderabad | D | Nichino India PvtLtd | null | KCX6 | 3394K1847 | 3231706093 | 2022-09-05 | 323170 | 2022-09-03 | delivery valve leakage | 2021-07-31 | 2021-10-31 | 3200 | null | chemical / pharma | 3 | Piston ring set and del valve assly replaced | null | closed | Piston ring set and del valve assly replaced
2022-09-28 | Geekay Pneumatic Pvt Ltd | Kerala | D | Ice Land Pookayi | Kerala | KCX4 | 3384K2737 | 3063605881 | 2022-05-31 | 306360 | 2022-05-31 | abnormal noise & oil carry over | 2021-03-22 | 2021-07-16 | 524 | null | ice plant | 4 | Delivery valve leak | null | closed | Replaced cylinder liner,piston,piston ring set,
2022-09-30 | Multivista Global Pvt Ltd | Gurgaon | D | Hargovind Das Agro Farms | Uttar Pradesh | KC4 | 338K5763 | 3254146115 | 2022-09-13 | 325414 | 2022-09-14 | kc oil pump low oil pressure | 2021-12-28 | 2022-03-02 | 306 | null | cold storage | 3 | Replaced oil pump assly | null | closed | Replaced oil pump assly
2022-09-30 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Durga Dairy | Uttar Pradesh | KCX1 | 3354K245 | 3253586109 | 2022-09-12 | 325358 | 2022-09-16 | oil lifting | 2022-06-01 | 2022-07-29 | 308 | null | dairy / ice cream | 2 | Replaced piston ring set | null | closed | Replaced piston ring set
2022-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Jose Ice Plant | Kerala | KCX3 | 3374K2666 | 3233346094 | 2022-09-05 | 323334 | 2022-09-03 | cylinder overheating | 2021-08-31 | 2021-11-23 | 3573 | null | ice plant | 3 | Replaced delivery valve assly | null | closed | Replaced delivery valve assly
2022-09-30 | Cool Comfort Private Limited | West Bengal | D | Maa Kali Enterprises | West Bengal | KCX2 | 3364K2276 | 3256366120 | 2022-09-15 | 325636 | 2022-09-14 | oil lifting | 2022-02-22 | 2022-06-20 | 1282 | null | ice plant | 4 | Replaced Piston ring set | null | closed | Replaced Piston ring set
2022-10-14 | Cool Comfort Private Limited | West Bengal | D | S N Cold Storage | null | KCX4 | 3384K2884 | 3285006147 | 2022-09-30 | 328500 | 2022-10-03 | high oil consumption | 2021-08-29 | 2022-03-14 | 921 | null | cold storage | 7 | Piston rings wornout | null | closed | Replaced piston ring sets 2 nos.
2022-10-14 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K2895 | 3064685984 | 2022-07-14 | 306468 | 2022-06-03 | over heating | 2021-09-03 | 2021-11-19 | 2417 | null | food processing | 2 | Cylinder no. 1,2&3 cylinder overheating. ( No site observations in FSR) | null | closed | Replaced delivery valve assly 3 nos.
2022-10-14 | Trade Links | Secunderabad | D | Plr Foods Pvt Ltd | Andhra Pradesh | KCX72 | 3474K542 | 3271286148 | 2022-09-30 | 327128 | 2022-10-01 | shaft seal leakage | 2022-04-10 | 2022-07-09 | 98 | null | food processing | 3 | Shaft seal lekage due to wornut | null | closed | Replaced shaft seal assly
2022-10-14 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K2895 | 3164466004 | 2022-07-30 | 316446 | 2022-07-28 | shaft seal leakage | 2021-09-03 | 2021-11-19 | 2417 | null | food processing | 2 | Replaced shaft seal assly. ( No site observations in FSR) | null | closed | Replaced shaft seal assly.
2022-10-14 | S B Refrigeration | Bihar | D | G N Enterprises | Bihar | KCX2 | 3364K2100 | 3282106145 | 2022-09-29 | 328210 | 2022-10-07 | high oil consumption | 2021-02-27 | 2021-06-30 | 2922 | null | ice plant | 4 | Piston rings wornout | null | closed | Replaced piston ring sets 2 nos.
2022-10-14 | Parag Marketing Services | Pune | D | Walwa Shirala Co Op Dairy Ltd | Sangli | KCX1 | 3354K223 | 3229366088 | 2022-09-03 | 322936 | 2022-09-02 | knocking / abnormal sound | 2021-09-29 | 2021-11-25 | 1673 | null | ice plant | 2 | Delivery valve ring spring broken | null | closed | Replaced delivery valve assly.
2022-10-14 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3454K191 | 3277746140 | 2022-09-26 | 327774 | 2022-09-26 | cylinder overheating | 2021-06-23 | 2021-08-25 | 2820 | null | meat/fish process | 2 | Cyl no. 6 delivery valve leakage | null | closed | Replaced delivery valve assly
2022-10-21 | Multivista Global Pvt Ltd | null | D | Accord Distilleries & Breweries Pvt Ltd | Tamil Nadu | PCX2 | 3106K0179 | 3256046168 | 2022-10-15 | 325604 | 2022-10-14 | pcx2 oil pump seized | 2022-08-29 | 2022-10-14 | 0 | null | beverage / breweries | 2 | Pump seized & gear broken. | null | closed | Replaced pump assembly
2022-10-21 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Raja Dhiraj Cold Storage | Uttar Pradesh | KCX6 | 3394K1948 | 3320806182 | 2022-10-18 | 332080 | 2022-10-19 | cylinder overheating | 2022-02-05 | 2022-03-02 | 552 | null | cold storage | 1 | Replaced del valve assly | null | closed | Replaced del valve assly
2022-10-21 | Hss Solution Pvt Ltd | Rajasthan | D | R K Cold Store | Rajastan | KCX2 | 3364K2306 | 3269366135 | 2022-09-22 | 326936 | 2022-09-22 | cylinder overheating | 2022-03-30 | 2022-06-23 | 410 | null | cold storage | 3 | Delivery valve leakage | null | closed | Replaced Del valve assly1 No.
2022-10-21 | Hss Solution Pvt Ltd | null | D | Shree Maruti Chilling Udyaog | Rajastan | KCX2 | 3364K2139 | 3167346084 | 2022-08-30 | 316734 | 2022-08-30 | abnormal noise | 2021-04-27 | 2021-05-29 | 1573 | null | dairy / ice cream | 1 | Replaced piston,liner,del valve,piston ring set- site analysis is missing in FSR | null | closed | Replaced piston,liner,del valve,piston ring set
2022-10-21 | Multivista Global Pvt Ltd | null | D | Maa Durga Dairy | Uttar Pradesh | KCX1 | 3354K245 | 3305606159 | 2022-10-10 | 330560 | 2022-10-09 | high oil consumption | 2022-06-01 | 2022-07-29 | 486 | null | dairy / ice cream | 1 | Open oil throw observed. Piston , Cylinder liner & Piston rings cut marks. | null | closed | Replaced liner, piston & piston ring set
2022-10-21 | Trade Links | Secunderabad | D | Mavee Foods | Telangana | KCX4 | 3384K2720 | 3308466161 | 2022-10-11 | 330846 | 2022-10-10 | abnormal noise | 2021-02-27 | 2021-11-20 | 2575 | null | food processing | 9 | Replaced Del valve assly-1 No. | null | closed | Replaced Del valve assly1 No.
2022-10-21 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Jeyes Enterprises | Kerala | KCX2 | 3364K2300 | 3268626131 | 2022-09-21 | 326862 | 2022-09-20 | cylinder overheating | 2022-03-28 | 2022-07-07 | 1505 | null | ice plant | 4 | Replaced del valve assly | null | closed | Replaced Del valve assly1 No.
2022-10-21 | Trade Links | Goa | D | Mandovi Ice Plant | Goa | KCX3 | 3374K2569 | 3264746152 | 2022-10-04 | 326474 | 2022-09-17 | cylinder overheating | 2021-05-09 | 2021-08-07 | 6693 | null | ice plant | 3 | Delivery valve leakage | null | closed | Replaced Del valve assly1 No.
2022-10-21 | Kalp Marketing | Gujrat | D | Aries Dye Chem Industries | Gujrat | KCX6 | 3394K1828 | 3284726150 | 2022-10-03 | 328472 | 2022-10-03 | high oil consumption | 2021-07-28 | 2021-10-30 | 5122 | null | ice plant | 2 | Replaced ORV | null | closed | Replaced ORV
2022-10-21 | Geekay Pneumatic Pvt Ltd | null | D | Vinayak Ice Plant | Kerala | KCX1 | 3354K244 | 3196446107 | 2022-09-12 | 319644 | 2022-09-12 | shaft seal leakage | 2022-05-08 | 2022-06-21 | 503 | null | ice plant | 1 | Shaft seal leakage due to scoring marks , Lapping done but leak not arrested. Hence replaced shaft seal assly | null | closed | Replaced shaft seal assembly
2022-10-21 | Kalp Marketing | Gujrat | D | Ocean Aquatech Product | Gujrat | KCX51 | 3454K187 | 3245243108 | 2022-09-12 | 324524 | 2022-09-12 | cylinder overheating | 2021-03-27 | 2021-09-03 | 379 | null | meat/fish process | 6 | Delivery valve leakage | null | closed | Replaced Del valve assly1 No.
2022-10-21 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3354K191 | 3302946162 | 2022-10-11 | 330294 | 2022-10-11 | oil carryoverdel valve leak | 2021-06-23 | 2021-08-25 | 3112 | null | meat/fish process | 2 | Replaced del valve assly & VLD orings | null | closed | Replaced del valve assly & VLD orings
2022-10-21 | Multivista Global Pvt Ltd | null | D | Ashrafi Agri Fresh Pvt Ltd | Uttar Pradesh | KC42 | 344K1144 | 3317986186 | 2022-10-20 | 331798 | 2022-10-20 | oil pressure problem | 2021-03-31 | 2022-09-07 | 74 | null | meat/fish process | 6 | Pump seized & gear broken. | null | closed | Replaced pump assembly
2022-10-21 | Gargi Engineering Enterprices Pvt Ltd | null | D | Transpek Silox Inductries Pvt Ltd | Gujrat | KCX4 | 3384K2767 | 3136585983 | 2022-07-13 | 313658 | 2022-07-12 | cylinder overheatingpiston crack | 2021-04-30 | 2021-12-13 | 1530 | null | chemical / pharma | 8 | Piston crack & del valve leakage | null | closed | Replaced piston and del valve
2022-10-30 | Multivista Global Pvt Ltd | null | D | Smc Foods Ltd | Uttar Pradesh | KCX9 | 3404K205 | 3323306188 | 2022-10-20 | 332330 | 2022-10-20 | oil liftingdischarge valve leak | 2021-09-29 | 2022-05-03 | 2877 | null | dairy / ice cream | 8 | Discharge valve leak - site analysis is missing in FSR | null | closed | Discharge valve leak
2022-10-30 | Kalp Marketing | Gujrat | D | Sagar Food | Gujrat | KCX31 | 3434K0189 | 3311186169 | 2022-10-15 | 331118 | 2022-10-13 | discharge temprature sensor not working | 2022-09-17 | 2022-09-25 | 387 | null | meat/fish process | 1 | Discharge temp sensor not working | null | closed | Discharge temp sensor not working
2022-10-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX42 | 3444K362 | email | 2022-10-21 | 332158 | 2022-10-21 | wrinkles on paint surface at discharge pipe | 2022-09-17 | 2022-10-20 | 5 | null | chemical / pharma | 1 | Wrinkles on paint surface at discharge pipe. | null | closed | null
2022-11-08 | Multivista Global Pvt Ltd | Tamil Nadu | D | Grb Dairy Foods Pvt Ltd | Tamil Nadu | KCX2 | 3364K2174 | 3327606195 | 2022-10-27 | 332760 | 2022-10-31 | shaft seal leakage | 2021-07-21 | 2022-09-03 | 38 | null | dairy / ice cream | 14 | Shaft seal leakage due to deep scoring | null | closed | Replaced shaft seal assly
2022-11-08 | Pragya Industrial Supply | Karnataka | D | Sheetal Ice Plant | Karnataka | KCX6 | 3394K1853 | 3321606187 | 2022-10-20 | 332160 | 2022-10-20 | abnormal noise | 2021-08-28 | 2022-09-17 | 669 | null | ice plant | 12 | Cylinder no.5 abnormal sound, DV,Piston, Piston ring , liner & bearings damaged. - Suction & discharge bypass line provides by welding. | null | closed | Replaced Liner , piston , piston ring , bearings & delivery valve assl
2022-11-08 | Robin Refrigeration Works | Odisha | D | Capital Refrigeration & Engineering Industry | Odisha | KCX2 | 3364K2351 | 3331806200 | 2022-11-01 | 333180 | 2022-11-01 | shaft seal leakage | 2022-09-28 | 2022-09-28 | 1.5 | null | ice plant | 1 | Replaced O ring & lapping done but seal found leak. Refrigerant R22 | null | closed | Replaced shaft seal assembly
2022-11-08 | Pragya Industrial Supply | Karnataka | D | Manasa Ice Plant | Karnataka | KCX6 | 3394K2024 | 3315826189 | 2022-10-21 | 331582 | 2022-10-20 | solenoid valve coil not working | 2022-09-07 | 2022-10-20 | 3 | null | ice plant | 1 | Site observations not mentioned in FRR & FSR. | null | closed | Replaced solenoid valve coil
2022-11-08 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Frontline Exports Pvt Ltd | Kerala | KCX72 | 3474K459 | 3309286185 | 2022-10-19 | 330928 | 2022-10-18 | high oil carryover | 2021-03-29 | 2022-07-12 | 676 | null | meat/fish process | 4 | Cylinder liner step cut mark - 1 , Piston rings wornout 8 nos , Discharge valve leak - 2 | null | closed | Replaced liner1, piston ring set8, DV2
2022-11-08 | Trade Links | Secunderabad | D | Banyan Sustainable Waste Management P Ltd | Telangana | KCX6 | 3394K1970 | 3318066181 | 2022-10-18 | 331806 | 2022-10-17 | k5 valve leakage | 2022-03-14 | 2022-10-17 | 4 | null | others | 6 | K5 Valve leakage - site analysis is missing in FSR | null | closed | Replaced K5 Valve
2022-11-08 | Trade Links | Secunderabad | D | Nichino Chemical India Pvt Ltd | Telangana | KCX6 | 3394K1846 | 3320226179 | 2022-10-17 | 332022 | 2022-10-17 | cylinder overheating | 2022-07-31 | 2021-10-31 | 3150 | null | chemical / pharma | 1 | Cylinder no. 6 temp found above 160 deg c , Delivery valve ring spring broken and buffer spring shrink. | null | closed | Replaced delivery valve assly & buffer spring.
2022-11-14 | Parag Marketing Services | null | D | Sunfresh Agro Industries Pvt Ltd | Shrirampur | KCX72 | 3474K517 | 3357226219 | 2022-11-10 | 335722 | 2022-11-05 | loading unloading problem. | 2022-01-24 | 2022-09-14 | 27 | null | dairy / ice cream | 9 | NO Type Solenoid valve not working.Oil not pass. | null | closed | Replaced NO Type solenoid valve
2022-11-14 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K2896 | 3167366041 | 2022-08-16 | 316736 | 2022-08-01 | shaft seal leakage | 2021-09-03 | 2021-11-21 | 4145 | null | food processing | 2 | Shaft seal leakage & High vibrations observed. Oring replaced but problem not resolved. | null | closed | Replaced shaft seal assly
2022-11-14 | Parag Marketing Services | null | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1924 | 3366366218 | 2022-11-10 | 336636 | 2022-11-08 | shaft seal leakage | 2021-12-27 | 2022-07-14 | 83 | null | food processing | 7 | Shaft seal leakage & replaced. (FRR Remark : wrong site analysisi & site photos not attched.) | null | closed | Replaced shaft seal assembly
2022-11-14 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Botco Charitable Society | Kerala | KCX2 | 3364K2278 | 3179146022 | 2022-08-08 | 317914 | 2022-08-06 | pressure gauge out & male run tee thredaing damaged. | 2022-02-26 | 2022-08-06 | 15 | null | ice plant | 6 | Suction pressure gauge out & Male run tee thredaing damaged. | null | closed | Replaced pressure gauge & male run tee
2022-11-14 | Parag Marketing Services | null | D | Harbour Arabian Exports | Ratnagiri | KCX51 | 3454K198 | 3305826163 | 2022-10-12 | 330582 | 2022-10-11 | delivery valve leakage | 2022-03-28 | 2022-10-11 | 24 | null | meat/fish process | 6 | HP Cylinder delivery valve leakage , rectified by cleaning. Again found leak. Replaced valve kit due to HP cylinder. | null | closed | Replaced DV assly
2022-11-14 | Kalp Marketing | Gujrat | D | Shyam Marine Foods | Veraval, Gujarat | KCX72 | 3474K466 | 3317886178 | 2022-10-17 | 331788 | 2022-10-17 | high oil carryover | 2021-04-26 | 2021-11-01 | 1193 | null | meat/fish process | 6 | Oil found in VLD. Orings replaced | null | closed | Replaced VLD Orings
2022-11-14 | Parag Marketing Services | null | D | Finolex Industries Limited | Ratnagiri | KCX3 | 3374K2909 | 3297786177 | 2022-10-17 | 329778 | 2022-10-15 | k5 valve leakage | 2022-09-16 | 2022-10-15 | 17 | null | chemical / pharma | 1 | Site analysis not mentioned in FSR | null | closed | Replaced K5 Valve
2022-11-22 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ambernath Organic | Thane | KC3 | 337K4826 | 3209046213 | 2022-11-07 | 320904 | 2022-09-26 | op pressure switch malfunctioning | 2022-03-25 | 2022-09-26 | 120 | null | ice plant | 6 | OP Pressure switch not working | null | closed | Replaced OP Pressure switch
2022-11-22 | Multivista Global Pvt Ltd | Gurgaon | D | Green Earth Cryogenics | Haryana | KCX72 | 3474K444 | 3378486223 | 2022-11-14 | 337848 | 2022-11-11 | cylinder overheatingpiston crack | 2021-01-30 | 2022-01-08 | 4175 | null | others | 12 | Piston crack | null | closed | Replaced piston and ring set
2022-11-30 | Cool Comfort Private Limited | West Bengal | D | Maa Jharboni Cold Storage | West Bengal | KCX4 | 3384K2919 | 3343826204 | 2022-11-01 | 334382 | 2022-11-25 | high oil consumption | 2021-11-30 | 2022-02-28 | 1868 | null | cold storage | 3 | Cyl no.1 Piston ring wornout & cut mark in liner | null | closed | Replaced Piston ring set1 & Liner1
2022-11-30 | Multivista Global Pvt Ltd | Gurgaon | D | Hfl Consumater Private Limited | Uttar Pradesh | KCX9 | 3404K0193 | Service email | 2022-12-02 | 336634 | 2022-11-08 | shaft seal leakage | 2021-05-31 | 2022-05-27 | 1872 | null | dairy / ice cream | 12 | Shaft seal leakage , Orings replaced | null | closed | Orings replaced
2022-11-30 | Trade Links | Secunderabad | D | Sony Ice Factory | Andhra Pradesh | KCX6 | 3394K2004 | Service email | 2022-12-02 | 334402 | 2022-11-21 | compressor welding leak/ crack at foot. | 2022-05-17 | 2022-09-09 | PC | null | ice plant | 3 | Compressor foot no.3 crack - Comp called back for rectification. | null | closed | Compressor rectified at KPCL
2022-11-30 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Al Falah Factory | Kerala | KCX4 | 3384K2987 | 3392486228 | 2022-11-18 | 339248 | 2022-11-16 | cylinder overheating | 2022-01-22 | 2022-09-20 | 1311 | null | ice plant | 8 | Cyl no. 1 & 3 delivery valve leakage | null | closed | Replaced DV2
2022-11-30 | Pragya Industrial Supply | Karnataka | D | Vignaraja Ice Plant | Karnataka | KCX6 | 3394K1852 | 3396426225 | 2022-11-16 | 339642 | 2022-11-16 | delivery valve leakage | 2021-08-28 | 2022-10-31 | 414 | null | ice plant | 14 | Cyl no. 3,4&6 overheating due to Delivery valve leak. Site Analysis: suction & discharge bypass line provided by welding. | null | closed | Replaced DV3
2022-11-30 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Jeyes Enterprises | Kerala | KCX2 | 3364K2300 | 3378646224 | 2022-11-14 | 337864 | 2022-11-12 | high oil consumption | 2022-03-28 | 2022-07-07 | 2750 | null | ice plant | 3 | Piston ring set wornout | null | closed | Replaced piston ring set 2
2022-12-10 | Parag Marketing Services | null | D | Laxmi Ice And Cold Storage | Maharashtra | KCX3 | 3374K2728 | 3430686251 | 2022-11-29 | 343068 | 2022-11-23 | k5 valve leakage | 2021-12-20 | 2022-03-28 | 2166 | null | ice plant | 3 | K5 Valve gas leakage from steam. | null | closed | Replaced K5 Valve
2022-12-10 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX63 | 3464K121 | 3414486230 | 2022-11-21 | 341448 | 2022-11-19 | high oil consumption | 2021-03-26 | 2021-11-26 | 1781 | null | chemical / pharma | 8 | ORV Leakage 4 nos & VLD Orings flat 9 nos replaced | null | closed | ORV Leakage 4 nos & VLD Orings flat 9 nos replaced
2022-12-16 | Trade Links | Secunderabad | D | Siri Ice Links | Andhra Pradesh | KCX4 | 3384K2992 | 3339726216 | 2022-11-08 | 333972 | 2022-11-08 | oil pressure problem | 2022-01-24 | 2022-03-03 | 4328 | null | ice plant | 1 | KCX oil pump tang broken | null | closed | KCX oil pump element
2022-12-16 | Gargi Engineering Enterprices Pvt Ltd | Baroda | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX51 | 3454K0210 | email | 2022-11-29 | null | 2022-11-29 | leakage from oil return line 15 dia.pin and ferule | 2022-10-31 | 2022-11-29 | 0 | null | chemical / pharma | 1 | Leakage from Oil return line 15 dia.Pin and ferule | null | closed | 15 Dia.pin and ferule
2022-12-16 | Trade Links | Secunderabad | D | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 3434606248 | 2022-11-29 | 343460 | 2022-11-28 | shaft seal leakage | 2022-09-20 | 2022-11-22 | 68 | null | chemical / pharma | 2 | Freon application shaft seal leak arrested by using Viton Oring | null | closed | Shaft seal assly
2022-12-19 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Vasudev Haregovind Cold Chain | Gujrat | KCX31 | 3434K0182 | 3435386244 | 2022-11-28 | 343538 | 2022-11-26 | pressure guage not working | 2022-03-15 | 2022-11-26 | 6 | null | cold storage | 8 | 0-25 kg/cm2 pressure gauge not working | null | closed | Replaced 025kg/cm2 pressure gauge
2022-12-19 | Trade Links | Secunderabad | D | Sony Ice Factory | Andhra Pradesh | KCX6 | 3394K2004 | 3512826287 | 2022-12-15 | 351582 | 2022-12-15 | base frame warpage | 2022-05-17 | 2022-09-09 | PC | null | ice plant | 3 | Replaced base frame due to warpage | null | closed | Base frame
2022-12-19 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3454K191 | 3428806241 | 2022-11-25 | 342880 | 2022-11-24 | oil carry over | 2021-06-23 | 2021-08-25 | 3723 | null | meat/fish process | 2 | Piston ring set wornout | null | closed | Replaced piston ring set
2022-12-21 | Trade Links | Secunderabad | D | Bsr Industries | Telangana | KCX3 | 3374K2993 | 3519686289 | 2022-12-20 | 351968 | 2022-12-20 | shaft seal cover drain pipe not fitted | 2022-12-05 | 2022-12-16 | 0 | null | cold storage | 1 | Shaft seal drain pipe not fitted | null | closed | null
2022-12-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Gro Enterprises | Kochi | KCX31 | 3434K0187 | email | 2022-12-20 | null | 2022-12-20 | connecting rod no 1 & 2 bolts found partially tightened.improper fitment gap observed between bolt head and conrod face. | 2022-08-29 | 2022-12-20 | 0 | null | meat/fish process | 3 | Gap found between conrod face and bolt head | null | closed | null
2022-12-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX42 | 3444K375 | email | 2022-12-30 | null | 2022-12-30 | bubbles/blistering on paint surface at discharge pipe | 2022-11-28 | 2022-12-28 | 32 | null | chemical / pharma | 1 | Bubbles/blistering on paint surface at discharge pipe | null | closed | null
2022-12-31 | Parag Marketing Services | null | D | Kpcl | Hadapsar | KRC4 | 3206K001 | Service email | 2022-01-02 | 5657000 | 2022-12-19 | shaft seal leakage and thrust ring wornout | 2022-02-23 | 2022-03-25 | 3300 | null | ac plant | 1 | Replaced shaft seal assly,thrust ring and main bearings | null | closed | Replaced shaft seal assly,thrust ring and main bearings
2022-12-31 | Cool Comfort Private Limited | West Bengal | D | Celebrity Breweries | West Bengal | KCX4 | 3384K3030 | 3525786294 | 2022-12-20 | 352578 | null | abnormal noise | 2022-02-28 | 2022-07-22 | 1314 | null | beverage / breweries | 5 | Replaced delivery valve kit due to springs broken | null | closed | Delivery valve kit1
2022-12-31 | Cool Comfort Private Limited | West Bengal | D | Baba Basantroy Cold Storage | West Bengal | KCX4 | 3384K2989 | 3522026290 | 2022-12-17 | 352202 | 2022-12-17 | oil lifting | 2022-01-23 | 2022-03-31 | 1675 | null | cold storage | 2 | Replaced piston ring set | null | closed | Replaced piston ring set
2022-12-31 | Multivista Global Pvt Ltd | Tamil Nadu | D | Amali Dairy Products | Tamil Nadu | PCX2 | 3106K0110 | 3536046303 | 2022-12-24 | 353404 | 2022-12-24 | wrong pressure switch fitted in control pannel i.e. fitted kp1a instead of kp5a | 2022-08-30 | 2022-12-24 | 0 | null | dairy / ice cream | 3 | Wrong pressure switch fitted in control pannel i.e. fitted KP1A instead of KP5A | null | closed | KP1A
2022-12-31 | Hss Solution Pvt Ltd | Rajasthan | D | Sparsh Industries | Rajastan | KCX2 | 3364K2068 | 3253506114 | 2022-09-13 | 325350 | 2022-09-13 | cylinder overheating | 2021-01-11 | 2021-10-08 | 525 | null | dairy / ice cream | 9 | Piston and liner siezed | null | closed | Replaced piston,piston ring set,liner,del valve
2022-12-31 | Geekay Pneumatic Pvt Ltd | Tamil Nadu | D | Nanda Ice And Cold Storage | Kerala | KCX3 | 3374K2637 | 35404806314 | 2022-12-29 | 354080 | 2022-12-28 | cylinder overheating | 2021-08-25 | 2022-09-13 | 1254 | null | ice plant | 12 | Replaced discharge valve assly-1 | null | closed | Discharge valve assly1
2022-12-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Vasai Frozen Foods | Bhivandi | KCX3 | 3374K2957 | 3501766283 | 2022-12-13 | 350176 | 2022-12-12 | cylinder overheating | 2022-11-12 | 2022-11-23 | 1300 | null | ice plant | 1 | Replaced kit del valve-1 & dicharge valve assly-1 | null | closed | Replaced kit del valve1 & dicharge valve assly1
2022-12-31 | Pragya Industrial Supply | Karnataka | D | Abhimanya Ice Plant | Karnataka | KCX4 | 3384K2818 | 3456526258 | 2022-11-29 | 343652 | 2022-11-28 | discharge valve leakage | 2021-07-19 | 2021-11-27 | 2189 | null | ice plant | 3 | Replaced Discharge valve assly | null | closed | Discahrge valve assly1
2022-12-31 | Trade Links | Secunderabad | D | Lnr Ice Factory | Andhra Pradesh | KCX4 | 3384K3034 | 3503826279 | 2022-12-13 | 350382 | 2022-12-12 | oil lifting | 2022-03-09 | 2022-05-08 | 3838 | null | ice plant | 2 | Replaced piston ring set | null | closed | Piston ring set1
2022-12-31 | Parag Marketing Services | null | D | Finolex Industries Limited | Ratnagiri | KCX3 | 3374K2909 | email | 2022-12-29 | null | 2022-12-29 | high oil carryover | 2022-09-16 | 2022-10-15 | 500 | null | chemical / pharma | 1 | Replaced cylinder liner no 1 two times | null | closed | Replaced cylinder liner
2022-12-31 | Trade Links | Secunderabad | D | Aurbindo Pharma Pvt Ltd | Telangana | KCX42 | 3444K299 | 3438606261 | 2022-11-29 | 343860 | 2022-11-29 | oil lifting | 2021-08-30 | 2022-09-28 | 935 | null | chemical / pharma | 12 | Replaced pistin ring sets 4 nos | null | closed | Piston ring sets4
2023-01-14 | Cool Comfort Private Limited | West Bengal | D | Clebrety Breweries | West Bengal | KCX9 | 3404K251 | 3540486312 | 2022-12-29 | 354048 | 2022-12-27 | delivery valve kit broken | 2022-03-12 | 2022-07-12 | 1412 | null | beverage / breweries | 4 | Replaced del valve kit | null | closed | Delivery valve kit
2023-01-14 | Cool Comfort Private Limited | West Bengal | D | Clebrety Breweries | West Bengal | KCX9 | 3404K250 | 3543766322 | 2022-12-29 | 354376 | 2022-12-29 | delivery valve kit broken | 2022-02-28 | 2022-07-12 | 1794 | null | beverage / breweries | 5 | Kit delivery valve broken | null | closed | Kit delivery valve 1 no.
2023-01-14 | Kalp Marketing | Gujrat | D | Sahaj Cold Storage | Gujrat | KCX2 | 3364K2181 | 3540386311 | 2022-12-28 | 354038 | 2022-12-28 | shaft seal leakage | 2021-07-28 | 2021-12-07 | 1048 | null | cold storage | 5 | O rings flattened , replace do ring kit | null | closed | Orings replaced
2023-01-14 | Multivista Global Pvt Ltd | Chennai | D | Nesam Ice Plant | Pondicherry | KCX2 | 3364K2130 | 3554106335 | 2023-01-04 | 355410 | 2023-01-04 | kcx oil pump pressure not developedpurging | 2021-03-29 | 2022-11-08 | 536 | null | ice plant | 20 | Replaced KCX oil pump assly | null | closed | Replaced KCX oil pump assly
2023-01-14 | Kalp Marketing | Gujrat | D | Rc Enterprises | Gujrat | KCX4 | 3384K2800 | 3535766319 | 2022-12-29 | 353576 | 2022-12-27 | shaft seal leakage | 2021-06-25 | 2022-07-23 | 4212 | null | ice plant | 13 | O rings flattened , replaced oring kit | null | closed | O ring kit shaft seal
2023-01-14 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3454K191 | 3531806320 | 2022-12-29 | 353180 | 2022-12-28 | oil carry over | 2021-06-23 | 2021-08-25 | 4583 | null | meat/fish process | 2 | Delivery valve leakage,liner worn out,piston rings worn out | null | closed | Replaced liner,piston ring and del valve assly,orings
2023-01-14 | Kalp Marketing | Gujrat | D | S S International | Gujrat | KCX93 | 3485K096 | 3533766318 | 2022-12-29 | 353376 | 2022-12-27 | shaft seal leakage | 2021-01-11 | 2021-08-15 | 906 | null | meat/fish process | 7 | Orings flattned | null | closed | Replaced orings
2023-01-14 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX72 | 3474K585 | 3456966330 | 2023-01-02 | 345696 | 2022-12-11 | leakage from oil return line 15 dia.pin and ferule | 2022-11-02 | 2022-12-11 | 0 | null | chemical / pharma | 1 | Leakage from Oil return line 15 dia.Pin and ferule | null | closed | 15 Dia.pin and ferule
2023-01-14 | Parag Marketing Services | null | D | Shivalkashi Chemicals | null | KCX3 | 3374K2960 | Mail 13.01.23 | null | null | null | v belt loose | 2022-11-01 | 2023-01-13 | 0 | null | chemical / pharma | 3 | Variation in length & Batch code of supplied V belts. | null | closed | V Bels 4 nos.
2023-01-25 | Parag Marketing Services | null | D | Gravis Foods | Shirval | KCX72 | 3474K511 | 3350726333 | 2023-01-03 | 335072 | 2022-12-22 | oil carry over | 2021-11-30 | 2022-04-19 | 3478 | null | dairy / ice cream | 5 | Replaced Piston ring set,ORV | null | closed | Replaced Piston ring set,ORV
2023-01-25 | Parag Marketing Services | null | D | Gravis Foods | Shirval | KCX102 | 3495K001 | 3380326334 | 2023-01-03 | 338032 | 2022-12-12 | scoring marks kcx fw side bearing | 2021-11-30 | 2022-12-12 | 8 | null | dairy / ice cream | 12 | Replaced bearing due to scoring marks | null | closed | Replaced FW side bearing
2023-01-25 | Gargi Engineering Enterprices Pvt Ltd | null | D | Jay Chemical Industries | Gujrat | KCX9 | 3404K0246 | 3363126304 | 2022-12-26 | 336312 | 2022-11-25 | abnormal noise | 2022-02-12 | 2022-07-26 | 965 | null | ice plant | 5 | Replaced piston,liner,delivery valve,valve kit,buffer spring | null | closed | Rieplaced piston,liner,delivery valve,valve kit,buffer spring
2023-01-31 | Multivista Global Pvt Ltd | null | D | Ar Dairy Food Pvt Ltd | Tamil Nadu | PCX2 | 3106K0173 | 3557786347 | 2023-01-09 | 355778 | 2023-01-08 | pcx2 discharge oil filter damaged / magnetic element | 2022-06-29 | 2022-08-27 | 37 | null | dairy / ice cream | 2 | Replaced discharge filter PCX2/Magnetic elemnt | null | closed | Replaced discharge filter PCX2/Magnetic elemnt
2023-01-31 | Multivista Global Pvt Ltd | null | D | Vignaraja Ice Plant | Karnataka | KCX6 | 3394K1852 | 3540866317 | 2022-12-29 | 354086 | 2022-12-28 | abnormal noise | 2021-08-28 | 2022-10-31 | 930 | null | ice plant | 14 | Replaced piston,liner,piston ring set,del valve | null | closed | Replaced piston,liner,piston ring set,del valve
2023-01-31 | Kalp Marketing | Gujrat | D | Rc Enterprises | Gujrat | KCX4 | 3384K2800 | 3563966371 | 2023-01-19 | 356396 | 2023-01-16 | cylinder overheating | 2021-06-25 | 2022-07-23 | 2132 | null | ice plant | 13 | Replaced delivery valve kit | null | closed | Replaced del valve kit.
2023-01-31 | Pragya Industrial Supply | Karnataka | D | Mahalaxmi Ice Plant | Karnataka | KCX4 | 3384K2816 | 3565906362 | 2023-01-14 | 356590 | 2023-01-14 | kcx oil pump element tang broken | 2021-07-19 | 2022-02-19 | 3344 | null | ice plant | 7 | Replaced pump element | null | closed | Replaced pump element KCX
2023-01-31 | Trade Links | Secunderabad | D | Niranjan Industries | Goa | KCX3 | 3374K2860 | 3346326259 | 2022-11-29 | 334632 | 2022-11-09 | oil carry over | 2022-05-13 | 2022-07-31 | 2052 | null | ice plant | 3 | Replaced liner,piston,piston ring set | null | closed | Replaced liner,piston,piston ring set
2023-02-11 | Trade Links | Secunderabad | D | Plr Foods Pvt Ltd | Andhra Pradesh | KCX93 | 3485K0127 | 3358026350 | 2023-01-09 | 355802 | 2023-01-09 | shaft seal leakage | 2022-03-27 | 2022-07-08 | 222 | null | food processing | 3 | Replacced shaft seal assly | null | closed | Shaft seal assly
2023-02-14 | Multivista Global Pvt Ltd | null | D | Varun Beverages Limited | Chennai | KCX9 | 3404K274 | email | null | 362440 | 2023-02-15 | direct drive coupling hub broken | 2022-08-28 | 2023-02-15 | 8 | null | beverage / breweries | 5 | Replaced Coupling piece | null | closed | Replaced coupling piece
2023-02-14 | Cool Comfort Private Limited | West Bengal | D | Arati Maya Cold Storage Pvt Ltd | West Bengal | KCX3 | 3374K2749 | 3605786403 | 2023-01-31 | 360578 | 2023-01-31 | overheatingpiston crack | 2022-01-04 | 2022-03-17 | 647 | null | cold storage | 2 | Replaced Piston ,kit delivery valve-1 | null | closed | Replaced Piston ,kit delivery valve1
2023-02-14 | Pragya Industrial Supply | Karnataka | D | Sheetal Ice Plant | Karnataka | KCX6 | 3394K1853 | 3600606396 | 2023-01-27 | 360060 | 2023-01-26 | high oil consumption | 2021-08-28 | 2022-09-17 | 1980 | null | ice plant | 1 | Replace piston ring set & cylinder liner | null | closed | Replaced piston ring set3, cylinder liner2
2023-02-14 | Geekay Pneumatic Pvt Ltd | null | D | Al-Falah Ice Factory | Kerala | KCX4 | 3384K2987 | 3606186408 | 2023-02-02 | 360618 | 2023-02-02 | over heating | 2022-01-22 | 2022-09-20 | 2616 | null | ice plant | 8 | Replaced Discharge valve assly-1 | null | closed | Replaced Discharge valve assly1
2023-02-14 | Kalp Marketing | Gujrat | D | Sun Exports | Gujrat | KCX72 | 3474K560 | 3569766373 | 2023-01-19 | 356976 | 2023-01-17 | oil carry over | 2022-07-27 | 2022-11-07 | 1120 | null | meat/fish process | 4 | Replaced VLD Orings | null | closed | Replaced VLD Orings
2023-02-14 | Kalp Marketing | Gujrat | D | Ocean Aquatech Product | Gujrat | KCX72 | 3474K457 | 3571666372 | 2023-01-19 | 357168 | 2023-01-18 | oil carry over | 2021-03-27 | 2021-09-03 | 3036 | null | meat/fish process | 5 | Replaced VLD orings | null | closed | Replaced VLD Orings
2023-02-14 | Kalp Marketing | Gujrat | D | Nishi Indoo Foods | Junagadh Veraval, Gujarat | KCX51 | 3454K0191 | 3571946397 | 2023-01-27 | 357194 | 2023-01-27 | oil carryover piston crack | 2021-06-23 | 2021-08-25 | 4752 | null | meat/fish process | 2 | Replaced Piston ,liner,piston ringset,VLD orings | null | closed | Replaced Piston ,liner,piston ringset,VLD orings
2023-02-14 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K019 | 3622826426 | 2023-02-10 | 362282 | 2023-02-10 | over heating | 2021-11-20 | 2022-01-18 | 9328 | null | chemical / pharma | 2 | Replaced Discharge valve assly-1 | null | closed | Replaced Discharge valve assly1
2023-02-25 | Model Pneumatic Co | Punjab | D | Kartik Cold Storage | Punjab | KCX3 | 3374K2849 | 3610746414 | 2023-02-04 | 361074 | 2023-02-04 | stop valve leakage | 2022-03-30 | 2023-02-04 | 0 | null | cold storage | 10 | Stop valve Tal 50 leakage | null | closed | Replaced stop valve
2023-02-25 | Parag Marketing Services | null | D | Krushnai Milk | Satara | KCX2 | 3364K2348 | 3625346431 | 2023-02-15 | 362534 | 2023-02-14 | k5 valve leakage | 2022-09-25 | 2022-12-14 | 246 | null | dairy / ice cream | 3 | K5 Valve leakage | null | closed | Replaced K5 Valve
2023-02-25 | Kalp Marketing | Gujrat | D | Vrs Foods Ltd | Madhya Pradesh | KCX9 | 3404K283 | 3597746409 | 2023-02-02 | 359774 | 2023-01-31 | over heating | 2022-09-23 | 2022-11-03 | 1274 | null | dairy / ice cream | 3 | Cyl.no. 8 overheating due to kit broken | null | closed | Replaced delivery valve assly
2023-02-25 | Multivista Global Pvt Ltd | Chennai | D | Ar Ice Blocks | Tamil Nadu | KCX4 | 3384K3057 | 3435446246 | 2022-11-26 | 343544 | 2022-11-28 | oil carry over | 2022-03-29 | 2022-09-27 | 891 | null | ice plant | 6 | Replaced cylinder liner,piston ring set, del. Valve assly | null | closed | Replaced cylinder liner,piston ring set,Del valve assly
2023-02-25 | Geekay Pneumatic Pvt Ltd | Kerala | D | Marine Ice Plant | Kerala | KCX3 | 3374K2850 | 3620406427 | 2023-02-11 | 362040 | 2023-02-11 | over heating | 2022-04-09 | 2022-09-28 | 2770 | null | ice plant | 5 | Replaced Piston,piston ring set,discharge valve assly | null | closed | Replaced Piston,piston ring set,discharge valve assly
2023-02-25 | Trade Links | null | D | Anjali Ice Factory | Andhra Pradesh | KCX6 | 3394K1869 | 3627566444 | 2023-02-18 | 362756 | 2023-02-17 | over heating | 2021-09-04 | 2021-09-18 | 6838 | null | ice plant | 1 | Cylinder no.1 overheating due to delivery valve leakage & spring broken. | null | closed | Replaced discharge valve assly
2023-02-25 | Parag Marketing Services | null | D | Harbour Arabian Exports | Ratnagiri | KCX51 | 3454K198 | 3624946433 | 2023-02-16 | 362494 | 2023-02-15 | shaft seal leakage | 2022-03-28 | 2022-10-11 | 464 | null | meat/fish process | 7 | Shaft seal assly-site issue | null | closed | Replaced shaft seal assly
2023-02-25 | Pragya Industrial Supply | Karnataka | D | Sicgil Industrial Gases Ltd | Karnataka | KCX93 | 3485K145 | 3618986424 | 2023-02-09 | 361898 | 2023-02-08 | shaft seal leakage | 2022-10-31 | 2023-01-13 | 18 | null | chemical / pharma | 3 | Oil pressure problem , shaft seal leakage. | null | closed | Replaced Pump assly,Bearings & shaft seal assly.
2023-02-25 | Trade Links | null | D | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 3561786349 | 2023-01-09 | 356178 | 2023-01-09 | shaft seal leakage | 2022-09-20 | 2022-11-22 | 395 | null | chemical / pharma | 3 | Shaft seal leakage - R22 | null | closed | Replaced shaft seal assly
2023-03-20 | Multivista Global Pvt Ltd | Tamil Nadu | D | Varun Beverages Limited | Tamil Nadu | KCX9 | 3404K274 | 3627866453 | 2023-02-23 | 362786 | 2023-03-08 | coupling piece broken | 2022-08-28 | 2023-02-15 | 4 | null | beverage / breweries | 6 | Site analysis missing in FSR | null | closed | Replaced Nylock nut 16 nos & Spacer reel 1 no.
2023-03-20 | Multivista Global Pvt Ltd | Tamil Nadu | D | Daler Lakshmi Cold Storage | Uttar Pradesh | KC6 | 339K3644 | 3640406461 | 2023-02-27 | 364040 | 2023-02-27 | solenoid valve coil not working | 2022-11-05 | 2023-02-27 | 10 | null | cold storage | 3 | Solenoid valve coil not working. | null | closed | Replaced solenoid valve coil1
2023-03-20 | Parag Marketing Services | Pune | D | Kolhapur Zila Sahakari Dudh Utpadak Sangh | Kolhapur | KCX6 | 3394K1925 | 3624446452 | 2023-02-23 | 362444 | 2023-02-22 | knocking / abnormal sound | 2022-01-10 | 2022-10-17 | 650 | null | dairy / ice cream | 10 | Cyl no. 1 & 6 has knocking sound. Cyl 6 delivery valve ring spring broken , bufferspring shrinkage , cylinder seized. Cyl no. 6 piston crack. | null | closed | Replaced cylinder assly
2023-03-20 | Multivista Global Pvt Ltd | Tamil Nadu | D | Nufarm Frozens Pvt Ltd | null | KC72 | 347K1003 | 3638066460 | 2023-02-27 | 363806 | 2023-02-26 | suction valve spring defective | 2023-02-11 | 2023-02-26 | 3 | null | food processing | 1 | Site analysis & photos are missing | null | closed | Replaced valve spring suction2
2023-03-20 | Model Pneumatic Co | Punjab | D | Nestle India Ltd | Himachal Pradesh | KCX6 | 3394K2027 | 3634286474 | 2023-03-04 | 363428 | 2023-03-03 | wrong supply of solenoid valve coil | 2022-08-23 | 2023-03-03 | 2 | null | food processing | 7 | Order was 24VDC Coil however supplied 230 VAC. | null | closed | Replaced coils
2023-03-20 | Model Pneumatic Co | Punjab | D | Nestle India Ltd | Himachal Pradesh | KCX6 | 3394K2026 | 3634306475 | 2023-03-04 | 463430 | 2023-03-03 | wrong supply of solenoid valve coil | 2022-08-23 | 2023-03-03 | 2 | null | food processing | 7 | Order was 24VDC Coil however supplied 230 VAC. | null | closed | Replaced coils
2023-03-20 | Multivista Global Pvt Ltd | Tamil Nadu | D | Ar Ice Blocks | Tamil Nadu | KCX4 | 3384K3057 | 3653406492 | 2023-03-14 | 365340 | 2023-03-14 | krms controller board malfunctioning | 2022-03-29 | 2022-09-27 | 1026 | null | ice plant | 6 | High discharge temp alarm issue.Site analysis missing. | null | closed | Replaced controller
2023-03-20 | Multivista Global Pvt Ltd | Tamil Nadu | D | Ar Ice Blocks | Tamil Nadu | KCX4 | 3384K3057 | 3628526456 | 2023-02-24 | 362852 | 2023-02-22 | oil carryover piston crack | 2022-03-29 | 2022-09-27 | 856 | null | ice plant | 6 | Piston crack | null | closed | Replaced Piston 1 & Piston ring set2
2023-03-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Fathima Ice Industries | Kerala | KCX3 | 3374K2668 | 3049886487 | 2023-03-12 | 364988 | 2023-03-10 | over heating | 2021-08-31 | 2022-06-08 | 3864 | null | ice plant | 10 | Delivery valve leakage , stroke limitor wornout | null | closed | Replaced DV
2023-03-20 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K019 | 3634826450 | 2023-02-22 | 363482 | 2023-02-22 | abnormal noise | 2021-11-20 | 2022-01-18 | 9587 | null | chemical / pharma | 2 | HP Cyl.4 - Liner gasket damaged, Piston top clearance reduced & abnormal sound. Piston ring wornout & Needle roller bearing spacer damaged. Incomplate FSR Vibrating readings are missing. | null | closed | Replaced Piston ring set 1 & Needle roller bearing 2 , spacer 1
2023-03-20 | Kalp Marketing | Gujrat | D | Godrej Consumer Products Ltd | Madhya Pradesh | KCX12 | 3415K044 | 367246462 | 2023-02-28 | 363724 | 2023-02-26 | piston crack | 2021-12-21 | 2022-05-24 | 264 | null | chemical / pharma | 5 | Cyl no. 4 & 6 tap bolts are broken and cylinder 4 piston crack. | null | closed | Replaced Piston
2023-03-27 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Pitambara Cold Storage | Uttar Pradesh | KC6 | 339K3674 | 3641786484 | 2023-03-09 | 364178 | 2023-03-08 | abnormal noisesuction valve spring broken | 2023-01-22 | 2023-03-08 | 4 | null | cold storage | 1 | Knocking sound from cylinder no 03 ,replaced cylinder liner,piston,piston ring set,del valve assly, suction valve ring and spring | null | closed | Replaced cylinder liner,piston,piston ring set,del valve assly, suction valve ring and spring
2023-03-27 | Model Pneumatic Co | Punjab | D | Daliwal Cold Storage | Punjab | KCX4 | 3384K3197 | 3640306482 | 2023-03-07 | 364030 | 2023-03-06 | op pressure switch malfunctioning | 2022-12-06 | 2023-03-06 | 23 | null | cold storage | 3 | Pressure switch not working | null | closed | Replaced MP55A pressure switch
2023-03-27 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX84 | 3305K025 | 3642306470 | 2023-03-03 | 364230 | 2023-03-02 | overheatingdelivery valve spring broken | 2022-09-28 | 2022-11-12 | 2500 | null | chemical / pharma | 2 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-03-29 | Kirloskar Pneumatic Co Ltd | New Delhi | D | United Farm | Haryana | KCX9 | 3404K210 | 3655986509 | 2023-03-21 | 365598 | 2023-03-21 | discharge valve assembly | 2021-08-30 | 2023-03-21 | 0 | null | meat/fish process | 19 | Replaced discharge valve assly | null | closed | Del valve assly
2023-03-29 | Trade Links | Secunderabad | D | Shimoga Health Care | Andhra Pradesh | KCX2 | 3364K2428 | 3651646488 | 2023-03-13 | 365164 | 2023-03-12 | key loose in c.shaft keyway | 2023-02-18 | 2023-03-12 | 5 | null | chemical / pharma | 1 | Replaced key | null | closed | Key
2023-03-31 | Cool Comfort Private Limited | West Bengal | D | Bhanulal Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K1940 | 3658706512 | 2023-03-23 | 365870 | 2023-03-22 | cylinder overheatingdelivery valve kit broken | 2022-01-21 | 2022-03-27 | 2936 | null | cold storage | 2 | Replaced kit del valve-1 | null | closed | Replaced kit del valve 1
2023-03-31 | Kalp Marketing | Gujrat | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX42 | 3444K309 | 3663846523 | 2023-03-27 | 366384 | 2023-03-27 | high oil consumption | 2021-10-24 | 2022-12-31 | 764 | null | cold storage | 2 | Replaced Piston ring set | null | closed | Replaced Piston ring set
2023-03-31 | Kalp Marketing | Gujrat | D | Gadre Marine Export Pvt Ltd | Ratnagiri | KCX42 | 3444K309 | 3642346521 | 2023-03-27 | 364234 | 2023-03-03 | oil carry over | 2021-10-24 | 2022-12-31 | 584 | null | cold storage | 2 | Replaced Piston ring set | null | closed | Piston ring set, VLD Orings
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Biswar Sheetgrah Pvt Ltd | Uttar Pradesh | KC6 | 339K3655 | 3642246468 | 2023-03-02 | 364224 | 2023-03-15 | pressure gauge damaged | 2022-12-24 | 2023-03-01 | ZH | null | cold storage | 2 | Replaced pr. Gauge -760 to 16 kg/cm2 | null | closed | Replaced pr. Gauge 760 to 16 kg/cm2
2023-03-31 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Veekay Cold Storage | Gujrat | KCX4 | 3384K3161 | 3650226491 | 2023-03-14 | 365022 | 2022-03-14 | retaining plate nut welding damaged | 2022-11-11 | 2023-03-14 | 6 | null | cold storage | 3 | Replaced Retaining plate | null | closed | Retaining plate
2023-03-31 | Pragya Industrial Supply | Karnataka | D | Himalaya Cold Storage | Karnataka | KCX3 | 3374K3072 | 3622286528 | 2023-03-28 | 362228 | 2023-02-09 | rms device not working | 2023-01-22 | 2023-01-31 | 50 | null | cold storage | 1 | Replaced RMS device | null | closed | Replaced RMS device
2023-03-31 | Model Pneumatic Co | Punjab | D | Narsingh Cold Storgae | Punjab | KCX3 | 3374K2702 | 3643226473 | 2023-03-03 | 364322 | 2023-03-02 | shaft seal leakage | 2021-11-26 | 2022-02-11 | 2000 | null | cold storage | 3 | Replaced Shaft seal assly | null | closed | Shaft seal assly
2023-03-31 | Parag Marketing Services | null | D | Graviss Food Pvt Ltd | Satara | KCX72 | 3474K511 | 3649286496 | 2023-03-16 | 364928 | 2023-03-15 | oil carry over | 2021-11-30 | 2022-04-19 | 4388 | null | dairy / ice cream | 4 | Replaced float valve | null | closed | Float valve
2023-03-31 | Parag Marketing Services | null | D | Suman Agro | Vaduj | KCX4 | 3384K3043 | 3661226530 | 2023-03-28 | 366122 | 2023-03-28 | flywheel fitment issue | 2022-03-15 | 2022-03-28 | 0 | null | dairy / ice cream | 1 | Replaced Flywheel | null | closed | Replaced Flywheel
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Govind Dairy | Uttar Pradesh | KC4 | 338K5791 | 3661086518 | 2023-03-25 | 366108 | 2023-03-24 | solenoid valve coil burnt | 2022-11-19 | 2023-03-24 | 3 | null | dairy / ice cream | 4 | Replaced Sol valve | null | closed | Replaced sol valve
2023-03-31 | Parag Marketing Services | null | D | Frutons Exports | Nashik | KCX31 | 3434K0193 | 3664506526 | 2023-03-27 | 366450 | 2023-03-27 | rms device not working | 2022-12-02 | 2023-03-15 | 0 | null | food processing | 3 | Replaced RMS device | null | closed | RMS Device
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uttar Pradesh | KC84 | 330K58 | 3618206517 | 2023-03-24 | 361820 | 2023-03-30 | solenoid valve malfuctioning | 2022-10-08 | 2023-01-30 | 611 | null | food processing | 3 | Replaced sol valve | null | closed | Replaced sol valve
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uttar Pradesh | KC84 | 330K59 | 3666186540 | 2023-03-31 | 366618 | 2023-03-31 | solenoid valve not working | 2022-10-08 | 2023-01-14 | 823 | null | food processing | 4 | Replaced Sol valve-4 nos | null | closed | Sol valve4 nos
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uttar Pradesh | KC4 | 338K5788 | 3666206541 | 2023-03-31 | 366620 | 2023-03-31 | solenoid valve not working | 2022-10-08 | 2023-01-30 | 651 | null | food processing | 4 | Replaced Sol valve | null | closed | Sol valve
2023-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uttar Pradesh | KC84 | 330K60 | 3618186516 | 2023-03-24 | 361818 | 2023-03-30 | solenoid valve not working | 2022-10-08 | 2023-01-30 | 628 | null | food processing | 4 | Replaced solenoid valve | null | closed | Replaced sol valve
2023-03-31 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX1 | 3354K237 | 3650626507 | 2023-03-21 | 365062 | 2023-03-20 | cylinder overheatingdischarge valve leakage | 2022-01-28 | 2022-09-20 | 25779 | null | ice plant | 8 | Replaced del valve assly | null | closed | Del valve assly
2023-03-31 | Kalp Marketing | Gujrat | D | Rc Enterprises | Gujrat | KCX4 | 3384K2801 | 3660806522 | 2023-03-27 | 366080 | 2023-03-27 | cylinder overheatingstep mark on del stroke limitor | 2021-06-25 | 2022-07-23 | 2620 | null | ice plant | 12 | Replaced piston,liner,piston ring set,del valve | null | closed | Replaced piston,liner,piston ring set,del valve
2023-03-31 | Kalp Marketing | Gujrat | D | R K K Sea Food | Gujrat | KCX6 | 3394K1932 | 3663906524 | 2023-03-27 | 366390 | 2023-03-27 | delivery valve leakagestroke limitor step mark | 2022-01-02 | 2022-07-21 | 896 | null | ice plant | 7 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-03-31 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kumbhaza Ice Plant | Kerala | KCX3 | 3374K2927 | 3654826497 | 2023-03-16 | 365482 | 2023-03-16 | pressure gauge not working | 2022-10-03 | 2023-03-16 | 26 | null | ice plant | 6 | Replaced Pressure gauge -760 to 25 KG/Cm2 | null | closed | Replaced Pressure gauge 760 to 25 kg/cm2
2023-03-31 | Kalp Marketing | Gujrat | D | Jinny Marine0Gujarat | null | KCX51 | 3454K207 | 3641386534 | 2023-03-29 | 364138 | 2023-03-24 | abnormal noisesite issue | 2022-09-24 | 2022-11-05 | 959 | null | meat/fish process | 1 | Replaced piston,Bearings | null | closed | Piston,bearings
2023-03-31 | Parag Marketing Services | Pune | D | Finolex Industries Limited | Ratnagiri | KCX3 | 3374K2909 | 3414526436 | 2023-02-16 | 341452 | 2023-02-16 | high oil carryover | 2022-09-16 | 2022-10-15 | 2012 | null | chemical / pharma | 1 | Replaced cylinder liner,piston,piston ring sets-2 nos | null | closed | Replaced cylinder liner,piston,piston ring sets2 nos
2023-04-19 | Hss Solution Pvt Ltd | Rajasthan | D | Shri Agrasen Agrotech Pvt Ltd | Rajastan | KCX3 | 3374K2819 | 3661346543 | 2023-03-31 | 366134 | 2023-04-01 | abnormal noise | 2022-03-09 | 2022-07-20 | 771 | null | cold storage | 4 | Cylinder no. 1 & 2 Liner , Piston , Piston rings wornout. Cyl 2 delivery valve partially leakage. | null | closed | Replaced Liners , Piston ring sets, Gudgeon pins 2 nos each, DV 1 & Main bearings.
2023-04-19 | Parag Marketing Services | Pune | D | Bothera Agro Cold Storage | Maharashtra | KCX3 | 3374K3039 | 3656406533 | 2023-03-29 | 365640 | 2023-03-28 | gauge board fittings leakage | 2023-01-08 | 2023-03-28 | 4 | null | cold storage | 2 | Feamale run tee , ferrule & union nut fiiting leakage. | null | closed | Replaced Feamale run tee 3/8 bsp1 , ferrule set front & back 6 & union nut m6 6
2023-04-19 | Kalp Marketing | Gujrat | D | Divyashakti Foods Private Limited | Madhya Pradesh | KCX4 | 3384K3233 | 3659666529 | 2023-03-28 | 365966 | 2023-03-28 | pressure gauge thread damaged/spoiled. | 2022-12-29 | 2023-03-18 | 1 | null | cold storage | 3 | Feamale eual cross 3/8 BSP & Pressure gauge 16 kg/cm2 threading spoiled. | null | closed | Replaced Feamale eual cross 3/8 BSP & Pressure gauge 16 kg/cm2.
2023-04-19 | Hss Solution Pvt Ltd | Rajasthan | D | Dev Milk | Rajastan | KCX4 | 3384K3260 | 3653326544 | 2023-03-31 | 365332 | 2023-03-23 | solenoid valve not working | 2023-01-13 | 2023-03-23 | 3.9 | null | dairy / ice cream | 2 | Site analysis/observation missing | null | closed | Replaced solenoid valve
2023-04-19 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Satish Enterprises | Ulhasnagar | KCX3 | 3374K3049 | 3665146537 | 2023-03-30 | 366514 | 2023-03-30 | rms device issue(log history not showing) | 2023-01-11 | 2023-02-16 | 0 | null | ice plant | 1 | Log history not showing from the system.(Site analysis/observations missing) | null | closed | Replaced remote monitoring system kit.(Site analysis/observations missing)
2023-04-29 | Cool Comfort Private Limited | West Bengal | D | Shivashri Cold Storage | West Bengal | KCX6 | 3394K2133 | 3666826546 | 2023-04-14 | 366682 | 2023-04-14 | abnormal noise | 2022-12-19 | 2023-03-17 | 210 | null | cold storage | 3 | Piston rings and cylinder liner wornout. | null | closed | Replaced piston ring set 2 nos & Liner 1 no.
2023-04-29 | Model Pneumatic Co | Punjab | D | New Modern Cold Storage | Punjab | KCX4 | 3384K3242 | 3660286536 | 2023-03-30 | 366028 | 2023-03-29 | pump element broken | 2023-01-04 | 2023-03-29 | 4 | LC 12 22 693 | cold storage | 2 | Site analysis not done./ missing | null | closed | Pump assembly
2023-04-29 | Trade Links | Secunderabad | D | Nekkanti Foods Ltd | Andhra Pradesh | KCX72 | 3474K0613 | 3658386535 | 2023-03-30 | 365838 | 2023-03-29 | pump element broken | 2023-01-24 | 2023-03-29 | 6 | LC 12 22 689 | food processing | 2 | Site analysis/observation missing- Element broken may be due to liquid entry during comm. | null | closed | Pump element
2023-04-29 | Pragya Industrial Supply | Karnataka | D | Abhinaya Ice Plant | Karnataka | KCX4 | 3384K2818 | 3675586568 | 2023-04-11 | 367558 | 2023-04-08 | high oil consumption | 2021-07-19 | 2021-11-27 | 2938 | null | ice plant | 4 | Piston ring ovality & Liner wornout. All DV ok. | null | closed | Replaced piston ring set 2 nos & Liner 1 no.
2023-04-29 | Geekay Pneumatic Pvt Ltd | Kerala | D | Choice Trading Cooperation Pvt Ltd | Kerala | KCX72 | 3474K562 | 3671886557 | 2023-04-07 | 367188 | 2023-04-06 | unloading problem | 2022-08-09 | 2022-11-04 | 1771 | null | meat/fish process | 3 | Teflon coming out as per branch remark but it is ok as per FSR remark. | null | closed | Replaced Solenoid valve
2023-04-29 | Trade Links | Secunderabad | D | Benova Labs Pvt Ltd | Telangana | KCX6 | 3394K2146 | 3628246466 | 2023-03-01 | 362824 | 2023-03-01 | shaft seal leakage | 2022-12-30 | 2023-03-01 | 28 | null | chemical / pharma | 3 | R22 Refrigerant. shaft seal leakage issue. | null | closed | Replaced shaft seal assly
2023-04-29 | Trade Links | Secunderabad | D | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 3641526469 | 2023-03-03 | 364152 | 2023-03-01 | shaft seal leakage | 2022-09-20 | 2022-11-22 | 829 | null | chemical / pharma | 2 | R22 Refrigerant. Repeated shaft seal leakage issue. | null | closed | Replaced shaft seal & fitted Viton Oring.
2023-05-24 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Durga Cold Storage & Ice Factory | Uttar Pradesh | KCX4 | 3384K3005 | 3703666587 | 2023-04-17 | 370366 | 2023-04-17 | abnormal noise | 2022-02-07 | 2022-03-15 | 781 | null | cold storage | 1 | High vibrations & Cylinder assly damaged | null | closed | Replaced liner, piston ,piston ring & delivery valve 1 no each.
2023-05-24 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Arihant Storage And Agri Impex Llp | Nagpur | PCX2 | 3106K0184 | 3727706616 | 2023-05-03 | 372770 | 2023-05-03 | stop valve gland nut damaged | 2022-09-30 | 2023-03-31 | 771 | null | cold storage | 6 | Site analysis missing in FSR | null | closed | Replaced gland nut
2023-05-24 | Parag Marketing Services | Pune | D | Graviss Food Pvt Ltd | Shirval | KCX72 | 3474K511 | 3699326615 | 2023-05-03 | 369932 | 2023-05-03 | oil carry over | 2021-11-30 | 2022-04-19 | 5228 | null | dairy / ice cream | 6 | Oil throw in Cyl no. 1,2,3,4,5,7,8 & 9. Also 4 ORVs found blocked. | null | closed | Replaced piston ring set 7 nos & ORVs 4 nos.
2023-05-24 | Multivista Global Pvt Ltd | Gurgaon | D | Kvg Agro Pvt Ltd | Haryana | KCX6 | 3394K2167 | 3717306592 | 2023-04-20 | 371730 | 2023-05-09 | oil pressure problem | 2023-01-15 | 2023-04-13 | 9 | null | dairy / ice cream | 3 | Outer rotor shaft tang broken | null | closed | Replaced pump assembly
2023-05-24 | Trade Links | Secunderabad | D | Plr Foods Pvt Ltd | Andhra Pradesh | KCX93 | 3485K126 | 3705266610 | 2023-04-29 | 370526 | 2023-04-29 | hp suction strainer element damaged. | 2022-04-27 | 2022-07-08 | 414 | null | food processing | 3 | HP Strainer filter damaged. Site analysis missing. | null | closed | Replaced filter
2023-05-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Laxmi Frozen Foods | Uttar Pradesh | KCX3 | 3374K2914 | 3699366595 | 2023-04-21 | 369936 | 2023-05-02 | oil pressure problem | 2022-09-19 | 2022-12-29 | 896 | null | food processing | 3 | Air purging problem | null | closed | Replaced pump assembly
2023-05-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Pair Exports (India) Pvt Ltd | Kerala | KCX72 | 3474K632 | 3683446694 | 2023-04-20 | 368344 | 2023-04-10 | krms smps burned | 2022-02-28 | 2023-04-10 | 8 | null | meat/fish process | 2 | KRMS SMPS is burned. Detail site analysis not mentioned in FSR | null | closed | Replaced SMPS 24VDC
2023-05-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Pair Exports (India) Pvt Ltd | Kerala | KCX72 | 3474K631 | 3683426693 | 2023-04-20 | 368342 | 2023-04-10 | krms smps burned | 2022-02-28 | 2023-04-10 | 12 | null | meat/fish process | 2 | KRMS # 72000110 SMPS is burned. Detail site analysis not mentioned in FSR | null | closed | Replaced SMPS 24VDC
2023-05-24 | Pragya Industrial Supply | Karnataka | D | Karthik Marine | Karnataka | KCX6 | 3394K2019 | 3703566576 | 2023-04-14 | 370356 | 2023-04-13 | lp oil pressure not develop | 2022-08-27 | 2023-03-29 | 19 | null | meat/fish process | 7 | LP Oil pressure not develop & LP Regulator not working. | null | closed | Replaced pump assembly
2023-05-24 | Robin Refrigeration Works | Odisha | D | Sreeragam Exports Pvt Ltd | Odisha | KCX93 | 3485K110 | 3771346640 | 2023-03-15 | 377134 | 2023-05-20 | over heating | 2021-06-29 | 2022-05-04 | 169 | null | meat/fish process | 11 | Cylinder no. 2 HP overheated and seized. | null | closed | Replaced liner , piston , piston ring set , delivery valve kits & assly
2023-05-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kay Kay Exports | Kerala | KCX31 | 3434K0196 | 3600466538 | 2023-03-30 | 360046 | 2023-01-25 | pressure gauge out | 2022-12-21 | 2023-01-25 | 4 | null | meat/fish process | 1 | 16 Kg/cm2 Pressure gauge out | null | closed | Replaced pressure gauge
2023-05-24 | Parag Marketing Services | Pune | D | Aqua Foods Exim | Maharashtra | KCX42 | 3444K326 | 3687586602 | 2023-04-25 | 368756 | 2023-04-25 | shaft seal leakage | 2022-02-20 | 2023-04-05 | 374 | null | meat/fish process | 2 | Site analysis missing in FSR | null | closed | Replaced shaft seal assly
2023-05-30 | Kalp Marketing | Gujrat | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX42 | 3444K362 | Email | 2023-05-22 | null | 2023-05-22 | lp discharge pipe crack | 2022-09-17 | 2022-10-20 | 2438 | null | chemical/dye | 1 | Replaced compressor due to LP discharge pipe crack | null | closed | Replaced Compressor
2023-05-30 | Kalp Marketing | Gujrat | D | Pb Cold Storage | Madhya Pradesh | KC3 | 337K4828 | 3783846659 | 2023-05-25 | 378384 | 2023-05-24 | over heating | 2022-04-29 | 2022-12-20 | 551 | null | cold storage | 8 | Replaced del valve assly,buffer spring. | null | closed | Del valve assly,buffer spring
2023-05-30 | Kalp Marketing | Gujrat | D | Maha Laxmi Dairy Products | Gujrat | KCX3 | 3374K2918 | 3783626653 | 2023-05-23 | 378362 | 2023-05-22 | kcx oil pump tang broken | 2022-09-26 | 2023-05-19 | 5 | null | dairy / ice cream | 8 | KCX oil pump tang broken | null | closed | Replaced Pump element
2023-05-30 | Cool Comfort Private Limited | West Bengal | D | Rajan Seafoods | West Bengal | KCX21 | 3424K141 | Email | 2023-05-26 | null | 2023-05-26 | connecting rod bolts not fitted properly | 2022-07-20 | 2023-05-26 | ZH | null | food processing | 10 | Refitted connecting rod bolts properly | null | closed | null
2023-05-30 | Cool Comfort Private Limited | West Bengal | D | Sreeragam Exports Pvt Ltd | Odisha | KCX93 | 3485K110 | 3771346640 | 2023-03-15 | 377134 | 2023-05-20 | hp strainer wire mesh damaged / torn out | 2021-06-29 | 2022-05-04 | 169 | null | meat/fish process | 11 | Replaced HP strainer element | null | closed | HP Strainer element
2023-05-30 | Kalp Marketing | Gujrat | D | Keshodwala FoodsVeraval | Gujrat | KCX72 | 3474K540 | 3803406666 | 2023-05-27 | 380340 | 2023-05-27 | oil carry over | 2022-03-27 | 2022-09-12 | 942 | null | meat/fish process | 6 | Replaced VLD orings | null | closed | Replaced VLD orings
2023-06-22 | Cool Comfort Private Limited | West Bengal | D | Maa Jarbhoni Cold Storage | West Bengal | KCX4 | 3384K2919 | 3821886694 | 2023-06-05 | 382188 | 2023-06-05 | abnormal noise | 2021-11-30 | 2022-02-28 | 2396 | null | cold storage | 3 | Replaced disk pack of coupling assly | null | closed | Replaced disk pack assly
2023-06-22 | Trade Links | Secunderabad | D | Mega Food ParkTelangana | null | KCX72 | 3474K535 | 3837026712 | 2023-06-13 | 383702 | 2023-06-12 | kcx oil pump tang broken | 2022-03-23 | 2023-06-12 | 7 | null | food processing | 15 | Replaced KCX oil pump assly | null | closed | Replaced KCX oil pump assly
2023-06-22 | Cool Comfort Private Limited | West Bengal | D | Larsen And Toubro Limited | Assam | KCX21 | 3424K136 | 3809386711 | 2023-06-13 | 380938 | 2023-06-12 | cylinder overheating | 2022-05-18 | 2023-02-09 | 945 | null | ice plant | 9 | Replaced safety valve spring and teflon ring | null | closed | Replaced safety valve spring and teflon ring
2023-06-22 | Cool Comfort Private Limited | West Bengal | D | Knc Agro Ltd | West Bengal | KCX3 | 3374K2811 | 3817526680 | 2023-06-01 | 381752 | 2023-05-31 | kcx oil pump tang broken | 2022-02-28 | 2023-05-20 | 7 | null | ice plant | 15 | Replaced KCX oil pump element | null | closed | KCX oil pump element
2023-06-22 | Robin Refrigeration Works | Odisha | D | Sreeragam Exports Pvt Ltd | Odisha | KCX93 | 3485K112 | 3811506697 | 2023-06-06 | 381150 | 2023-06-07 | cylinder overheating | 2021-06-29 | 2022-05-04 | 423 | null | meat/fish process | 11 | Replaced Delivery valve assly | null | closed | Replaced del valve assly
2023-06-22 | Robin Refrigeration Works | Odisha | D | Sreeragam Exports Pvt Ltd | Odisha | KCX93 | 3485K110 | 3811526698 | 2023-06-06 | 381152 | 2023-06-07 | delivery valve leakage | 2021-06-29 | 2022-05-04 | 361 | null | meat/fish process | 11 | Replaced delivery valve kit | null | closed | Replaced del valve kit
2023-06-22 | Trade Links | Secunderabad | D | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 3821306693 | 2023-06-05 | 382130 | 2023-06-05 | shaft seal leakage | 2022-09-20 | 2022-11-20 | 1762 | null | chemical / pharma | 2 | Replaced shaft seal cover | null | closed | Replaced shaft seal cover
2023-06-30 | S. B. Refrigeration Services | Bihar | D | Varun Beverage Limited | Bihar | KCX9 | 3404K199 | 3848606718 | 2023-06-16 | 384860 | 2023-06-16 | cylinder overheatingpiston crack | 2021-08-24 | 2022-01-30 | 2325 | null | beverage / breweries | 5 | Replaced piston due to crack | null | closed | Replaced piston 1 no.
2023-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Ram Enterprises | Uttar Pradesh | KC3 | 337K4847 | 3774406692 | 2023-06-05 | 377440 | 2023-06-05 | knocking / abnormal sound | 2023-01-14 | 2023-02-16 | 293 | null | cold storage | 1 | Cylinder no.2 delivery valve leakage | null | closed | Replaced delivery valve kit
2023-06-30 | Kalp Marketing | Gujrat | D | Fidelity Agro Pvt Ltd | Madhya Pradesh | KCX6 | 3394K1825 | 3833586704 | 2023-06-08 | 383358 | 2023-06-08 | abnormal noise & shaft seal leakage | 2021-07-28 | 2022-09-14 | 1256 | null | dairy / ice cream | 14 | Delivery valve leakage and step in delivery valve. (Site analysis missing) | null | closed | Replaced Liner, Piston ring set , Delivery valve & shaft seal kit
2023-06-30 | Parag Marketing Services | Pune | D | Graviss Food Pvt Ltd | Shirval | KCX102 | 3495K001 | 3859926735 | 2023-06-24 | 385992 | 2023-06-29 | pump air purging problem | 2021-11-30 | 2022-12-12 | 1345 | null | dairy / ice cream | 12 | System issue. Visited Mr. Omkar Mali dt.28.06.23 | null | closed | Replaced Oring & suction pipe
2023-06-30 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1922 | 3783766656 | 2023-05-24 | 378376 | 2023-05-23 | shaft seal leakage | 2021-12-27 | 2022-07-14 | 653 | null | food processing | 7 | Site analysis missing. | null | closed | Replaced shaft seal assembly.
2023-06-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Jay Chemical Industries | Gujrat | KCX9 | 3404K307 | 3821566750 | 2023-06-28 | 382156 | 2023-06-28 | low oil pressure | 2022-11-23 | 2023-06-28 | 5 | null | ice plant | 7 | Replaced thrust ring & OPRs | null | closed | Replaced thrust ring & OPRs
2023-06-30 | Kalp Marketing | Gujrat | D | Kshodwala Foods | Gujrat | KCX72 | 3474K540 | 3767746654 | 2023-05-23 | 376774 | 2023-05-16 | hp con rod be bearing wornout | 2022-03-27 | 2022-09-12 | 897 | null | meat/fish process | 6 | HP Connecting rod big end bush wornout. ( Site analysis missing) | null | closed | Replaced big end bushes 2 nos.
2023-06-30 | Kalp Marketing | Gujrat | D | Sun Exports | Gujrat | KCX72 | 3474K560 | 3784146667 | 2023-05-27 | 378414 | 2023-05-27 | oil carry over | 2022-07-27 | 2022-11-07 | 2887 | null | meat/fish process | 4 | Piston rings wornout & VLD Orings flat | null | closed | Replaced all piston rings & VLD Orings
2023-07-24 | S B Refrigeration | Bihar | D | Varun Beverage Limited | Bihar | KCX9 | 3404K199 | 3848606718 | 2023-06-16 | 384860 | 2023-06-16 | piston crack | 2021-08-20 | 2022-01-30 | 2325 | null | beverage / breweries | 5 | Replaced piston due to crack | null | closed | Piston1 no.
2023-07-24 | Multivista Global Pvt Ltd | Gurgaon | D | Svk Cool Chains Pvt Ltd | Haryana | KCX4 | 3384K3020 | 3665826747 | 2023-06-28 | 366582 | 2023-07-04 | delivery valve leakage | 2022-02-18 | 2022-05-30 | 1455 | null | cold storage | 3 | Delivery valve leakage ,replaced del valve assly | null | closed | Replaced del valve assly1
2023-07-24 | Hss Solution Pvt Ltd | Rajasthan | D | Sri Agrasen | Rajastan | KCX3 | 3374K2819 | 3743286706 | 2023-06-10 | 374328 | 2023-06-09 | oil carry over | 2022-03-09 | 2022-07-20 | 1057 | null | cold storage | 4 | Replaced cylinder liner and piston ring set,piston,gudgon pin | null | closed | Replaced cylinder liner and piston ring set,piston,gudgon pin
2023-07-24 | Multivista Global Pvt Ltd | Gurgaon | D | Sri Ramji Dairy | Uttar Pradesh | KCX2 | 3364K2327 | 3869366763 | 2023-07-03 | 386936 | 2023-07-02 | kcx oil pump tang broken | 2022-06-28 | 2022-10-10 | 1711 | null | dairy / ice cream | 4 | Replaced oil pump element | null | closed | Replaced oil pump element
2023-07-24 | S B Refrigeration | Bihar | D | Mithila Dairy | Bihar | KCX3 | 3374K2779 | 3860026766 | 2023-07-04 | 386002 | 2023-07-03 | shaft seal leakage | 2022-02-04 | 2022-06-01 | 2974 | null | dairy / ice cream | 3 | Site issue mentioned in FSR-Liquid ,dust entry found in compressor | null | closed | Replaced shaft seal assly
2023-07-24 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KCX4 | 3384K3129 | 3879746782 | 2023-07-13 | 387974 | 2023-07-14 | solenoid valve leakage | 2022-09-21 | 2022-12-31 | 385 | null | dairy / ice cream | 3 | solenoid valve leak from plunger body | null | closed | Replaced sol valve
2023-07-24 | Kalp Marketing | Gujrat | D | Shree Natraj Ice Factory | Gujrat | KCX4 | 3384K3293 | 3789506758 | 2023-07-01 | 378950 | 2023-05-27 | abnormal noisecylinder liner & piston ring set worn out | 2023-02-07 | 2023-04-25 | 9 | null | ice plant | 2 | Replaced cylinder liner and piston ring set | null | closed | Cylinder liner and piston ring set
2023-07-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Al-Falah Ice Factory | Kerala | KCX4 | 3384K2987 | 3837246717 | 2023-06-16 | 383724 | 2023-06-16 | cylinder overheatingdelivery valve leakage | 2022-01-22 | 2022-09-20 | 4752 | null | ice plant | 8 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-07-24 | Hss Solution Pvt Ltd | Rajasthan | D | Jai Girnari Agro | Rajastan | KCX2 | 3364K2170 | 3784786685 | 2023-06-02 | 378448 | 2023-06-02 | delivery valve leakage | 2021-07-31 | 2023-02-07 | 745 | null | ice plant | 19 | Replaced del valve assly | null | closed | Replaced del valve
2023-07-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Cool Land Ice Plant | Kerala | KCX2 | 3364K2358 | 3845706715 | 2023-06-15 | 384570 | 2023-06-15 | leak from panel boardtee threading damaged and leak | 2022-10-11 | 2022-12-26 | 68 | null | ice plant | 2 | Leakage Female run tee | null | closed | Female run tee
2023-07-24 | Trade Links | Secunderabad | D | Bsr Industries | Telangana | KCX3 | 3374K2993 | 3861326744 | 2023-06-26 | 386132 | 2023-06-26 | oil carry over | 2022-12-05 | 2022-12-16 | 2601 | null | ice plant | 1 | Replaced liner,buffer spring,ORV,Suction valve ring | null | closed | Replaced liner,buffer spring,ORV,Suction valve ring
2023-07-24 | Parag Marketing Services | Pune | D | Gadre Marine Export Pvt Ltd | null | KCX72 | 3474K604 | 3853766749 | 2023-06-28 | 385376 | 2023-06-20 | delivery valve leakage | 2022-12-28 | 2023-03-12 | 511 | null | meat/fish process | 3 | Delivery valve leakage ,replaced del valve assly | null | closed | Replaced del valve assly1
2023-07-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | A S Marine Ice Plant | Kerala | KCX42 | 3444K409 | 3661726745 | 2023-06-27 | 386172 | 2023-06-26 | kcx oil pump tang broken | 2023-04-29 | 2023-07-19 | 2 | null | meat/fish process | 3 | Replaced oil pump assly | null | closed | Replaced oil pump assly
2023-07-24 | Parag Marketing Services | Pune | D | Izhan Sea Food | Maharashtra | KCX42 | 3444K351 | 3859066734 | 2023-06-24 | 385906 | 2023-06-24 | krms issuerms devise malfunctioning | 2022-06-10 | 2023-02-16 | 2500 | null | meat/fish process | 8 | RMS device replaced | null | closed | RMS device replaced
2023-07-24 | Parag Marketing Services | Pune | D | Aqua Foods Exim | Maharashtra | KCX3 | 3374K2792 | 3858086731 | 2023-06-22 | 385808 | 2023-06-22 | krms issuerms devise malfunctioning | 2022-02-20 | 2023-02-19 | 543 | null | meat/fish process | 12 | RMS device replaced | null | closed | RMS device
2023-07-24 | Hss Solution Pvt Ltd | Rajasthan | D | Shri Tirupati Enterprises | Rajastan | KCX6 | 3394K2072 | 3769806645 | 2023-05-18 | 376980 | 2023-05-17 | pressure gauge outpointer below zero | 2022-10-21 | 2023-05-17 | 3 | null | others | 7 | Replaced pressure gauge | null | closed | Pressure gauge
2023-07-24 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KC72 | 347K1001 | email | 2023-07-18 | null | 2023-07-18 | hammer found in crankcase oil sump | 2023-01-29 | 2023-07-18 | 0 | null | chemical / pharma | 5 | null | null | closed | null
2023-07-31 | Kalp Marketing | Gujrat | D | Vrs Foods Ltd | Uttar Pradesh | KCX9 | 3404K283 | 3872826769 | 2023-07-04 | 387282 | 2023-07-04 | cylinder overheatingdelivery valve leakage | 2022-09-23 | 2022-11-03 | 3819 | null | dairy / ice cream | 2 | Replaced Del valve assly,Buffer spring,Piston ring set | null | closed | Replaced Del valve assly,Buffer spring,Piston ring set
2023-07-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K635 | 3884126816 | 2023-07-25 | 388412 | 2023-07-24 | krms panel issuedischarge tempararture sensor not working cable is broken | 2023-03-27 | 2023-06-21 | 405 | null | ice plant | 3 | Replaced Discharge temp sensor | null | closed | Replaced Discharge temp sensor
2023-08-23 | Cool Comfort Private Limited | West Bengal | D | Kholta Agro Cold Storage | West Bengal | KCX4 | 3384K3289 | 3890846827 | 2023-07-31 | 389084 | 2023-07-30 | cylinder overheating | 2023-02-04 | 2023-03-21 | 967 | null | cold storage | 1 | Delivery valve ring spring break. Site analysis missing | null | closed | Replaced DV Kit.
2023-08-23 | Parag Marketing Services | Pune | D | Ecofresh Cold Storage & Warehousing PvtLtd | Pune | KCX2 | 3364K2487 | 3895066829 | 2023-08-01 | 389506 | 2023-08-03 | oil separator welding leakage | 2023-07-07 | 2023-08-03 | 35 | null | cold storage | 1 | OS welding leakage at bottom run. | null | closed | Replaced OS type40
2023-08-23 | Kalp Marketing | Gujrat | D | Eskimo Agrifresh Cold Storage Pvt Ltd | Gujrat | KCX42 | 3444K417 | 3920066853 | 2023-08-08 | 392006 | 2023-08-05 | pressure gauge glycerin leak | 2023-07-22 | 2023-08-05 | 1 | null | cold storage | 1 | Pressure gauge glycerin leaked. | null | closed | Relaced 16 kg/cm2 Pr.gauge
2023-08-23 | Kalp Marketing | Gujrat | D | Eskimo Agrifresh Cold Storage Pvt Ltd | Gujrat | KCX3 | 3374K3193 | 3913526852 | 2023-08-08 | 391352 | 2023-08-02 | solenoid valve coil not working | 2023-07-22 | 2023-08-03 | 4 | null | cold storage | 1 | Coil not working & female run tee thrd damaged. | null | closed | Replaced solenoid valve coil 1 & Female run tee1
2023-08-23 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Andhra Pradesh | KCX4 | 3384K3182 | 3885886819 | 2023-07-27 | 388588 | 2023-07-26 | oil carry over | 2022-11-23 | 2023-01-03 | 2787 | null | dairy / ice cream | 2 | Cyl no.3 DV Leakage replaced, Oil carryover under monitoring. | null | closed | Replaced DV Assly
2023-08-23 | Parag Marketing Services | Pune | D | Krishana Dairy | Ahmed Nagar | KCX2 | 3364K2431 | 3887586851 | 2023-08-08 | 388758 | 2023-07-27 | oil pressure problem | 2023-02-19 | 2023-07-06 | 233 | null | dairy / ice cream | 5 | Oil pressure not develop due to tang broken. | null | closed | Replaced pump element
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX3 | 3374K2943 | 3915746842 | 2023-08-05 | 391574 | 2023-08-09 | cylinder overheating | 2022-11-02 | 2022-12-11 | 1958 | null | food processing | 1 | Direct cyl no.3 overheated , seized. | null | closed | Replaced DV, Piston , rings , liner & buffer spring.
2023-08-23 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1924 | 3865666775 | 2023-07-07 | 386566 | 2023-06-06 | cylinder overheating, del valve ring spring broken | 2021-12-27 | 2022-07-14 | 2322 | null | food processing | 8 | Replaced piston,liner,del valve | null | closed | Replaced piston,liner,del valve
2023-08-23 | Kalp Marketing | Gujrat | D | Harshey India Pvt Ltd | Madhya Pradesh | KCX6 | 3394K2097 | 3884066832 | 2023-08-01 | 388406 | 2023-07-29 | delivery valve leakage | 2022-11-29 | 2023-07-28 | 0 | null | food processing | 8 | Cyl no. 1 & 6 delivery valve leakage . Overheating problem. | null | closed | Replaced delivery valve assembly 2 nos.
2023-08-23 | Pragya Industrial Supply | Karnataka | D | Tropical Mushrooms Pvt Ltd | Karnataka | KCX42 | 3444K410 | 3880246802 | 2023-07-17 | 388024 | 2023-07-17 | k5 valve leakage | 2023-05-24 | 2023-07-14 | 1 | null | food processing | 1 | K5 Valve leakage | null | closed | Replaced K5 Valve assly
2023-08-23 | Pragya Industrial Supply | Karnataka | D | Infra Fine Products | Karnataka | KCX42 | 3444K402 | 3865886834 | 2023-08-02 | 386588 | 2023-08-02 | kcx low oil pressure problemhigh intermidiate pressure & liquid entry | 2023-03-29 | 2023-06-23 | 6 | null | food processing | 3 | Replaced bearings,piston ring set,delivery valve. | null | closed | Bearings,piston ring,del valve
2023-08-23 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1923 | 3845646774 | 2023-07-07 | 384564 | 2023-07-06 | knocking / abnormal sound | 2021-12-27 | 2022-07-14 | 2006 | null | food processing | 7 | Cyl.3 DV Ring spring broken and cylinder sesized. | null | closed | Replaced liner, piston , piston ring set , DV Kit & assly
2023-08-23 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1923 | 3950966890 | 2023-08-29 | 395096 | 2023-08-26 | oil carry over | 2021-12-27 | 2022-07-14 | 2675 | null | food processing | 8 | Replaced piston,piston ring set,connecting rod assly & gudgeon pin | null | closed | Replaced piston,piston ring set,connecting rod assly & gudgeon pin
2023-08-23 | Kalp Marketing | Gujrat | D | Jagdish Agri Exporters Pvt Ltd | Madhya Pradesh | KCX72 | 3474K586 | 3936146866 | 2023-08-18 | 393614 | 2023-08-18 | oil pressure not buildup | 2022-10-22 | 2023-01-18 | 723 | null | food processing | 3 | Air purging problem | null | closed | Replaced pump assly
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Foods And Inns Ltd | Gujrat | KCX72 | 3474K520 | 3759466868 | 2023-08-18 | 375946 | 2023-06-17 | stop valve not working | 2022-02-11 | 2023-06-17 | 22 | null | food processing | 4 | Suction stop valve Tal 100 Not working- Handle wheel running around there. | null | closed | Replaced stop valve Tal 100
2023-08-23 | Geekay Pneumatic Pvt Ltd | Kerala | D | Bharath Seafoods | Kerala | KCX2 | 3364K2317 | 3927546861 | 2023-08-11 | 392754 | 2023-08-11 | cylinder overheating | 2022-05-28 | 2023-04-26 | 310 | null | ice plant | 10 | Cyl.1 discharge stroke limitor wornout. | null | closed | Replaaced delivery valve assembly
2023-08-23 | Trade Links | Secunderabad | D | J H Ice Factory | Andhra Pradesh | KCX3 | 3374K3180 | 3917446846 | 2023-08-07 | 391744 | 2023-08-07 | low oil pressure | 2023-07-08 | 2023-07-14 | 406 | null | ice plant | 1 | Drive shaft tang broken - Replaced pump element. | null | closed | Replaced pump element
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Ambernath Org Pvt Ltd | Thane | KC3 | 337K4827 | 3861426754 | 2023-06-29 | 386142 | 2023-06-27 | oil carry over | 2022-03-25 | 2022-09-26 | 1535 | null | ice plant | 6 | All 3 cylinders piston ring sets wornout. | null | closed | Replaced piston ring sets
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Vidhi Specialty Food Ltd | Gujrat | KCX6 | 3394K2056 | 3890886826 | 2023-07-27 | 389088 | 2023-07-29 | oil pump tang broken | 2022-10-10 | 2023-07-27 | 5 | null | ice plant | 9 | Oil pressure not develop due to tang broken. | null | closed | Replaced pump assly
2023-08-23 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kozhikode Fishing | Kerala | KCX4 | 3384K3056 | 3905186840 | 2023-08-05 | 390518 | 2023-08-05 | pressure switch mp55a malfuctioning | 2022-03-29 | 2023-08-05 | 20 | null | ice plant | 5 | OP Pressure switch frequently tripping problem. | null | closed | Replaced OP Switch
2023-08-23 | Trade Links | Secunderabad | D | Akshay Food Impex | Andhra Pradesh | KCX6 | 3394K2247 | 3872786780 | 2023-07-11 | 387278 | 2023-07-11 | shaft key loose | 2023-06-21 | 2023-07-11 | 68 | null | ice plant | 1 | Sfat key free. Site analysis missing | null | closed | Replaced key
2023-08-23 | Cool Comfort Private Limited | West Bengal | D | Z A Sea Foods Pvt Ltd | null | KCX4 | 3384K3083 | 3931406862 | 2023-08-14 | 393140 | 2023-08-16 | shaft seal leakage | 2022-06-03 | 2022-08-11 | 1810 | null | ice plant | 2 | Rotary seal crack & leakage. | null | closed | Replaced shaft seal assembly.
2023-08-23 | Cool Comfort Private Limited | West Bengal | D | K N C Agro Products | West Bengal | KCX6 | 3394K1965 | 3927386859 | 2023-08-10 | 392738 | 2023-08-17 | knocking / abnormal sound | 2022-02-28 | 2023-02-13 | 2802 | null | meat/fish process | 11 | Cylinder seized. Delivery ring spring broken. Piston , piston rings damaged. | null | closed | Replaced DV kit, Piston , Piston ring set, Bush , Gudgeon pin.
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Organic Industries Pvt Ltd | Gujrat | KCX12 | 3415K058 | 3755706751 | 2023-06-28 | 375570 | 2023-05-25 | cylinder overheating | 2023-01-31 | 2023-02-22 | 1590 | null | others | 1 | Direct cylinder DV leak. | null | closed | Replaced DV assly
2023-08-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Oneiro Chemicals Pvt Ltd | Gujrat | KCX93 | 3485K134 | 3885346823 | 2023-07-27 | 388534 | 2023-07-27 | delivery valve leakage | 2022-06-25 | 2022-10-15 | 4440 | null | chemical / pharma | 4 | HP Cyl.1 delivery valve ring spring broken. | null | closed | Replaced DV assly
2023-09-18 | Hss Solution Pvt Ltd | Rajasthan | D | Mount Shivalik Brewries/Trinetra Beverage Pvt Ltd | Rajastan | KCX9 | 3404K244 | 3981726943 | 2023-09-11 | 398172 | 2023-09-09 | oil separator welding leakage | 2022-01-31 | 2022-09-08 | 741 | null | beverage / breweries | 8 | High vibrations at discharge line. OS welding leakage at flange welding run. | null | closed | Replaced oil separator Type D80
2023-09-18 | Cool Comfort Private Limited | West Bengal | D | Matri Bhumi Agritech LLP | West Bengal | KCX4 | 3384K3013 | 3942986874 | 2023-08-21 | 394298 | 2023-08-21 | coupling diskpack crack | 2022-02-12 | 2022-03-12 | 2533 | null | cold storage | 1 | Site observations missing in FSR | null | closed | Replaced disk pack assly
2023-09-18 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KCX6 | 3394K2281 | 3971366903 | 2023-08-31 | 397136 | 2023-09-07 | oil pressure problem | 2023-08-18 | 2023-08-28 | 5 | null | dairy / ice cream | 1 | Oil pump tang broken | null | closed | Replaced pump assembly
2023-09-18 | Multivista Global Pvt Ltd | Gurgaon | D | Govind Dairy | Uttar Pradesh | KC4 | 338K5791 | 3954946889 | 2023-08-25 | 395494 | 2023-08-26 | oil pressure problem | 2022-11-19 | 2023-03-24 | 1026 | null | dairy / ice cream | 4 | Oil pressure drop due to housing damage. | null | closed | Replaced pump assembly
2023-09-18 | Parag Marketing Services | Pune | D | Kolhapur Zila Sahakari Dudh Utpadak Sangh | Kolhapur | KCX6 | 3394K1926 | 3703586577 | 2023-04-14 | 370358 | 2023-04-14 | solenoid valve coil not working | 2022-01-10 | 2022-10-17 | 881 | null | dairy / ice cream | 10 | Due to overheat 2 times coil burnt so valve body replaced and problem solved. | null | closed | Replaced solenoid valve (NC)1
2023-09-18 | Trade Links | Secunderabad | D | J H Ice Factory | Andhra Pradesh | KCX3 | 3374K3180 | 3937026872 | 2023-08-21 | 393702 | 2023-08-19 | kcx oil pump purging | 2023-07-08 | 2023-07-14 | 623 | null | ice plant | 1 | Pump replaced due to purging | null | closed | Replaced KCX oil pump assly
2023-09-18 | Multivista Global Pvt Ltd | Tamil Nadu | D | Theva & Co | null | KCX72 | 3474K567 | 3936226871 | 2023-08-21 | 393622 | 2023-08-18 | pressure gauge out | 2022-09-26 | 2023-08-18 | 10 | null | meat/fish process | 11 | 16 KG/CM2 Pressure gauge out. Minus error. | null | closed | Replaced pressure gauge
2023-09-30 | Model Pneumatic Co | Punjab | D | Sophina Orchid Fresh | J&K | KCX4 | 3384K3053 | 3984706955 | 2023-09-13 | 398470 | 2023-09-13 | shaft seal leakage | 2022-03-29 | 2022-09-21 | 978 | null | cold storage | 6 | Shaft seal leakage. Photos attchments missing. | null | closed | Replaced shaft seal assly
2023-09-30 | Trade Links | Secunderabad | D | Dodla Dairy Ltd | Andhra Pradesh | KCX2 | 3364K2406 | 3960926895 | 2023-08-29 | 396092 | 2023-08-29 | oil carry over | 2022-12-30 | 2023-07-22 | 313 | null | dairy / ice cream | 7 | Cyl. No. 1 Delivery valve leakage | null | closed | Replaced delivery valve assembly 1 nos.
2023-09-30 | Multivista Global Pvt Ltd | Gurgaon | D | Sunrise Victuals Pvt Ltd | Haryana | KCX63 | 3464K137 | 3977406949 | 2023-09-12 | 397740 | 2023-09-16 | abnormal noise | 2021-09-29 | 2023-01-15 | 2782 | null | food processing | 15 | Delivery valve ring broken. Improper site analysis , seems system dirt on piston top. | null | closed | Replaced piston , suction ring/spring & delivery valve assly.
2023-09-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Asvini Fisheries Pvt Ltd | Tamil Nadu | KCX72 | 3474K626 | 3973386921 | 2023-09-04 | 397338 | 2023-09-02 | cylinder overheating | 2023-03-06 | 2023-04-20 | 2234 | null | food processing | 1 | Delivery valve ring spring broken. | null | closed | Replaced delivery valve , buffer spring , piston and piston ring set.
2023-09-30 | Multivista Global Pvt Ltd | Gurgaon | D | Sunrise Victuals Pvt Ltd | Haryana | KCX63 | 3464K135 | 4003046966 | 2023-09-18 | 400304 | 2023-09-27 | oil carry over | 2021-09-29 | 2023-01-15 | 2369 | null | food processing | 15 | HP Cyl1 found piston crack - 1 no. | null | closed | Replaced piston
2023-09-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Zara Industries | Kerala | KCX4 | 3384K3339 | 3984586954 | 2023-09-13 | 398458 | 2023-09-12 | cylinder overheating | 2023-03-29 | 2023-08-17 | 214 | null | ice plant | 5 | Delivery valve leak, stroke limitor wornout. | null | closed | Replaced DV assly
2023-09-30 | Parag Marketing Services | Pune | D | Sairam Milk & Milk Products | Sangli | KCX2 | 3364K2288 | 3820106850 | 2023-08-08 | 382010 | 2023-07-22 | oil carry over | 2022-03-18 | 2023-02-20 | 2099 | null | ice plant | 14 | Oil throw from cyl.2 , Liner cut marks observed. | null | closed | Replaced liner , piston , piston ring set.
2023-09-30 | Cool Comfort Private Limited | West Bengal | D | Larsen And Toubro Limited | Assam | KCX63 | 3464K168 | 3989306974 | 2023-09-23 | 398930 | 2023-09-23 | oil pump tang broken | 2023-02-28 | 2023-09-23 | 0 | null | ice plant | 7 | Oil pressure not develop after 30 min running. | null | closed | Replaced pump element
2023-09-30 | Kirloskar South East Asia Co Ltd | Thailand | E | Thai Union | Thailand | KCX63 | Sr.No. & details awaited from IBD | email | 2023-09-25 | null | 2023-09-25 | k5 valve leakage | null | null | 0 | null | null | null | null | null | null | null
2023-09-30 | Kirloskar South East Asia Co Ltd | Thailand | E | Thai Union | Thailand | KCX12 | Sr.No. & details awaited from IBD | email | 2023-09-25 | null | 2023-09-25 | stop valve leakage | null | null | 0 | null | null | null | null | null | null | null
2023-10-18 | Multivista Global Pvt Ltd | Tamil Nadu | D | Nila Sea Foods | Tamil Nadu | KCX3 | 3374K2844 | 3955906897 | 2023-08-30 | 3955590 | 2023-08-27 | rms device malfuctioning | 2022-03-29 | 2022-12-18 | WC | null | beverage / breweries | 9 | RMS Device malfuctioning | null | closed | Replaced RMS device
2023-10-18 | Multivista Global Pvt Ltd | Gurgaon | D | Welga Foods Ltd | Uttar Pradesh | KCX3 | 3374K3032 | 3979146957 | 2023-09-13 | 397914 | 2023-09-13 | safety valve leakage | 2022-12-29 | 2023-03-07 | 6 | null | cold storage | 3 | Safety valve leak . | null | closed | Replaced sefty valve teflon.
2023-10-18 | Cool Comfort Private Limited | West Bengal | D | PPSingh Ice Plant | West Bengal | PCX2 | 3106K0160 | 4045767005 | 2023-10-03 | 404576 | 2023-10-03 | abnormal noise | 2022-04-29 | 2023-03-20 | 1889 | null | ice plant | 11 | Damaged piston,Liner,piston ring sets , Gudgeon pin & bearings . | null | closed | Replaced piston,Liner,piston ring sets , Gudgeon pin & bearings 2 nos each.
2023-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | Bharath Seafoods | Kerala | KCX4 | 3364K2317 | 4021046980 | 2023-09-26 | 402104 | 2023-09-24 | abnormal noisedelivery valve leak | 2022-05-28 | 2023-04-26 | 1157 | null | ice plant | 11 | One delivery valve leak. | null | closed | Replaced Delivery valve
2023-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | M M Ice Industries | Anand (Gj) | KCX4 | 3384K3305 | email | 2023-10-07 | null | 2023-10-07 | crankcase shell crack | 2023-02-17 | 2023-02-17 | 1200 | null | ice plant | 1 | Shell crack near foot no. 1 crack | null | closed | Compressor foot rectified at KPCL.
2023-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Patneshwar Ice Factory | Raigad | KCX2 | 3364K2373 | 3975806963 | 2023-09-15 | 397580 | 2023-10-02 | high oil carry over | 2022-11-22 | 2022-11-24 | 5056 | null | ice plant | 1 | Oil throw from both cylinders , Liner , piston , piston ring set and gudgeon pins wornout. | null | closed | Replaced Liner , piston , piston ring set and gudgeon pins wornout.
2023-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kalathilparambil Enterprises | Kerala | KCX4 | 3384K3269 | 3972206906 | 2023-09-02 | 397220 | 2023-09-01 | high oil carry over | 2023-01-24 | 2023-05-06 | 1326 | null | ice plant | 5 | Piston rings wornout. | null | closed | 2 nos piston ring sets replaced
2023-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K635 | email | 2023-10-07 | null | 2023-10-07 | hp discharge pipe welding crack | 2023-03-27 | 2023-06-21 | 1988 | null | ice plant | 3 | Welding crack at HP discharge pipe joint. | null | closed | Compressor replaced
2023-10-18 | Geekay Pneumatic Pvt Ltd | Kerala | D | Annmary Ice Plant | Kerala | KCX4 | 3384K3390 | 4019146975 | 2023-09-25 | 401914 | 2023-09-23 | over heating | 2023-07-24 | 2023-08-24 | 494 | null | ice plant | 1 | One delivery valve leak & high vibrations to the compressor. | null | closed | Replaced Delivery valve
2023-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K661 | email | 2023-10-13 | null | 2023-10-13 | paint blistering on discharge pipe bend | 2023-06-27 | 2023-10-03 | 8 | null | ice plant | 4 | Blistering patch on discharge pipe bend. Surface defect , base layer is ok. | null | open | To be rectified at site
2023-10-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Castelrock Fisheries Pvt Ltd | Taloja, Mh | KCX3 | KCX3AV7550001 | 3971026937 | 2023-09-08 | 397102 | 2023-09-01 | discharge temp sensor burnt. | 2023-03-27 | 2023-08-16 | 272 | null | meat/fish process | 5 | Depth of thermowell is more than length of sensor & nut is touching to wire causing burnt. | null | closed | Replaced Sensor
2023-10-30 | Cool Comfort Private Limited | West Bengal | D | Sunit Breweries | Assam | KCX9 | 3404K259 | 4046667010 | 2023-10-05 | 404666 | 2023-10-05 | vbelt loose | 2023-03-28 | 2023-08-29 | 985 | null | beverage / breweries | 5 | Replaced V belt | null | closed | Replaced V belt
2023-10-30 | Pragya Industrial Supply | Karnataka | D | Shree Marala Cold Storage | Karnataka | KCX3 | 3374K3081 | 4021166983 | 2023-09-27 | 402116 | 2023-09-27 | abnormal noisecylinder liner & piston ring set worn out | 2023-01-29 | 2023-04-01 | 600 | null | cold storage | 3 | Replaced Cylinder liner & piston ring set | null | closed | Replaced Cylinder liner & piston ring set
2023-10-30 | Pragya Industrial Supply | Karnataka | D | Shree Marala Cold Storage | Karnataka | KCX3 | 3374K3081 | 4021166983 | 2023-09-27 | 402116 | 2023-09-27 | abnormal noisedelivery valve leak | 2023-01-29 | 2023-04-01 | 600 | null | cold storage | 2 | Replaced del.valve,liner,piston ring set,bearing bush | null | closed | Replaced del.valve,liner,piston ring set,bearing bush
2023-10-30 | Kalp Marketing | Gujrat | D | Mehsana District Co Op Producers Union Ltd | Gujrat | KCX4 | 3384K34303 | 3989187037 | 2023-10-16 | 398918 | 2023-09-28 | k5 valve thread damaged | 2023-08-11 | 2023-09-28 | 18 | null | dairy / ice cream | 1 | Replaced K5 valve | null | closed | Replaced K5 valve
2023-10-30 | Pragya Industrial Supply | Karnataka | D | Bharath Dairy Agro | Karnataka | PCX2 | 3106K0237 | 4065387071 | 2023-10-28 | 406538 | 2023-10-28 | oil carryoverpiston ring set worn out | 2023-07-20 | 2023-08-19 | 840 | null | dairy / ice cream | 1 | Replaced piston ring set-4nos | null | closed | Replaced piston ring set4nos
2023-10-30 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KCX6 | 3394K2281 | 4019047032 | 2023-10-14 | 401904 | 2023-10-14 | oil liftingcylinder liner & piston ring set wornout | 2023-08-18 | 2023-08-28 | 345 | null | dairy / ice cream | 1 | Replaced Cylinder liner & piston ring set | null | closed | Replaced Cylinder liner & piston ring set
2023-10-30 | Multivista Global Pvt Ltd | Chennai | D | Flex Foods Ltd | Tamil Nadu | KCX9 | 3404K315 | 3936026958 | 2023-09-14 | 393602 | 2023-09-14 | shaft seal leakage | 2023-12-31 | 2023-03-24 | 850 | null | food processing | 3 | Replaced shaft seal assly & Thrust ring | null | closed | Replaced shaft seal assly & Thrust ring
2023-10-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Rahamat Ice Palnt | Kerala | KCX3 | 3374K3157 | 3931506884 | 2023-08-24 | 393150 | 2023-08-24 | oil carryoverdelivery valve leak | 2023-05-12 | 2023-06-13 | 750 | null | ice plant | 1 | Delivery valve leak due to step observed on del stroke limiter | null | closed | Replaced Del valve assly
2023-10-30 | Trade Links | Secunderabad | D | Sony Ice Factory | Andhra Pradesh | KCX6 | 3394K2004 | 3947146887 | 2023-08-25 | 394714 | 2023-08-24 | oil liftingcylinder liner & piston ring set wornout | 2022-05-17 | 2022-09-09 | 4828 | null | ice plant | 4 | Replaced Cylinder liner & piston ring set | null | closed | Replaced cylinder liner & piston ring set
2023-10-30 | Kalp Marketing | Gujrat | D | Shafi Marine | Gujrat | KCX72 | 3474K563 | 4046267003 | 2023-10-03 | 404626 | 2023-10-03 | kcx oil pressure not developingopr malfunctioning | 2022-07-29 | 2023-05-26 | 180 | null | meat/fish process | 10 | Replaced both OPR | null | closed | Replaced LP & HP regulator
2023-10-30 | Trade Links | Secunderabad | null | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 4057767051 | 2023-10-20 | 405776 | 2023-10-19 | abnormal noisepiston crack | 2022-09-20 | 2022-11-22 | 3430 | null | chemical / pharma | 3 | Piston crack & shaft seal leak | null | closed | Replaced piston2,piston ring set2,Shaft seal assly1
2023-11-16 | Parag Marketing Services | Pune | D | Shrinivasa Milk & Milk Products | Sangli | KCX3 | 3374K3110 | 4088507079 | 2023-11-08 | 408850 | 2023-11-08 | oil separator leakage | 2023-02-21 | 2023-06-27 | 788 | null | dairy / ice cream | 4 | Oil separator leakage from welding pin hole at inlet connection. | null | closed | Replaced Demister OS 50
2023-11-16 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX72 | 3474K648 | 4019467041 | 2023-10-17 | 401946 | 2023-10-15 | krms pressure sensor cable not working | 2023-06-10 | 2023-10-15 | 5 | null | meat/fish process | 4 | Pressure sensor cable not working. Cross verified by interchanging with another cable and noticed that working properly. | null | closed | Replaced pressure sensor cable with connector,12MTR Length, Makecarel, codeSPKC00A310.
2023-11-30 | S B Refrigeration | Bihar | D | Mithila Dairy | Bihar | KCX3 | 3374K3203 | 4117567123 | 2023-11-23 | 411756 | 2023-11-26 | extended female adaptor damaged in transportation | 2023-08-02 | 2023-11-26 | 0 | null | dairy / ice cream | 3 | Compressor tubing damaged in transportation | null | closed | Replaced Extended female adaptor,union nut & Ferule
2023-11-30 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX51 | 3454K210 | 4057287029 | 2023-10-12 | 405728 | 2023-10-12 | discharge temparature sensor malfunctioning | 2022-10-31 | 2022-12-11 | 1368 | null | food processing | 2 | Discharge temparature sensor malfunctioning | null | closed | Discharge temparature sensor
2023-11-30 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1924 | 4055047061 | 2023-10-25 | 406504 | 2023-10-23 | discharge valve leakage | 2021-12-27 | 2022-07-14 | 3251 | null | food processing | 7 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-11-30 | Parag Marketing Services | Pune | D | Tirupati Balaji Agro Products Pvt Ltd | Baramati | KCX6 | 3394K1921 | 4065027060 | 2023-10-25 | 406502 | 2023-10-23 | discharge valve leakage | 2021-12-27 | 2022-07-13 | 3312 | null | food processing | 7 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-11-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises | Panvel | KCX3 | 3374K3170 | 3970986938 | 2023-09-08 | 397098 | 2023-09-02 | discharge valve leakage | 2023-06-16 | 2023-08-14 | 50 | null | food processing | 2 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-11-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX72 | 3474K585 | 4066387055 | 2023-10-21 | 406638 | 2023-11-24 | krms discharge temparature sensor malfunctioning | 2022-11-02 | 2022-12-11 | 1500 | null | food processing | 1 | Replaced discharge temparature sensor | null | closed | Replaced discharge temparature sensor
2023-11-30 | Parag Marketing Services | Pune | D | Indiaqo Foods Pvt Ltd | Maharashtra | KCX72 | 3474K593 | 4074087098 | 2023-11-08 | 407408 | 2023-10-27 | shaft seal leakage | 2022-11-28 | 2023-08-25 | 164 | null | food processing | 9 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2023-11-30 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kahnjagad Ice Plant | Kerala | KCX2 | 3364K2427 | 4048287014 | 2023-10-08 | 404828 | 2023-10-06 | discharge valve leakage | 2023-02-17 | 2023-06-15 | 1362 | null | ice plant | 4 | Replaced del.valve assly | null | closed | Replaced del.valve assly
2023-11-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Newvalenkani Enterprises | Thane | KCX4 | 3384K3249 | 4030987000 | 2023-10-02 | 403098 | 2023-09-26 | shaft seal leakage | 2023-01-10 | 2023-04-13 | 2168 | null | ice plant | 8 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2023-11-30 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX51 | 3454K223 | 4019447042 | 2023-10-17 | 401944 | 2023-10-15 | krmspressure transducer short supply | 2023-06-27 | 2023-10-15 | 3 | null | meat/fish process | 4 | Short supply | null | closed | Short supply
2023-11-30 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Nanak Nutrition | Raigad | KCX72 | 3474K637 | 4019067004 | 2023-10-03 | 401906 | 2023-10-03 | shaft seal leakage | 2023-03-30 | 2023-06-07 | 860 | null | meat/fish process | 2 | Replaced shaft seal assly | null | closed | Shaft seal assly
2023-12-18 | Hss Solution Pvt Ltd | Rajasthan | D | Suvidha Cold Storage | Rajastan | KCX2 | 3364K2510 | 4073147095 | 2023-11-08 | 407314 | 2023-11-08 | discharge stop valve threading damaged | 2023-08-18 | 2023-09-01 | 0 | null | cold storage | 1 | Replaced Stop valve TAL 50 | null | closed | Replaced Stop valve TAL 50
2023-12-18 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KCX6 | 3394K2281 | 4131567151 | 2023-12-02 | 413156 | 2023-12-02 | oil carryoverknocking sound | 2023-08-18 | 2023-08-28 | 50 | null | dairy / ice cream | 1 | Replaced cylinder liner,piston,piston ring set,conrod-2 & thrust ring | null | closed | Replaced cylinder liner,piston,piston ring set,conrod2 & thrust ring
2023-12-18 | Pragya Industrial Supply | Karnataka | D | Manasa Ice Plant | Karnataka | KCX6 | 3394K2024 | 4062187076 | 2023-10-31 | 406218 | 2023-10-20 | high oil consumption | 2022-09-07 | 2022-10-20 | 3475 | null | ice plant | 1 | Replaced piston ring set,cylinder liner,shaft seal assly | null | closed | Replaced piston ring set,cylinder liner,shaft seal assly
2023-12-18 | Trade Links | Goa | D | Mandovi Fisherman | Goa | KCX3 | 3374K3184 | 4184847157 | 2023-12-04 | 418484 | 2023-12-04 | oil carry over | 2023-07-13 | 2023-08-12 | 864 | null | ice plant | 1 | Replaced Cylinder liner,piston ring set,conrod assly-3 | null | closed | Replaced Cylinder liner,piston ring set,conrod assly3
2023-12-18 | Trade Links | Goa | D | Mandovi Fisherman | Goa | KCX3 | 3374K3184 | 4059407062 | 2023-10-26 | 405940 | 2023-10-20 | oil carry over | 2023-07-13 | 2023-08-12 | 864 | null | ice plant | 1 | Replaced cylinder liner & piston ring set,ORV | null | closed | Replaced cylinder liner & piston ring set,ORV
2023-12-18 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX31 | 3434K0218 | 4169767132 | 2023-11-25 | 416976 | 2023-11-25 | krms issue | 2023-06-27 | 2023-10-15 | 65 | null | meat/fish process | 4 | Replaced Controller / 7'' HMI Display screen | null | closed | Replaced Controller / 7'' HMI Display screen
2023-12-21 | Kalp Marketing | Gujrat | D | Innovative Agrotech | Gujrat | KCX72 | 3474K694 | 4186607165 | 2023-12-07 | 418660 | 2023-12-06 | delivery valve leakage | 2023-09-26 | 2023-12-06 | 4 | null | food processing | 3 | Replaced del valve assly | null | closed | Del valve assly
2023-12-21 | Parag Marketing Services | null | D | Harbour Arabian Exports | Ratnagiri | KCX51 | 3454K200 | 3935526929 | 2023-09-07 | 393552 | 2023-09-06 | delivery valve leakge | 2022-03-28 | 2022-10-11 | 1024 | null | meat/fish process | 7 | Replaced del valve assly | null | closed | Replaced del valve assly
2023-12-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Ic Abf Special Foods Pvt Ltd | Kerala | KCX72 | 3474K685 | 4085327099 | 2023-11-09 | 408532 | 2023-11-08 | kcx oil pump pressure not stable | 2023-08-22 | 2023-11-08 | 18 | null | meat/fish process | 3 | Replaced oil pump assly KCX | null | closed | Replaced oil pump assly KCX
2023-12-21 | Geekay Pneumatic Pvt Ltd | Kerala | D | Abm Marine Products | Kerala | KCX51 | 3454K218 | 4091347104 | 2023-11-14 | 409134 | 2023-11-11 | pressure gauge glycerin leak & gauge out | 2023-04-17 | 2023-11-11 | 16 | null | meat/fish process | 7 | Replaced pressure gauge -760 to 16 kg/cm2 | null | closed | Replaced pressure gauge 760 to 16 kg/cm2
2023-12-21 | Pragya Industrial Supply | Karnataka | D | Synnova Intermidiates Pvt Ltd | Karnataka | KC4 | 338K5844 | 4283007201 | 2023-12-23 | 428300 | 2023-12-24 | kc suction filter housing leak | 2023-04-27 | 2023-12-24 | 4 | null | chemical / pharma | 8 | Replaced filter housing assly KC | null | closed | KC Suction filter assly
2023-12-21 | Kirloskar South East Asia Co Ltd | Thailand | E | Thai Union | Thailand | KCX12 | 3415K0055 | email | 2023-12-20 | null | 2023-12-20 | kcx low oil pressure problem | 2022-04-10 | 2023-12-21 | 0 | null | null | null | Grub screw fouling in oil path | null | closed | Grub screw fouling in oil path
2023-12-30 | Kalp Marketing | Gujrat | D | Shreenath Cold Depalpur | Madhya Pradesh | KCX3 | 3374K3265 | email | 2023-12-28 | null | 2023-12-28 | discharge flange bend | 2023-10-26 | 2023-12-28 | 0 | null | cold storage | 2 | End flange connector fitted | null | closed | End flange connector fitted
2024-01-15 | Parag Marketing Services | null | D | Srinivasa Milk & Milk Products | Sangli | KCX3 | 3374K3109 | 40990587194 | 2023-12-20 | 409058 | 2023-12-09 | high oil consumption | 2023-02-21 | 2023-06-27 | 1724 | null | dairy / ice cream | 4 | Replaced cylinder liner,piston,piston ring set | null | closed | Cylinder liner1,piston1,Piston ring sets3
2024-01-15 | Parag Marketing Services | null | D | Jai Janardhan Shitkaran Dudh Kendra | Nashik | KCX2 | 3364K2408 | 4180507192 | 2023-12-20 | 418050 | 2023-11-30 | pressure gauge malfunctioning | 2023-01-09 | 2023-02-04 | 2831 | null | dairy / ice cream | 1 | Pressure gauge 0 to 10 kg/cm2 internally leak | null | closed | Pressure gauge 0 to 16 kg/cm2
2024-01-15 | Parag Marketing Services | null | D | Nestle India Ltd | Gujrat | KCX6 | 3394K2228 | email | 2024-01-15 | null | 2024-01-15 | asme oil separator 80 demister float valve position wrong | 2023-08-17 | 2023-12-22 | 0 | null | food processing | 4 | Flaot valve position corrected | null | closed | null
2024-01-15 | Kalp Marketing | Gujrat | D | Jagdish Agri Exporters Pvt Ltd | Madhya Pradesh | KCX72 | 3474K586 | 4304707238 | 2024-01-06 | 430470 | 2024-01-05 | piston overheatingdel valve leak | 2022-10-22 | 2023-01-18 | 802 | null | food processing | 3 | Replaced del valve assly,HP piston,cylinder liner,buffer spring,needle roller bearing | null | closed | Replaced del valve assly,HP piston,cylinder liner,buffer spring,needle roller bearing
2024-01-15 | Parag Marketing Services | null | D | Sairam Milk & Milk Products | Sangli | KCX2 | 3364K2288 | 4041146998 | 2023-09-30 | 404114 | 2023-09-29 | cylinder overheatingdelivery valve leakage | 2022-03-16 | 2023-02-20 | 3018 | null | ice plant | 11 | Replaced del valve assly | null | closed | Del valve assly
2024-01-15 | Geekay Pneumatic Pvt Ltd | Kerala | D | Rahamat Ice Palnt | Kerala | KCX3 | 3374K3157 | 4274927188 | 2023-12-19 | 427992 | 2023-12-18 | high oil carryoverdelivery valve leakage | 2023-05-12 | 2023-06-13 | 3334 | null | ice plant | 1 | Replaced del valve assly | null | closed | Del valve assly
2024-01-15 | Trade Links | Secunderabad | D | Ananada Enterprises | Andhra Pradesh | KCX72 | 3474K590 | 4298407221 | 2023-12-29 | 429840 | 2023-12-28 | abnormal noisedelivery valve leak | 2022-11-23 | 2022-12-20 | 4314 | null | meat/fish process | 1 | Replaced Delivery valve assly | null | closed | Del valve assly
2024-01-15 | Kalp Marketing | Gujrat | D | Shree Niddhi ExportsPorbandar | Gujrat | KCX51 | 3485K224 | 4178407148 | 2023-12-01 | 417840 | 2023-12-01 | cylinder overheatingdelivery valve leakage | 2023-05-24 | 2023-08-11 | 929 | null | meat/fish process | 3 | Replaced del valve assly-2,valve kit-1 | null | closed | Replaced del valve assly2,valve kit1
2024-01-15 | Geekay Pneumatic Pvt Ltd | Kerala | D | Fair Exports | Kerala | KCX63 | 3464K143 | 4117487108 | 2023-11-20 | 411748 | 2023-11-19 | high oil consumption | 2022-03-04 | 2023-04-10 | 1041 | null | meat/fish process | 1 | Replaced piston ring set 9 nos | null | closed | Piston ring set9 nos
2024-01-15 | Parag Marketing Services | null | D | Finolex Industries Limited | Ratnagiri | KCX6 | 3394K2195 | 4082067131 | 2023-11-25 | 408206 | 2023-11-23 | kcx low oil pressure | 2023-02-20 | 2023-09-30 | 402 | null | others | 7 | Replaced oil pump assly KCX | null | closed | KCX oil pump assly
2024-01-15 | Trade Links | Secunderabad | D | Sainor Laboratories Pvt Ltd | Telangana | KCX4 | 3384K3128 | 4222327170 | 2023-12-11 | 422232 | 2023-12-09 | abnormal noisebuffer spring shrinkage | 2022-09-20 | 2022-11-22 | 3952 | null | chemical / pharma | 2 | Replaced buffer spring-2 nos | null | closed | Buffer spring 2
2024-01-15 | Kalp Marketing | Gujrat | D | Bostec Cryogenic Gases | Ahmedabad | KCX93 | 3485K136 | 4283027202 | 2023-12-23 | 428302 | 2023-12-22 | shaft seal leakage | 2022-07-31 | 2023-04-21 | 4320 | null | chemical / pharma | 9 | Replaced Shaft seal assly | null | closed | Shaft seal assly
2024-01-15 | Kalp Marketing | Gujrat | D | Bostec Cryogenic Gases | Ahmedabad | KCX93 | 3485K136 | 4178627150 | 2023-12-01 | 417862 | 2023-12-21 | shaft seal leakage | 2022-07-31 | 2023-04-21 | 4320 | null | chemical / pharma | 9 | Replaced oring kit due to leakage | null | closed | Oring kit
2024-01-24 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX31 | 3434K0218 | 4298387216 | 2023-12-27 | 429838 | 2023-12-27 | solenoid valve not working | 2023-06-27 | 2023-10-15 | 108 | null | meat/fish process | 4 | Solenoid valve not working | null | closed | Replaced sol valve
2024-01-31 | Parag Marketing Services | null | D | Siddhi Vinayak Agrotech Cold Stoarge | Sangli | KCX3 | 3374K3013 | 4061207058 | 2023-10-23 | 406120 | 2023-10-21 | abnormal noisedelivery valve leak | 2022-12-20 | 2023-05-23 | 564 | null | cold storage | 5 | Replaced delivery valve and buffer spring | null | closed | Del valve assly & buffer spring
2024-01-31 | Geekay Pneumatic Pvt Ltd | Kerala | D | Laya Milk | Kerala | PCX2 | 3106K0225 | 4184447174 | 2023-12-13 | 418444 | 2023-12-12 | high oil consumption | 2023-05-27 | 2023-08-23 | 964 | null | dairy / ice cream | 3 | Replaced piston ring set PCX2 | null | closed | Replaced piston ring set PCX2
2024-01-31 | Multivista Global Pvt Ltd | Gurgaon | D | Kiran Foods | Uttar Pradesh | KCX63 | 3464K159 | 4236587171 | 2023-12-11 | 423658 | 2023-12-13 | shaft seal leakage | 2023-01-13 | 2023-01-13 | 3262 | null | food processing | 1 | Replaced shaft seal assly,liner,piston,piston ring set | null | closed | Replaced shaft seal assly,liner,piston,piston ring set
2024-01-31 | Trade Links | Secunderabad | D | Jayalaxmi Sea Foods | Andhra Pradesh | KCX6 | 3394K2118 | 4021266981 | 2023-09-26 | 402126 | 2023-09-26 | abnormal noisedelivery valve leak | 2022-12-09 | 2023-06-09 | 1714 | null | ice plant | 6 | Delivery valve leak due to step observed on del stroke limiter | null | closed | Replaced piston,del valve,piston ring set,buffer spring
2024-01-31 | Kalp Marketing | Gujrat | D | Crystal Ice & Cold Storage | Ratnagiri | KCX3 | 3374K2912 | 4319407252 | 2024-01-10 | 431940 | 2024-01-10 | krms issuesmps and controller not working | 2022-09-18 | 2022-09-24 | 5910 | null | ice plant | 1 | Controller damaged due to failure of SMPS. | null | closed | Replaced SMPS and Controller
2024-01-31 | Geekay Pneumatic Pvt Ltd | Kerala | D | Cheruvathur Ice & Cold Storage | Kerala | KCX3 | 3374K2949 | 4150047120 | 2023-11-23 | 415004 | 2023-11-23 | oil carry over | 2022-11-07 | null | null | null | ice plant | 3 | Replaced Piston ring set,cylinder liner | null | closed | Replaced Piston ring set,cylinder liner
2024-01-31 | Trade Links | Secunderabad | D | Ananada Enterprises | Andhra Pradesh | KCX72 | 3474K590 | 4220267186 | 2023-12-18 | 422026 | 2023-12-16 | abnormal noisecylinder siezed | 2022-11-23 | 2023-02-20 | 4168 | null | meat/fish process | 3 | HP cylinder no 4- piston,needle bearing,cylinder liner,piston ring set damaged | null | closed | HP cylinder no 4 piston,needle bearing,cylinder liner,piston ring set damaged
2024-02-03 | Gargi Engineering Enterprices Pvt Ltd | null | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX51 | 3454K210 | 4322607257 | 2024-01-11 | 432260 | 2024-01-30 | krms issue | 2022-10-31 | 2022-12-11 | 1781 | 880 | food processing | 2 | Suction and discharge snsors malfunctioning. | null | closed | Replaced suction and discharge temp sensors.
2024-02-03 | Pragya Industrial Supply | Karnataka | D | Sats Food Pvt Ltd | Karnataka | KCX63 | 3464K170 | 4354547324 | 2024-02-03 | 435454 | 2024-02-03 | shaft seal leakage | 2023-02-28 | 2023-12-26 | 500 | 950 | food processing | 10 | Flywheel wobbling , crankshaft key way broken and shaft seal leakage. | null | closed | Replaced crankcasft and key
2024-02-03 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vilayat Pharma | Gujrat | KCX72 | 3474K533 | 4316887242 | 2024-01-08 | 431688 | 2024-01-08 | oil pressure not buildup | 2022-03-07 | 2024-01-08 | 4 | 830 | ice plant | 21 | Oil pressure not develop due to pump tang broken. DD to DC GAP IS MORE THAN 1.5 YEAR. | null | closed | Replaced element.
2024-02-03 | Kalp Marketing | Gujrat | D | Shree Niddhi ExportsPorbandar | Gujrat | KCX51 | 3454K224 | 4322447263 | 2024-01-16 | 432244 | 2024-01-16 | abnormal noise delivery valve leakage | 2023-05-20 | 2023-08-11 | 1150 | 990 | meat/fish process | 3 | HP Cylinder damaged due to delivery valve leakage. | null | closed | Replaced Liner , Piston rings , valve ki, buffer spring and bearings..
2024-02-06 | Kalp Marketing | Gujrat | D | Mayur Fish Suppliers | Gujrat | KCX42 | 3444K414 | 4300287223 | 2023-12-30 | 430028 | 2023-12-29 | abnormal noise | 2023-07-17 | 2023-08-12 | 1428 | 880 | cold storage | 1 | Cyl 2 and 4 liner , piston and piston rings wornout. | null | closed | Replaced liner , piston , piston rings
2024-02-06 | Parag Marketing Services | null | D | Maa Banbhori Agro | Chhattisgarh | KCX4 | 3384K3537 | 4344747293 | 2024-01-25 | 434474 | 2024-01-23 | retainer plate damaged | 2023-12-26 | 2024-01-23 | 8 | 770 | cold storage | 1 | Retainer plate welding crack. (This is due to excess tightning as per FRR remark) | null | closed | Replaced retainer plate assly
2024-02-06 | Trade Links | Secunderabad | D | Sids Farm Pvt Ltd | Telangana | KCX2 | 3364K2458 | 4242267173 | 2023-12-12 | 424226 | 2023-12-11 | abnormal noise | 2023-03-30 | 2023-07-28 | 1485 | 750 | dairy / ice cream | 4 | Cyl no.1 Liner and piston rings wornout | null | closed | Replaced liner and Piston ring set.
2024-02-06 | Multivista Global Pvt Ltd | Tamil Nadu | D | Dodla Dairy Ltd | Tamil Nadu | KCX1 | 3354K264 | 4318127254 | 2024-01-10 | 431812 | 2024-01-10 | oil carry over | 2022-12-28 | 2023-01-30 | 1238 | 850 | dairy / ice cream | 1 | Piston rings wornout | null | closed | Replaced piston ring set
2024-02-06 | Parag Marketing Services | null | D | Krishana Dairy | Ahmed Nagar | KCX2 | 3364K2431 | 4172087193 | 2023-12-20 | 417208 | 2023-11-27 | pressure gauge leak | 2023-02-19 | 2023-06-07 | 1001 | 850 | dairy / ice cream | 4 | Pressure gauge 16 Kg/cm2 Leak after 1000 hrs. | null | closed | Replaced Pressure gauge 16 Kg/cm2
2024-02-06 | Parag Marketing Services | null | D | Jay Milk And Milk Products | Khatav | PCX2 | 3106K0238 | 4029627191 | 2023-12-20 | 402962 | 2023-09-20 | pressure gauge not working | 2023-07-22 | 2023-09-29 | 2 | 850 | dairy / ice cream | 2 | Pressure gauge 16 Kg/cm2 found out. | null | closed | Replaced Pressure gauge 16 Kg/cm2
2024-02-06 | Kalp Marketing | Gujrat | D | R S Food Chain | Madhya Pradesh | KCX72 | 3474K715 | 4336267286 | 2024-01-23 | 433628 | 2024-01-23 | oil pressure not buildup | 2023-11-22 | 2024-01-12 | 33 | 767 | food processing | 2 | Pump tang broken. | null | closed | Replaced element.
2024-02-06 | Trade Links | Goa | D | Thomas Ice Plant | Goa | KCX3 | 3374K3182 | 4073727089 | 2023-11-04 | 407372 | 2023-11-07 | oil carry over | 2023-07-13 | 2023-08-09 | 862 | 700 | ice plant | 1 | Piston ring set wornout , Orv leak. Actual oil consumption not mentioned in FSR | null | closed | Replaced piston rings and ORV 3nos
2024-02-06 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sesaga Enterprises | Panvel | KCX72 | 3474K654 | 4284387215 | 2024-12-27 | 428438 | 2023-12-27 | oil carry over | 2023-06-16 | 2023-08-14 | 1037 | 985 | meat/fish process | 2 | All piston rings wornout, Liner step cut marks , 5 nos delivery valves leak. | null | closed | Replaced liner 9 , piston 9 , piston rings 9 , deleivery valve 5 nos.
2024-02-06 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX51 | 3454K222 | 4355007303 | 2024-01-29 | 435500 | 2024-01-28 | shaft seal leakage | 2023-06-10 | 2023-09-30 | 361 | 990 | meat/fish process | 3 | Found rotory seal damage. | null | closed | Replaced shaft seal assly
2024-02-06 | Parag Marketing Services | null | D | Finolex Industries Limited | Ratnagiri | KCX3 | 3374K2944 | 4285147275 | 2024-01-20 | 428514 | 2024-01-19 | oil carry over | 2022-11-04 | 2023-01-06 | 7464 | 840 | chemical / pharma | 2 | 3.5 lit/Hr. One liner , Piston , Piston ring set wornout. | null | closed | Replaced Liner , Piston and piston ring set
2024-02-14 | Parag Marketing Services | null | D | Melghat Cold Chain | Nagpur | KCX63 | 3464K201 | Mail | 2024-02-14 | null | 2024-02-14 | wrong name plate | null | null | 0 | null | null | null | Wrong SBM number punched. Required 3464 K 201 Actual punched 3364 K 201. | null | closed | Correct name plate handover to service
2024-02-20 | Kalp Marketing | Gujrat | D | Green Agro | Mansa, Gandhinagar | KCX3 | 3374K3281 | Mail | 2024-02-10 | null | 2024-02-10 | wrong name plate of demister oil separators | 2023-11-03 | 2024-02-10 | 0 | 936 | null | 3 | Wrong IN/OUT connections on OS Name plate. Old demister os name plate. | null | open | null
2024-02-20 | Kalp Marketing | Gujrat | D | Mayur Fish Suppliers | Gujrat | KCX42 | 3444K414 | 4319107262 | 2024-01-16 | 431910 | 2024-01-16 | knocking / abnormal sound | 2023-07-17 | 2023-08-12 | 1542 | 880 | cold storage | 1 | Liner cut mark in HP Cylinder no.4 | null | closed | Replaced Liner , Piston ring set , Gudgeon pin & Connecting rod.
2024-02-20 | Kalp Marketing | Gujrat | D | Mayur Fish Suppliers | Gujrat | KCX42 | 3444K414 | 4344867304 | 2024-01-29 | 434486 | 2024-01-29 | knocking / abnormal sound | 2023-07-17 | 2023-08-12 | 1660 | 880 | cold storage | 1 | HP Cylinders 1 & 4 Liners and piston rings wornout , 1 delivery valve leakage and buffer spring shrink | null | closed | Replaced liners & Piston rings 2 nos and Delivery valve & Buffer spring 1 no./ each.
2024-02-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Aimjay Agro Fresh Llp | Thane | KCX3 | 3374K3071 | 4356807312 | 2024-01-31 | 435680 | 2024-01-29 | oil carry over | 2023-01-22 | 2023-05-27 | 2358 | 750 | cold storage | 5 | Oil throw 12ml/cyl/hr. Piston rings wornout. | null | closed | Replaced piston ring sets 3 nos.
2024-02-20 | Multivista Global Pvt Ltd | Gurgaon | D | Arvind Dairy Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2152 | 4085207083 | 2023-11-02 | 408520 | 2023-12-10 | oil carry over | 2022-12-31 | 2023-07-19 | 1429 | 800 | dairy / ice cream | 7 | Liners, Piston and Piston rings wornout. | null | closed | Replaced Liners & Piston rings 6 nos and Pistons 4 nos.
2024-02-20 | Parag Marketing Services | Pune | D | Indiaqo Foods Pvt Ltd | Supa | KCX72 | 3474K593 | 4328847306 | 2024-01-29 | 432884 | 2024-01-29 | abnormal noise | 2022-11-28 | 2023-08-25 | 231 | 800 | food processing | 10 | Abnormal noise from cyl no.4 HP, Liner cut marks and piston rings wornout. | null | closed | Replaced liner, piston , piston rings 1 no each.
2024-02-20 | Kalp Marketing | Gujrat | D | Jagdish Agri Exporters Pvt Ltd | Madhya Pradesh | KCX6 | 3394K2071 | 4336647288 | 2024-01-24 | 433664 | 2024-01-23 | cylinder overheating | 2022-10-22 | 2023-01-17 | 1186 | 990 | food processing | 3 | Delivery valve ring spring broken. & Overheating. | null | closed | Replaced delivery valve , piston , piston ring and liner, Gudgeon pin 1 no/ each
2024-02-20 | Multivista Global Pvt Ltd | Gurgaon | D | Hfl Consumater Private Limited | Uttar Pradesh | KCX6 | 3394K2041 | 4318407245 | 2024-01-09 | 431840 | 2024-01-09 | oil carry over | 2022-09-30 | 2023-04-20 | 3837 | 850 | food processing | 7 | Piston and piston rings wornout 2 nos | null | closed | Replaced piston & piston rings 2 nos.
2024-02-20 | Kalp Marketing | Gujrat | D | Innovative Agrotech | Gujrat | KCX72 | 3474K694 | 4364447317 | 2024-02-01 | 436444 | 2024-01-31 | shaft seal leakage | 2023-09-26 | 2023-12-06 | 502 | 990 | food processing | 3 | Shaft seal Oring flatened. | null | closed | Replaced Oring kit
2024-02-20 | Kalp Marketing | Gujrat | D | Shree Nidhi Exports | Gujrat | KCX72 | 3474K650 | 4322467264 | 2024-01-16 | 432246 | 2024-01-16 | abnormal noise | 2023-05-20 | 2023-08-11 | 865 | 990 | meat/fish process | 3 | HP Cylinders seized | null | closed | Replaced Piston , liners , Gudgeon pin , Piston ring sets and bearings 2 nos each.
2024-02-20 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX72 | 3474K649 | 4356387301 | 2024-01-29 | 435638 | 2024-01-28 | shaft seal leakage | 2023-06-10 | 2023-10-01 | 989 | 990 | meat/fish process | 5 | Oring flattend. | null | closed | Replaced Oring kit.
2024-02-20 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX31 | 3434K0219 | 4356407302 | 2024-01-29 | 435640 | 2024-01-29 | shaft seal leakage | 2023-06-27 | 2023-10-01 | 373 | 990 | meat/fish process | 4 | Shaft seal leakage. | null | closed | Replaced Oring kit.
2024-02-20 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX31 | 3434K0219 | 4364527318 | 2024-02-01 | 436452 | 2024-01-31 | stop valve leakage | 2023-06-27 | 2023-10-01 | 379 | 990 | meat/fish process | 4 | Discharge stop valve Tal 50/70 Inlet leakage from welding joint. | null | closed | Replaced Stop valve 50/70 Inlet
2024-02-27 | Cool Comfort Private Limited | West Bengal | D | Nirupama Cold Storage | West Bengal | KCX6 | 3394K2076 | 4382947353 | 2024-02-12 | 438294 | 2024-03-01 | abnormal noise | 2022-10-31 | 2023-03-06 | 1496 | 850 | cold storage | 5 | Replaced cylinder liner,piston ring set | null | closed | Cylinder liner,piston ring set
2024-02-27 | Kalp Marketing | Gujrat | D | Mayur Fish Suppliers | Gujrat | KCX42 | 3444K414 | 4378267357 | 2024-02-13 | 437826 | 2024-02-10 | cylinder overheating | 2023-07-17 | 2023-08-12 | 1783 | 880 | cold storage | 1 | Cylinder no. 2 & 5 overheating due to delivery valve leakage. | null | closed | Replaced delivery valve 2 and Buffer spring 1
2024-02-27 | Kalp Marketing | Gujrat | D | Choudhary Cold Storage | Madhya Pradesh | KCX3 | 3374K3376 | 4402247396 | 2024-02-24 | 440224 | 2024-02-20 | gauge board fittings leakage | 2024-01-22 | 2024-02-20 | 1 | 767 | cold storage | 1 | Gaugeboard female run tee leakage from thread joint. | null | closed | Replaced Female run tee
2024-02-27 | Kalp Marketing | Gujrat | D | Jay Maa Ambe Cold Storage | Madhya Pradesh | KCX3 | 3374K2955 | 4423487417 | 2024-03-01 | 442348 | 2024-03-01 | oil carry over | 2022-11-11 | 2023-03-07 | 1494 | 767 | cold storage | 4 | All piston ring sets wornout and one liner cut mark. | null | closed | Replaced Liner1 and Piston rings3 sets
2024-02-27 | Kalp Marketing | Gujrat | D | Green Agro | Mansa, Gandhinagar | KCX3 | 3374K3281 | 4326507362 | 2024-02-14 | 432650 | 2024-02-09 | pressure gauge glyceryne leakage | 2023-11-03 | 2024-02-09 | 1 | 936 | cold storage | 3 | Pressure gauge glycerin leaked. | null | closed | 0 to 16 Kg/cm2 Pressure gauge
2024-02-27 | Multivista Global Pvt Ltd | Gurgaon | D | R S Cold Storage | Uttar Pradesh | KC6 | 339K3712 | 4402667392 | 2024-02-23 | 440266 | 2023-02-23 | pressure gauge not working | 2023-10-16 | 2024-02-23 | 2 | 750 | cold storage | 4 | Replaced discharge pressure gauge 25 kg/cm2 | null | closed | Replaced discharge pressure gauge 25 kg/cm2
2024-02-27 | Parag Marketing Services | Pune | D | Indiaqo Foods Pvt Ltd | Maharashtra | KCX42 | 3444K353 | 4402987382 | 2024-02-21 | 440298 | 2024-02-03 | shaft seal leakage | 2022-05-30 | 2023-09-29 | 0 | 750 | cold storage | 16 | Shaft seal assly & shaft seal cover replaced | null | closed | Shaft seal assly & Shaft seal cover
2024-02-27 | Multivista Global Pvt Ltd | Gurgaon | D | Mahadev Ind | Uttar Pradesh | KC4 | 338K5908 | 4409227422 | 2024-03-02 | 440922 | 2024-03-02 | solenoid coil burnt | 2024-01-18 | 2024-03-10 | 4 | 750 | cold storage | 2 | Coil burnt | null | closed | Replaced coil1 no.
2024-02-27 | Multivista Global Pvt Ltd | Gurgaon | D | Jay Kishan Cold Storage | Uttar Pradesh | KC4 | 338K5911 | 4414827460 | 2024-03-11 | 441482 | 2024-03-10 | solenoid coil burnt | 2024-01-30 | 2024-03-10 | 2 | 750 | cold storage | 2 | Coil burnt | null | closed | Replaced coil1 no.
2024-02-27 | Multivista Global Pvt Ltd | Gurgaon | D | Om Namah Shivay Cold Storage | Uttar Pradesh | KC4 | 338K5890 | 4408427456 | 2024-03-11 | 440842 | 2024-03-10 | solenoid coil burnt | 2024-01-03 | 2024-03-10 | 16 | 768 | cold storage | 3 | Coil burnt | null | closed | Replaced coil1 no.
2024-02-27 | Multivista Global Pvt Ltd | Gurgaon | D | Baba Lodheshwar Cold Storage | Uttar Pradesh | KC4 | 338K5874 | 4422907457 | 2024-03-11 | 442290 | 2024-03-10 | solenoid coil burnt | 2023-12-20 | 2024-03-10 | 2 | 750 | cold storage | 3 | Coil burnt | null | closed | Replaced coil1 no.
2024-02-27 | Parag Marketing Services | null | D | Shrinivasa Milk & Milk Products | Sangli | KCX3 | 3374K3110 | 4356527351 | 2024-02-12 | 435652 | 2024-02-10 | oil carry over | 2023-02-21 | 2023-06-27 | 1868 | 767 | dairy / ice cream | 5 | All piston rings wornout, one piston and liner wornout, 3 delivery valve kit broken. | null | closed | Replaced piston rings 3 sets, Liner 1, Piston 1 & kit delivery valve 3
2024-02-27 | Multivista Global Pvt Ltd | Tamil Nadu | D | Madurai Famous Jigarthanda | Tamil Nadu | KCX1 | 3354K276 | 4336747282 | 2024-01-22 | 433674 | 2024-01-20 | suction oil filter spring missing | 2023-02-28 | 2024-01-20 | 2 | 773 | dairy / ice cream | 11 | Suction oil filter spring missing | null | closed | Suction oil filter Spring
2024-02-27 | Parag Marketing Services | null | D | Indiaqo Foods Pvt Ltd | Supa | KCX72 | 3474K593 | 4385007366 | 2024-02-15 | 438500 | 2024-02-15 | abnormal noise | 2022-11-28 | 2023-08-25 | 238 | 800 | food processing | 9 | HP Cyl 4 liner, piston rings , Gudgeon pin wornout. | null | closed | Replaced liner, piston rings , Gudgeon pin
2024-02-27 | Trade Links | Secunderabad | D | Blue Earth Food Processing | Andhra Pradesh | KCX93 | 3485K171 | 4314907338 | 2024-02-06 | 431490 | 2024-01-24 | pressure transducer threading damaged at field by tl service engineer | 2023-10-21 | 2024-01-24 | 11 | 950 | food processing | 3 | Replaced Pressure transducer & adaptors | null | closed | Pressure transducer & adaptors
2024-02-27 | Parag Marketing Services | null | D | Indiaqo Foods Pvt Ltd | Supa | KCX72 | 3474K599 | 4402747381 | 2024-02-21 | 440274 | 2024-02-20 | shaft seal leakage | 2022-11-28 | 2023-08-25 | 649 | 800 | food processing | 9 | Shaft seal leakage. | null | closed | Replaced shaft seal assly
2024-02-27 | Parag Marketing Services | Pune | D | Indiaqo Foods Pvt Ltd | Maharashtra | KCX42 | 3444K344 | 4388827330 | 2024-02-05 | 436882 | 2024-02-03 | shaft seal leakage | 2022-03-26 | 2023-12-18 | 535 | 750 | food processing | 21 | Shaft seal oring kit | null | closed | Shaft seal oring kit
2024-02-27 | Geekay Pneumatic Pvt Ltd | null | D | Parvathy Ice Industries | Kerala | KCX2 | 3364K2433 | 4155707137 | 2023-11-28 | 415570 | 2023-11-27 | abnormal noise | 2023-02-22 | 2023-09-20 | 496 | 820 | ice plant | 7 | Replaced cylinder liner & piston ring set due to wornout | null | closed | Cylinder liner & piston ring sets
2024-02-27 | Trade Links | Secunderabad | D | Sri Venkateshwar Ice Factory | Andhra Pradesh | KCX4 | 3384K3365 | 4180547156 | 2023-12-04 | 418054 | 2023-12-02 | oil carry over | 2023-06-02 | 2023-08-01 | 3525 | 750 | ice plant | 2 | Oil carry over rate 5 lit/24 hrs. All piston rings and 2 liners wornout. | null | closed | Replaced liner2 & Piston rings 4 sets
2024-02-27 | Pragya Industrial Supply | Karnataka | D | Korgappa Ice And Cold Storage | Karnataka | KCX4 | 3384K3393 | 4327647265 | 2024-01-16 | 432764 | 2024-01-16 | oil carry over | 2023-07-27 | 2023-10-20 | 1896 | 800 | ice plant | 3 | Replaced piston ring set,cylinder liner,Discharge valve assly | null | closed | Piston ring set,Cylinder liner,Dischaarge valve assly
2024-02-27 | Kalp Marketing | Gujrat | D | Shree Nidhi Exports | Gujrat | KCX72 | 3474K651 | 4322487320 | 2024-02-01 | 432248 | 2024-02-01 | abnormal noise | 2023-08-11 | 2023-05-20 | 636 | 990 | meat/fish process | 5 | Knocking sound from HP cylinderS. | null | closed | Replaced Liners and piston rings.
2024-02-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises | Panvel | KCX72 | 3474K654 | 4327647298 | 2024-01-16 | 435064 | 2024-02-22 | abnormal noise & oil carry over | 2023-06-16 | 2023-08-14 | 643 | 985 | meat/fish process | 2 | Abnormal sound from HP Cylinders. | null | closed | Replaced liner 2, Piston 2 , Piston ring set 2, Shaft seal and bearings.
2024-02-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises | Panvel | KCX72 | 3474K654 | 4327647265 | 2024-01-16 | 435064 | 2024-02-22 | abnormal noise & oil carry over | 2023-06-16 | 2023-08-14 | 643 | 985 | meat/fish process | 2 | Abnormal sound from HP Cylinders.2 Piston ring sets, Liner 1 and Delivery valve 1 replaced. | null | closed | 2 Piston ring sets, Liner 1 and Delivery valve 1 replaced.
2024-02-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises | Panvel | KCX72 | 3474K657 | 4320427258 | 2024-01-12 | 432042 | 2024-02-29 | oil carry over | 2023-06-16 | 2023-08-14 | 1170 | 983 | meat/fish process | 2 | All cylinder liners, piston and piston rings wornout. | null | closed | Replaced All cylinder liners, piston and piston rings.
2024-02-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Upl Limited | Gujrat | KCX3 | 3374K3195 | 4085307168 | 2023-12-08 | 408530 | 2023-12-08 | oil pressure problem | 2023-07-26 | 2023-12-08 | 5 | 650 | chemical / pharma | 5 | Oil pressure regulator not working. | null | closed | Replaced OPR 1 NO.
2024-02-27 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Upl Limited | Gujrat | KCX3 | 3374K3195 | 4236267190 | 2023-12-20 | 423626 | 2023-12-26 | oil pressure problem | 2023-07-26 | 2023-12-08 | 236 | 650 | chemical / pharma | 5 | Oil pressure regulator not working. | null | closed | Replaced OPR 1 NO.
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Shridhar Agrofresh Pvt Ltd | null | KC4 | 338K5898 | 4453727481 | 2024-03-16 | 445372 | 2024-03-15 | coil burnt at the time of commisioning | 2024-01-15 | 2024-03-15 | 2 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Banke Bihari Sheetalaya | Uttar Pradesh | KC4 | 338K5900 | 4439307496 | 2024-03-19 | 443930 | 2024-03-19 | coil burnt at the time of commisioning | 2024-03-15 | 2024-03-15 | 0 | 750 | cold storage | 1 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve.Ammonia Pressure Guage
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Roopali Cold Storage | null | KC4 | 338K5909 | 4409267426 | 2024-03-04 | 440926 | 2024-03-02 | coil burnt at the time of commisioning | 2024-01-22 | 2024-03-02 | 2 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Om Namah Shivay Cold Storage | Uttar Pradesh | KC3 | 337K4873 | 4432607500 | 2024-03-20 | 443260 | 2024-03-19 | coil burnt at the time of commisioning | 2024-01-25 | 2024-03-19 | 2 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Prasad Agro Industries | null | KC6 | 339K3772 | 4452507470 | 2024-03-14 | 445250 | 2024-03-14 | coil burnt at the time of commisioning | 2024-01-24 | 2024-02-26 | 14 | 750 | cold storage | 1 | Coil burnt within few hrs after commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | RY Cold Warehouse | null | KC6 | 339K3775 | 4423527499 | 2024-03-20 | 442352 | 2024-03-19 | coil burnt at the time of commisioning | 2024-01-25 | 2024-03-19 | 4 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | SPS Cold Storage | null | KC6 | 339K3764 | 4453047480 | 2024-03-16 | 445304 | 2024-03-15 | coil burnt at the time of commisioning | 2024-01-13 | 2024-03-05 | 17 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | SPS Cold Storage | null | KC4 | 338K5899 | 4386307479 | 2024-03-16 | 438630 | 2024-03-15 | coil burnt at the time of commisioning | 2024-01-13 | 2024-03-15 | 2 | 750 | cold storage | 3 | Coil burnt at the time of commisioning | null | closed | Coil for NO Solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Durga Maa Sheetgrah Llp | null | KC4 | 338K5920 | 4446447459 | 2024-03-11 | 444644 | 2024-03-09 | coil burnt at the time of commisioning | 2024-02-06 | 2024-03-09 | 3 | 750 | cold storage | 1 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | SJIce & Cold Storage | null | KC4 | 338K5881 | 4402507426 | 2024-03-06 | 440250 | 2024-03-06 | coil burnt at the time of commisioning | 2023-12-20 | 2024-03-06 | 5 | 750 | cold storage | 4 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Geet Devi Cold Storage Ltd | null | KC4 | 338K5852 | 4466587512 | 2024-03-25 | 446658 | 2024-03-23 | coil burnt at the time of commisioning | 2023-10-23 | 2024-03-23 | 5 | 750 | cold storage | 6 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Ak Cold Storage & Allied Industry | null | KC4 | 338K5914 | 4463207503 | 2024-03-21 | 446320 | 2024-03-21 | coil burnt at the time of commisioning | 2024-01-30 | 2024-03-21 | 2 | 750 | cold storage | 4 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Karaniya Cold Storage Pvt Ltd | null | KC6 | 339K3753 | 4452787475 | 2024-03-14 | 445278 | 2024-03-14 | coil burnt at the time of commisioning | 2023-12-29 | 2024-03-13 | 3 | 750 | cold storage | 4 | Coil burnt at the time of commisioning | null | closed | Coil for solenoid valve
2024-03-29 | Kalp Marketing | Gujrat | D | Satish Ice & Cold Storage | null | KCX3 | 3374K3011 | 4439627454 | 2024-03-08 | 443962 | 2024-03-08 | cylinder overheating | 2022-12-17 | 2023-01-20 | 915 | 767 | cold storage | 1 | Replaced delivery valve , piston , piston ring and liner, Gudgeon pin 1 no/ each | null | closed | Replaced delivery valve , piston , piston ring and liner, Gudgeon pin 1 no/ each
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Govind Refrigation | null | KC4 | 3384K5877 | 4396567425 | 2024-03-04 | 439656 | 2024-03-03 | guage found damage at the time of comissioning | 2023-12-13 | 2024-03-03 | 18 | 757 | cold storage | 4 | Guage Found damage at the time of comissioning | null | closed | Ammonia Pressure Guage
2024-03-29 | Kalp Marketing | Gujrat | D | Jai Maa Ambe Cold Storage | null | KCX3 | 3374K2955 | 4423487417 | 2024-03-01 | 442348 | 2024-03-01 | high oil consumption | 2022-09-11 | 2023-03-07 | 1494 | 767 | cold storage | 5 | Replaced cylinder liner,piston,piston ring set | null | closed | Replaced cylinder liner,piston,piston ring set
2024-03-29 | Cool Comfort Private Limited | West Bengal | D | Bhanulal Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K2418 | 4451287469 | 2024-03-13 | 445128 | 2024-03-13 | hour meter not working | 2024-01-23 | 2024-03-13 | 4 | 850 | cold storage | 1 | Hour Meter not working | null | closed | Replaced Hour meter
2024-03-29 | Kalp Marketing | Gujrat | D | Jai Jinedra Agro Foods Llp | Gujrat | KCX63 | 3464K195 | 4388847434 | 2024-03-05 | 438884 | 2024-02-29 | k5 valve leakage | 2023-11-08 | 2024-02-29 | 1 | 771 | cold storage | 4 | Replaced K5 Valve | null | closed | Replaced K5 Valve
2024-03-29 | Trade Links | Secunderabad | D | Jeevan Sree Cold Storage | Andhra Pradesh | KCX2 | 3364K2623 | 4408307399 | 2024-02-26 | 440830 | 2024-02-24 | k5 valve leakage | 2024-01-27 | 2024-02-24 | 6 | 760 | cold storage | 1 | Replaced K5 Valve | null | closed | Replaced K5 Valve
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Frostar Foods Pvt Ltd | null | KCX72 | 3474K718 | 4439527453 | 2024-03-08 | 443952 | 2024-03-08 | kcx oil pump pressure issue | 2023-12-04 | 2024-02-15 | 3 | 850 | cold storage | 3 | Oil pump element broken,premature failure | null | closed | Replaced Oil Pump assembly KCX
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Tirupati Cold Storage & Ice Factory | null | KC6 | 339K3741 | 4462827511 | 2024-03-25 | 446282 | 2024-03-01 | knocking / abnormal sound | 2023-12-15 | 2024-03-01 | 8 | 750 | cold storage | 4 | Cylinder liners no.1 & no.4 having acut mark on upper side due to emert particles | null | closed | Cylinder liners, piston and piston rings
2024-03-29 | S. B. Refrigeration Services | null | D | Shri Janki Agro Product & Colod Storage | Bihar | KCX3 | 3374K3372 | 4456707495 | 2024-03-19 | 445670 | 2024-03-28 | oil pressure not buildup | 2024-01-20 | 2024-03-11 | 1 | 918 | cold storage | 2 | Replaced Oil Pump Element | null | closed | Replaced Oil Pump Element
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uttar Pradesh | KC84 | 330K60 | 4420367465 | 2024-03-12 | 442036 | 2024-03-12 | oil pressure problem | 2022-10-08 | 2023-01-30 | 570 | 937 | cold storage | 4 | Pump does not create desire pressure | null | closed | Replaced Oil Pump assembly KC
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Radha Krishna Shetgrah Pvt Ltd | null | KC4 | 338K5917 | 4456047494 | 2024-03-19 | 445604 | 2024-03-21 | oil pressure problem | 2024-01-31 | 2024-03-03 | 191 | 750 | cold storage | 1 | Pump does not create desire pressure upto 1 KG | null | closed | Replaced Oil Pump assembly KC
2024-03-29 | Cool Comfort Private Limited | West Bengal | D | Dooars Kanya Cold Storagepvt Ltd | West Bengal | KCX6 | 3394K2377 | 4455487487 | 2024-03-18 | 445548 | 2024-03-26 | oil pressure problem | 2023-12-25 | 2024-03-09 | 10 | 850 | cold storage | 3 | Small Gear Jam Driving Gear | null | closed | Replaced Pump Element
2024-03-29 | S. B. Refrigeration Services | null | D | Mishri Saw Ware Housing Pvt Ltd | Bihar | KCX6 | 3394K2343 | 4452927478 | 2024-03-15 | 445292 | 2024-03-14 | pressuere gauge not working | 2023-11-28 | 2024-03-14 | 1 | 866 | cold storage | 3 | Pressure Gauge not Working | null | closed | Replaces Pressure Gauge
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Baba Lodheshwar Cold Storage | Uttar Pradesh | KC6 | 339K3745 | 4422947458 | 2024-03-11 | 442294 | 2024-03-10 | solenoid coil burnt | 2023-12-20 | 2024-03-10 | 2 | 750 | cold storage | 3 | Coil burnt | null | closed | Replaced coil1 no.
2024-03-29 | Kalp Marketing | Gujrat | D | Gopi Cold Storage | Mansa, Gujrat | KCX3 | 3374K3250 | 4409467393 | 2024-02-23 | 440946 | 2024-02-23 | suction pressure gauge malfuctioning problem | 2023-10-16 | 2024-02-08 | 14 | 771 | cold storage | 4 | Glycerine Leakage from Suction Pressure Guage | null | closed | Replaces Suction Pressure Guage
2024-03-29 | Kalp Marketing | Gujrat | D | Rajkamal Cold Storage | null | KCX4 | 3384K3444 | 4428687427 | 2024-03-04 | 442868 | 2024-03-02 | suction pressure guage not working | 2023-10-06 | 2024-02-07 | 8 | 768 | cold storage | 5 | Ammonia Pressure Guage | null | closed | Ammonia Pressure Guage
2024-03-29 | Kalp Marketing | Gujrat | D | Sheenath Cold Storage | null | KCX4 | 3384K3463 | 4428667429 | 2024-03-04 | 442866 | 2024-03-02 | suction pressure guage not working | 2023-10-26 | 2024-01-31 | 10 | 767 | cold storage | 4 | Suction Pressure Guage not working | null | closed | Ammonia Pressure Guage
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | CPMilk & Food Product Pvt Ltd | null | KCX42 | 3444K422 | 4346607464 | 2024-03-12 | 434660 | 2024-03-12 | abnormal noise observed on liner(hp) | 2023-09-13 | 2024-01-16 | 268 | 750 | dairy / ice cream | 5 | Knocking sound from HP cylinderS. | null | closed | Replaced Liners and piston ring set
2024-03-29 | Multivista Global Pvt Ltd | Gurgaon | D | Batohi Chilling And Ice Plant | null | KCX4 | 3384K3503 | 4398627445 | 2024-03-06 | 439862 | 2024-03-12 | shaft sheal assembly problem | 2023-12-06 | 2024-03-12 | 5 | 750 | dairy / ice cream | 4 | Shaft Sheal Assembly Problem | null | closed | Shaft Sheal Assembly
2024-03-29 | Parag Marketing Services | null | D | Indiaqo Foods Pvt Ltd | Ahmed Nagar | KCX72 | 3474K600 | 4368687333 | 2024-02-05 | 436868 | 2024-02-03 | shaft seal leakage | 2022-11-28 | 2023-08-25 | 665 | 800 | food processing | 9 | Replaced shaft seal assly | null | closed | Replaced shaft seal assly
2024-03-29 | Geekay Pneumatic Pvt Ltd | null | D | Zara Industries | Kerala | KCX4 | 3384K3339 | 4435327450 | 2024-03-07 | 443532 | 2024-03-07 | cylinder overheating | 2023-03-29 | 2023-08-17 | 1736 | 850 | ice plant | 5 | Stroke Limitor Has Step Mark | null | closed | Replaced Discharg Valve Assly
2024-03-29 | Hss Solution Pvt Ltd | null | D | Suman Deviw/O Rajendra Kumar Moond | Rajastan | KCX2 | 3364K2630 | 4439487468 | 2024-03-13 | 443948 | 2024-03-12 | hour meter not working | 2024-02-07 | 2024-03-12 | 4 | 750 | ice plant | 1 | Hour Meter not working | null | closed | Replaced Hour meter
2024-03-29 | Trade Links | Secunderabad | D | Mandovi Fisherman Marketing Co-Op Society | Goa | KCX3 | 3374K3184 | 4374367394 | 2024-02-24 | 437436 | 2024-02-23 | oil carry over | 2023-07-13 | 2023-08-12 | 3266 | 700 | ice plant | 1 | Replaced Piston, Gudgeon pin, Filter Wire Guage Wire Filter & Discharge Valve Assly | null | closed | Replaced Piston, Gudgeon pin, Filter Wire Guage Wire Filter & Discharge Valve Assly
2024-03-29 | Trade Links | Secunderabad | D | Sri Laxmi Ice Factory | Andhra Pradesh | KCX4 | 3384K3238 | 4403467397 | 2024-02-26 | 440346 | 2024-02-24 | oil lifting | 2023-01-03 | 2023-03-24 | 6520 | 850 | ice plant | 3 | Replaced Kit Delivery Valve, Cylinder Liner & Piston Ring Set | null | closed | Kit Delivery Valve, Cylinder Liner & Piston Ring Set
2024-03-29 | Geekay Pneumatic Pvt Ltd | null | D | Kumbazha Ice Plant | null | KCX3 | 3374K2927 | 4376767349 | 2024-02-09 | 437676 | 2024-02-09 | shaft seal leakage | 2022-10-03 | 2023-03-16 | 5492 | 820 | ice plant | 6 | Shaft Seal Leakage | null | closed | Replaced shaft seal assly
2024-03-29 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3497 | 4428087449 | 2024-03-07 | 442808 | 2024-03-06 | solenoid coil issue | 2023-11-24 | 2024-03-06 | 12 | 800 | ice plant | 3 | Coil Not Working | null | closed | Replaced Solenoid Coil
2024-03-29 | Trade Links | Secunderabad | D | Sapala Organics P Ltd | Telangana | KCX1 | 3354K321 | 4414127406 | 2024-02-27 | 441412 | 2024-02-26 | shaft seal leakage | 2023-12-11 | 2024-02-23 | 4 | 750 | chemical / pharma | 3 | Replaced shaft seal assly | null | closed | Shaft seal assly
2024-03-29 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX42 | 3444K362 | 4423807409 | 2024-02-28 | 442380 | 2024-02-28 | krms(discharge temparature sensor fault) | 2022-09-17 | 2022-10-20 | 1894 | 912 | chemical / pharma | 1 | Replaced Discharge Temperature Sensor | null | closed | Replaced Discharge Temperature Sensor
2024-03-30 | Trade Links | Secunderabad | D | Varun Beverages Limited | null | KCX6 | 3394K2375 | 4385227369 | 2024-02-17 | 438522 | 2024-02-12 | key loose in c.shaft keyway | 2023-12-23 | 2024-02-02 | 80 | 750 | beverage / breweries | 2 | Key sliding free in crankshaft | null | closed | Key for c.shaft
2024-03-30 | Multivista Global Pvt Ltd | Chennai | D | Bala Ice Plant | Tamil Nadu | KCX4 | 3384K3069 | 4436447518 | 2024-03-27 | 443644 | 2024-03-05 | krmsdischarge temparature sensor broken | 2022-05-10 | 2023-02-02 | 4613 | 850 | ice plant | 8 | Temparature sensor broken | null | closed | Replaced temparature sensor
2024-03-30 | Geekay Pneumatic Pvt Ltd | null | D | Hic Abf Special Foods Pvt Ltd | Kerala | KCX72 | 3474K685 | 4466147514 | 2024-03-25 | 446614 | 2024-03-25 | discharge temparature sensor broken | 2023-08-22 | 2023-11-08 | 1332 | 818 | meat/fish process | 3 | Temparature sensor broken | null | closed | Replaced temparature sensor
2024-03-30 | Trade Links | Secunderabad | D | Sapala Organics P Ltd | Telangana | KCX1 | 3354K321 | 4440587476 | 2024-03-14 | 444058 | 2024-03-14 | shaft seal leakage | 2023-12-11 | 2024-02-23 | 45 | 750 | chemical / pharma | 2 | Shaft seal leak R22 Application | null | closed | Shaft seal assly
2024-04-24 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Gujrat State Energy Generation Ltd | null | KCX2 | 3364K2610 | 4451547532 | 2024-03-29 | 445154 | 2024-03-29 | shaft seal leakage | 2024-01-03 | 2024-03-29 | 24 | 770 | ac plant | 2 | Shaft Seal Leakage | null | closed | Replaced Shaftseal
2024-04-24 | Cool Comfort Private Limited | West Bengal | D | Mukti Firms Pvt Ltd | null | KCX4 | 338K#585 | 4480667563 | 2024-04-04 | 448066 | 2024-04-13 | abnormal noise | 2024-01-19 | 2024-03-14 | 199 | 850 | cold storage | 2 | Damage piston, Discharge valve aasly, Piston Ring set, Kit Delivery Valve | null | closed | Replaced piston, Discharge valve aasly, Piston Ring set, Kit Delivery Valve
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | New Kisan Cold Storage And Agro Industry | Uttar Pradesh | KC6 | 339K3746 | 4456547507 | 2024-03-23 | 445654 | 2024-03-23 | abnormal noise observed | 2023-12-21 | 2024-03-08 | 73 | 750 | cold storage | 3 | Piston Ring Wornout and cut marks on liner | null | closed | Replaced Cylinder Liner,piston ring set
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | RLSharma Sheetgrah | Uttar Pradesh | KC6 | 339K3648 | 4477227573 | 2024-04-08 | 447722 | 2024-04-18 | abnormal noise observed | 2022-11-22 | 2023-03-05 | 426 | 750 | cold storage | 3 | Piston Ring Wornout and cut marks on liner | null | closed | Replaced Cylinder Liner,piston,piston ring set
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Navaratana Cold Storage | null | KCX6 | 3394K2341 | 4466707513 | 2024-03-25 | 446670 | 2024-03-24 | ammonia pressure guage faulty | 2023-11-25 | 2024-03-24 | 2 | 750 | cold storage | 4 | Ammonia pressure guage faulty | null | closed | Rplaced Pressure Guage
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Ibrahim Cold Storage And Ice Factory | null | KCX4 | 3384K3542 | 4479267559 | 2024-04-03 | 447926 | 2024-04-03 | burn solenoid coil | 2023-12-27 | 2024-03-19 | 55 | 761 | cold storage | 3 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Sheetal Saksham Ice And Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2420 | 4447047558 | 2024-04-03 | 444704 | 2024-04-03 | burn solenoid coil | 2024-01-24 | 2024-04-03 | 4 | 750 | cold storage | 3 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Jeet Cold Storage & Ice Plant | null | KCX4 | 3384K3590 | 4414887571 | 2024-04-08 | 441488 | 2024-04-06 | burn solenoid coil | 2024-01-22 | 2024-04-06 | 14 | 750 | cold storage | 3 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | CP Foods | null | KCX3 | 3374K3356 | 4477347547 | 2024-04-01 | 447734 | 2024-04-01 | burn solenoid coil | 2024-01-08 | 2024-03-18 | 220 | 750 | cold storage | 3 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Atmaram Cold Storage | null | KC6 | 339K3759 | 4432527584 | 2024-04-10 | 443252 | 2024-04-09 | burn solenoid coil | 2024-01-09 | 2024-04-09 | 17 | 750 | cold storage | 3 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Dashrathpur Cold Storage Pvt Ltd | Uttar Pradesh | KC6 | 339K3771 | 4458207537 | 2024-03-30 | 445820 | 2024-03-19 | burn solenoid coil | 2024-01-23 | 2024-03-19 | 2 | 750 | cold storage | 2 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Sodhi Bodhi Farmer Producer Company Pvt Ltd | Haryana | KC3 | 337K4860 | 4376427533 | 2024-03-29 | 437642 | 2024-02-23 | burn solenoid coil | 2023-03-29 | 2024-02-23 | 45 | 746 | cold storage | 11 | Burn Solenoid Coil | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Rk Cold Storage Nad Allied Industry | Uttar Pradesh | KC4 | 338K5924 | 4473127527 | 2024-03-28 | 447312 | 2024-03-28 | burn solenoid coil | 2024-02-09 | 2024-03-28 | 4 | 750 | cold storage | 1 | Burn Solenoid Coil | null | closed | Burn Solenoid Coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Onkar Cold Storage | null | KC3 | 337K4858 | 4438247561 | 2024-04-04 | 443824 | 2024-04-12 | crack on elbow connector | 2023-11-25 | 2024-04-12 | 4 | 750 | cold storage | 5 | Crack on Female Elbow Connector | null | closed | Replaced Female Elbow Connector 3/8 BSP
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | New Kisan Cold Storage And Agro Industry | Uttar Pradesh | KC6 | 339K3746 | 4473007541 | 2024-04-01 | 447300 | 2024-03-31 | cut mark and blackish oil | 2023-12-21 | 2024-03-08 | 210 | 750 | cold storage | 3 | Cut Mark and Blackish Oil | null | closed | Replace Cylinder Liner, Piston and Piston ring Set
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Aditya Cold Storage | null | KC4 | 338K5853 | 4474587536 | 2024-03-30 | 447458 | 2024-03-29 | damage pressure guage and suction, discharge line vibration | 2023-10-30 | 2024-03-29 | 14 | 750 | cold storage | 5 | Damage pressure guage and Suction, Discharge line vibration | null | closed | Replace Pressure Guage
2024-04-24 | Parag Marketing Services | null | D | Konkan Ice & Cold Storage | Kokan | PCX2 | 3106K0189 | 4423507418 | 2024-03-01 | 442350 | 2024-03-01 | high oil consumption | 2022-11-15 | 2022-12-06 | 2500 | 1050 | cold storage | 1 | Oil Throw | null | closed | Replaced Piston ring Set
2024-04-24 | Cool Comfort Private Limited | West Bengal | D | Tarama Multi Purpose Cold Storage | null | KCX4 | 3384K3622 | 4475907540 | 2024-03-30 | 447590 | 2024-03-30 | hour meter not working | 2024-02-07 | 2024-03-30 | 4 | 850 | cold storage | 1 | Hour Meter not working | null | closed | Rplaced Hour Meter
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Madan Mohan Cold Storage | null | KC6 | 339K3659 | 4464727508 | 2024-03-23 | 446472 | 2024-03-22 | knocking / abnormal sound | 2022-12-28 | 2023-03-15 | 699 | 768 | cold storage | 3 | Knocking sound . | null | closed | Knocking sound .
2024-04-24 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Toor Cold Storage | null | KCX3 | 3374K3294 | 4474147535 | 2024-03-29 | 447414 | 2024-03-29 | loading unloading problem | 2023-11-17 | 2024-03-02 | 49 | 750 | cold storage | 4 | Solenoid Coil Not Working | null | closed | Replaced solenoid coil
2024-04-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Mahadev Enterprises | Uttar Pradesh | KC4 | 338K5932 | 4477167546 | 2024-04-01 | 447716 | 2024-04-01 | oil carry over | 2024-02-19 | 2024-03-17 | 302 | 750 | cold storage | 1 | Oil Carry Obver | null | closed | Replaced Piston ring Set
2024-04-24 | Trade Links | Secunderabad | D | Sri Geeta Dairy Products | null | KCX2 | 3364K2575 | 4456187506 | 2024-03-22 | 445618 | 2024-03-22 | discharge pressure adaptor m12 threeding damage | 2023-11-30 | 2024-03-22 | 2 | 750 | dairy / ice cream | 4 | Discharge Pressure adaptor M12 - Threeding Damage | null | closed | Replaced Adaptor and Discharge Pressure transduser
2024-04-24 | Parag Marketing Services | null | D | Indiaqo Foods Pvt Ltd | null | KCX72 | 3474K599 | 4468667332 | 2024-02-05 | 446866 | 2024-02-03 | shaft seal leakage | 2022-11-28 | 2023-08-25 | 574 | 800 | food processing | 10 | Shaft Seal Leakage | null | closed | Replaced Kit shaft seal oring
2024-04-24 | Geekay Pneumatic Pvt Ltd | null | D | Kumbarzha Ice Plant | null | KCX3 | 3374K2927 | 4448327474 | 2024-03-14 | 444832 | 2024-03-14 | shaft seal leakage | 2022-10-03 | 2023-03-16 | 6258 | 820 | ice plant | 6 | Shaft Seal Leakage | null | closed | Rplaced Stationary and rotary O ring
2024-04-24 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Navin Fluorine Internation Limited | Gujrat | KCX72 | 3474K594 | 4451567477 | 2024-03-14 | 445156 | 2024-03-14 | discharge valve leakage | 2022-11-30 | 2024-03-14 | 6 | 940 | others | 16 | Discharge Valve Leak | null | closed | Replaced Discharg Valve Assly
2024-04-24 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Organic Industries Pvt Ltd | null | KCX12 | 3415K058 | 4470727529 | 2024-03-28 | 447072 | 2024-03-28 | piston found crack | 2023-01-31 | 2023-02-22 | 2015 | 890 | others | 1 | Crack Piston | null | closed | Replaced Piston
2024-04-24 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Navin Fluorine Internation Limited | Gujrat | KCX9 | 3404K341 | 4332887272 | 2024-01-19 | 433288 | 2024-01-18 | over heating | 2023-08-05 | 2023-09-27 | 850 | 850 | chemical / pharma | 1 | Overheating | null | closed | Replaced Discharg Valve Assly
2024-04-30 | Cool Comfort Private Limited | West Bengal | D | A C Cold Storage | null | KCX6 | 3394K2349 | 4494947599 | 2024-04-16 | 449494 | 2024-04-27 | abnormal noise | 2023-12-08 | 2024-03-12 | 250 | 850 | cold storage | 5 | Delivery ring broken in 3 cylinder | null | closed | Replaced Piston, piston ring set, gudgeon pin, discharge valve assly
2024-04-30 | Cool Comfort Private Limited | West Bengal | D | Sethia Cold Storage | null | KCX6 | 3394K2397 | 4500727616 | 2024-04-19 | 450072 | 2024-04-26 | oil carry over | 2024-01-11 | 2024-02-22 | 559 | 850 | cold storage | 1 | Piston Ring Close gap increased | null | closed | Replaced Piston ring Set
2024-04-30 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Hanumant Cold Storage | Uttar Pradesh | KC6 | 338K5905 | 4475847597 | 2024-04-16 | 447584 | 2024-04-14 | solenoid coil burnt | 2024-01-18 | 2024-04-14 | 5 | 750 | cold storage | 3 | Solenoid Coil Burnt | null | closed | Replaced solenoid coil
2024-04-30 | Kalp Marketing | Gujrat | D | Mehsana Dist CoOp Producers Union Ltd | Mehsana Dist | KCX4 | 3384K3403 | 4485487583 | 2024-04-09 | 448548 | 2024-04-09 | high oil consumption | 2023-08-11 | 2023-09-28 | 2834 | 750 | dairy / ice cream | 1 | VLD Piston O-ring is flatten | null | closed | Replaced VLD Piston O Ring and VLD oring
2024-04-30 | Geekay Pneumatic Pvt Ltd | null | D | Kanjhangad Ice Plant | Kerala | KCX2 | 3364K2427 | 4470647522 | 2024-03-28 | 447064 | 2024-03-27 | abnormal noise | 2023-02-17 | 2023-06-15 | 3088 | 810 | ice plant | 4 | DV Step Mark cause this Sound | null | closed | Replaced Discharg Valve Assly, Piston Ring set
2024-04-30 | Trade Links | Secunderabad | D | Lakshmi Ganapthi Ice Factory | Andhra Pradesh | KCX6 | 3394K2328 | 4384607370 | 2024-02-17 | 438460 | 2024-02-16 | guage panal fitting leakage | 2023-11-20 | 2024-02-16 | 15 | 850 | ice plant | 3 | Guage Panal fitting leakage | null | closed | Replace unioin nut ID6, Light SS, Ferrule ID 6, Bulkhead Female connector M10, Male connector M6
2024-04-30 | Kalp Marketing | Gujrat | D | Shree Nidhi Export | null | KCX51 | 3454K224 | 4391567413 | 2024-02-29 | 439156 | 2024-02-29 | abnormal noise | 2023-05-20 | 2023-08-11 | 1138 | 990 | meat/fish process | 3 | Piston Ring Wornout and cut marks on liner | null | closed | Replaced cylinder liner,piston,piston ring set, needle roller bearing, spacer for needle roller bearing, bearing bush con rod, HP connecting rod with bolt, Thrust ring pump end side
2024-04-30 | Kalp Marketing | Gujrat | D | Shafi Marin | null | KCX72 | 3474K563 | 4484407578 | 2024-04-08 | 448440 | 2024-04-08 | discharge temp.sensor failure | 2022-07-29 | 2023-05-26 | null | 993 | meat/fish process | 10 | Thermister get disconnect from casing | null | closed | Replaced Discharge Temp. Sensor
2024-04-30 | Geekay Pneumatic Pvt Ltd | null | D | Nas Fisheries Pvt Ltd | null | KCX4 | 3384K3360 | 4466187510 | 2024-03-25 | 446618 | 2024-03-23 | kcx oil pump low oiltang broken | 2023-05-18 | 2024-03-23 | 17 | 850 | meat/fish process | 11 | High Vibration on Suction and Discharge Side | null | closed | Replaced Oil Pump Assly
2024-05-20 | Multivista Global Pvt Ltd | Gurgaon | D | Amma Cold Storage | Uttar Pradesh | KCX3 | 3374K3330 | 4502727622 | 2024-04-22 | 450272 | 2024-04-27 | abnormal noise | 2023-12-21 | 2024-03-13 | 512 | 750 | cold storage | 4 | Piston ring found worn out | null | closed | Replace piston ring set, cylider Liner
2024-05-20 | Cool Comfort Private Limited | West Bengal | D | Nabadwip Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3595 | 4518307660 | 2024-05-04 | 451830 | 2024-05-15 | excessive heat | 2024-01-23 | 2024-03-31 | 722 | 850 | cold storage | 3 | Discharge Valve Damage | null | closed | Replaced Delivery Valve
2024-05-20 | Multivista Global Pvt Ltd | Gurgaon | D | Om Namah Shivay Cold Storage | Uttar Pradesh | KC4 | 338K5910 | 4518167654 | 2024-05-03 | 451816 | 2024-05-03 | solenoid coil burnt | 2024-01-25 | 2024-05-03 | 18 | 750 | cold storage | 5 | Solenoid Coil Burnt | null | closed | Reolaced Solenoid Coil
2024-05-20 | Multivista Global Pvt Ltd | Gurgaon | D | Zansers Resorts Pvt Ltd | Haryana | KCX6 | 3394K2447 | 4484807634 | 2024-04-29 | 448480 | 2024-04-27 | hour meter not working | 2024-02-26 | 2024-04-27 | 0 | 768 | dairy / ice cream | 2 | Hour Meter shows 00 after 1 hr running | null | closed | Replaced Hour Meter
2024-05-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | New Valenkanni Enterprises | null | KCX4 | 3384K3249 | 4477787551 | 2024-04-02 | 447778 | 2024-04-02 | oil carry over | 2023-01-10 | 2023-04-13 | 5268 | 800 | ice plant | 4 | Step cut on liner and damaged gaskets | null | closed | Replaced Cylinder Liner, Set of Oring KCX4, Set of Gasket KCX4, ORV, Piston Ring Set
2024-05-20 | Kalp Marketing | Gujrat | D | Deepmala Marine Exports | Gujrat | KCX51 | 3454K229 | 4496927618 | 2024-04-20 | 449692 | 2024-04-20 | krms issue | 2023-07-17 | 2023-08-12 | 661 | 990 | meat/fish process | 1 | SMPS not showing 24 volt | null | closed | Replaced SMPS
2024-05-23 | Multivista Global Pvt Ltd | null | D | Amma Cold Storage | Uttar Pradesh | KCX3 | 3374K3330 | 4524567671 | 2024-05-08 | 452456 | 2024-05-18 | abnormal noise | 2023-12-21 | 2024-03-13 | 570 | 750 | cold storage | 4 | Piston ring found worn out | null | closed | Replaced Cylinder Liner, Piston, Piston Ring Set, Solenoid Coil
2024-05-23 | Trade Links | Secunderabad | D | Asvini Fisheries Pvt Ltd | Bhimavaran | KCX6 | 3394K2345 | email | 2024-04-10 | null | 2024-04-10 | abnormal noise | 2023-11-10 | 2024-02-20 | 769 | 750 | cold storage | 3 | Counter weight bolt broken | null | closed | Replaced Compressor
2024-05-23 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3602 | 4532667697 | 2024-05-16 | 453166 | 2024-05-16 | discharge valve leakage | 2024-01-27 | 2024-03-07 | 448 | 850 | cold storage | 2 | Dischaege Valve spring Boken | null | closed | Replaced Discharge Valve asly
2024-05-23 | Multivista Global Pvt Ltd | null | D | SS Cold Storage | Uttar Pradesh | KCX4 | 3384K3538 | 4463507572 | 2024-05-08 | 446350 | 2024-05-07 | knocking / abnormal sound | 2023-12-27 | 2024-03-07 | 25 | 768 | cold storage | 3 | Cylinder Liner worn out | null | closed | Replaced piston, piston ring set, pump element, bush connecting rod, kit delivery valve, gudgeo0n pin , Cylinder Liner
2024-05-23 | Multivista Global Pvt Ltd | null | D | Tirupati Cold Storage And Ice Factory | Uttar Pradesh | KC6 | 339K3741 | 4527387682 | 2024-05-09 | 452738 | 2024-05-17 | knocking / abnormal sound | 2023-12-15 | 2024-03-01 | 406 | 750 | cold storage | 3 | Damage due to emery particle | null | closed | Replaced Cylinder Liner, Piston, Piston Ring Set.
2024-05-23 | Cool Comfort Private Limited | West Bengal | D | Sethia Cold Storage | null | KCX6 | 3394K2397 | 4525547673 | 2024-05-09 | 452554 | 2024-05-09 | oil carry over | 2024-01-11 | 2024-02-22 | 618 | 850 | cold storage | 1 | Piston and Liner Damaged and Piston ring sett worn out | null | closed | Replaced Piston, Piston ring set, Cylinder liner
2024-05-23 | Cool Comfort Private Limited | West Bengal | D | Mahakal Agro Storage And Processing Unit | West Bengal | KCX4 | 3384K3662 | 4506747635 | 2024-04-29 | 450674 | 2024-04-29 | oil pump not working | 2024-03-12 | 2024-04-29 | 6.6 | 850 | cold storage | 1 | Oil Pump Gear Broken | null | closed | Replaced Oil Pump Element
2024-05-23 | Kalp Marketing | Gujrat | D | Radhakrishna Agri Cold Storage | Gujrat | KCX3 | 3374K3342 | 4516367658 | 2024-05-03 | 451636 | 2024-05-02 | pump manifold leakage | 2023-12-28 | 2024-03-26 | 167 | 640 | cold storage | 3 | Damaged Manifold oil filter housing | null | closed | Replaced Manifold oil filter housing
2024-05-23 | Multivista Global Pvt Ltd | null | D | Prasad Agro Industry | Uttar Pradesh | KC4 | 338K5873 | 4526547675 | 2024-05-09 | 452654 | 2024-05-08 | solenoid coil issue | 2023-12-12 | 2024-02-26 | 200 | 750 | cold storage | 3 | Solenoid Coil Burnt | null | closed | Replaced solenoid coil
2024-05-23 | Multivista Global Pvt Ltd | null | D | Sharvan Cold Storage And General Storage | null | KCX3 | 3374K3449 | 4531627712 | 2024-05-18 | 453162 | 2024-05-18 | stop valve leakage | 2024-04-13 | 2024-04-13 | 0 | 750 | cold storage | 1 | Welding Leakage of Stop Valve | null | closed | Replaced Stop Valve
2024-05-23 | Multivista Global Pvt Ltd | null | D | Meenakshi Dairy Products | Tamil Nadu | KCX2 | 3364K2618 | 4512407638 | 2024-04-29 | 451240 | 2024-04-29 | hour meter not working | 2024-01-11 | 2024-04-29 | 0 | 653 | dairy / ice cream | 4 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-05-23 | Multivista Global Pvt Ltd | null | D | Shree Shiv Dairy And Ice Factory | Uttar Pradesh | KCX1 | 3354K287 | 4517747653 | 2024-05-03 | 451774 | 2024-05-02 | oil lifting | 2023-06-24 | 2023-09-27 | 941 | 768 | dairy / ice cream | 2 | Found Leakage in ORV | null | closed | Replaced ORV
2024-05-23 | Geekay Pneumatic Pvt Ltd | null | D | Abad Exim Pvt Ltd | null | KCX2 | 3364K2641 | 4519547664 | 2024-05-07 | 451954 | 2024-05-06 | hour meter not working | 2024-02-22 | 2024-05-06 | 1 | 873 | ice plant | 1 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-05-23 | Cool Comfort Private Limited | West Bengal | D | ZA Sea Foods Pvt Ltd | null | KCX72 | 3474K744 | 4523167665 | 2024-05-07 | 452316 | 2024-05-07 | abnormal noise | 2024-01-31 | 2024-03-15 | 196 | 850 | meat/fish process | 3 | Cylinder Liner worn out and piston ring closed gap incresews | null | closed | Replaced Cylinder Liner, piston ring Set
2024-06-01 | Multivista Global Pvt Ltd | null | D | Raj Rani Cold Storage And Ice Plant | null | KC6 | 339K3691 | 4481067587 | 2024-04-10 | 448106 | 2024-04-18 | oil pressure trip | 2023-05-31 | 2023-10-08 | 228 | 750 | cold storage | 4 | Cut Mark on Oil Pump Plate | null | closed | Replaced Oil Pump Assly
2024-06-01 | Parag Marketing Services | null | D | Deccan Cold Storage Pvt Ltd | Bhor | KCX3 | 3374K3179 | 4504227693 | 2024-05-14 | 450422 | 2024-04-23 | shaft seal leakage | 2023-07-05 | 2023-08-08 | 3352 | 800 | cold storage | 1 | Shaft Seal Leakage | null | closed | Replaced Shaft Seal
2024-06-01 | Trade Links | Secunderabad | D | Sree Valliice Factory | null | KC3 | 337K4882 | 4493347598 | 2024-04-16 | 449334 | 2024-04-13 | hour meter not working | 2024-02-21 | 2024-04-13 | 6 | 700 | ice plant | 2 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-06-01 | Kalp Marketing | Gujrat | D | Sager Industry Co | Gujrat | KCX4 | 3384K3529 | 4513327659 | 2024-05-03 | 451332 | 2024-05-02 | oil carry over abnormal sound | 2023-12-22 | 2023-12-29 | 2284 | 770 | ice plant | 1 | Premature damage of Thrust ring, Cylinder Liner, Piston Ring Set | null | closed | Replaced Thrust ring, Piston ring set, cylinder liner
2024-06-01 | Parag Marketing Services | null | D | Finolex Industries Limited | Ratnagiri | KCX3 | 3374K2945 | 4478307642 | 2024-04-29 | 447830 | 2024-04-29 | shaft seal leakage | 2022-11-04 | 2023-12-06 | 3420 | 750 | chemical / pharma | 11 | Shaft Seal Leakage | null | closed | Replaced Shaft Seal
2024-06-11 | Cool Comfort Private Limited | West Bengal | D | Mahima Cold Storage | West Bengal | KCX4 | 3384K3596 | 4496127602 | 2024-04-17 | 449612 | 2024-04-30 | abnormal noisedelivery valve leak | 2024-01-23 | 2024-03-30 | 280 | 850 | cold storage | 2 | Delivery valve leakage and cylinder siezed | null | closed | Replaced Piston,Del. Valve,gudgeon pin, piston ring set
2024-06-11 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K2424 | 4533167714 | 2024-05-20 | 453316 | 2024-05-20 | delivery valve leakage | 2024-01-27 | 2024-03-07 | 456 | 850 | cold storage | 3 | Relaced piston,del valve,liner piston ring set | null | closed | Relaced piston,del valve,liner piston ring set
2024-06-11 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Shree Gayatri Deep Cold Storage | Gujrat | KCX3 | 3374K3176 | 4530347708 | 2024-05-17 | 453034 | 2024-05-17 | kcx oil pump purging | 2023-06-27 | 2023-07-14 | 1446 | 660 | cold storage | 1 | Replaced KCX oil pump assly | null | closed | Replaced KCX oil pump assly
2024-06-11 | Multivista Global Pvt Ltd | Chennai | D | S R Agro Pvt Ltd | Maharashtra | KCX4 | 3384K3488 | 4511127652 | 2024-05-02 | 451112 | 2024-04-27 | oil carry over & knocking sound | 2023-11-20 | 2024-02-23 | 493 | 750 | cold storage | 3 | Piston ring set & cylinder liner | null | closed | Replaced Piston,ring set & cylinder liner
2024-06-11 | Thailand | null | E | Thai Union | Thailand | KCX72 | 3474K782 | email | 2024-05-03 | null | 2024-05-03 | kcx manifold bolt broken | null | null | null | null | dairy / ice cream | null | null | null | closed | null
2024-06-11 | Multivista Global Pvt Ltd | null | D | Meenakshi Dairy Products | Tamil Nadu | KCX2 | 3364K2619 | 4512427643 | 2024-04-30 | 451242 | 2024-04-30 | pressure gauge malfunctioning | 2024-01-11 | 2024-04-30 | 2 | 653 | dairy / ice cream | 3 | Pressure gauge -760 to16 kg/cm2 error | null | closed | Replaced pressure gauge
2024-06-11 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Songadh Ice Factory | Gujrat | KCX2 | 3364K2613 | 4526967703 | 2024-05-16 | 452696 | 2024-05-16 | overheating of compressordel valve leakage | 2024-01-08 | 2024-02-01 | 133 | 700 | ice plant | 1 | Replaced kit del.valve | null | closed | Replaced kit del valve
2024-06-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Radhey Cold Storage | Haryana | KCX3 | 3374K3260 | 4552827748 | 2024-06-03 | 455282 | 2024-06-19 | kcx oil pump purging | 2023-10-23 | 2024-03-09 | 118 | 750 | cold storage | 5 | KCX oil pump purging required | null | closed | Replaced KCX oil pump assly
2024-06-24 | Geekay Pneumatic Pvt Ltd | Kerala | D | Hic Abf Special Foods Pvt Ltd | Kerala | KCX72 | 3474K685 | 4478787580 | 2024-04-08 | 447878 | 2024-04-08 | oil carry over & abnormal sound | 2023-08-22 | 2023-11-08 | 1515 | 818 | meat/fish process | 3 | Replaced Piston,Piston ring sets, | null | closed | Replaced Piston,Piston ring sets,
2024-06-30 | Cool Comfort Private Limited | West Bengal | D | Shitalpur Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3569 | 4564827784 | 2024-06-13 | 456482 | 2024-06-27 | abnormal noise | 2024-01-09 | 2024-03-10 | 656 | 850 | cold storage | 2 | Valve kit broken. | null | closed | Replaced valve kit
2024-06-30 | Cool Comfort Private Limited | West Bengal | D | Shitalpur Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K2396 | 4541227728 | 2024-05-27 | 454122 | 2024-06-08 | abnormal noisedel valve spring broken | 2024-01-09 | 2024-03-10 | 855 | 850 | cold storage | 2 | DV spring broken - Valve is not leak | null | closed | Replaced Piston, Piston ring set, Cylinder liner, Gudgeon Pin, Discharg Valve Assly
2024-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Srp Overseas | Mumbai | KCX3 | 3374K3121 | 4547287781 | 2024-06-12 | 454728 | 2024-06-14 | delivery valve leakage | 2023-02-26 | 2024-06-14 | 2 | 1000 | cold storage | 15 | All 3 delivery valves leakage. | null | closed | Replaced delivery valves 3 nos
2024-06-30 | Parag Marketing Services | null | D | Mapro Foods PvtLtd | null | KCX42 | 3444K369 | 4538867755 | 2024-06-04 | 453886 | 2024-05-21 | float valve of oil seprator is not working | 2022-12-27 | 2024-05-21 | 9 | 1000 | cold storage | 17 | Defective float valve assly | null | closed | Replace Float Valve od OIL SEP
2024-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Amma Cold Storage | Uttar Pradesh | KCX3 | 3374K3330 | 4538567718 | 2024-05-21 | 453856 | 2024-05-23 | oil carry over & abnormal sound | 2023-12-21 | 2024-03-13 | 595 | 750 | cold storage | 14 | Replaced Liner Cut & Piston Wornout | null | closed | Replaced Cylinder Liner, Piston, Piston Ring set
2024-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Amma Cold Storage | Uttar Pradesh | KCX3 | 3374K3330 | 4558767803 | 2024-06-18 | 455876 | 2024-06-18 | oil carry over & abnormal sound | 2023-12-21 | 2024-03-13 | 645 | 750 | cold storage | 15 | Piston ring wornout & liner cut problem repeatedly | null | closed | Replace cylinder Liner, Piston, Piston ring set, Bearing Bush big end con rod, Connecting rod with bolt, Bush connecting rod, Lock plate conrod & inter HSG bolt
2024-06-30 | Parag Marketing Services | null | D | Sairam Agro Export & Cold Storage | Latur | KCX2 | 3364K2507 | 4523247727 | 2024-05-25 | 452324 | 2024-05-08 | oil carry over & abnormal sound | 2023-08-12 | 2023-12-06 | 392 | 760 | cold storage | 3 | Step cut marks to liner & piston rings wornout. | null | closed | Replaed Cylinder liner, Piston, Piston Ring Set, Spring Cutain, liner Assly
2024-06-30 | Parag Marketing Services | null | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3540 | 4529047807 | 2024-06-18 | 452904 | 2024-06-11 | oil carry over & knocking sound | 2023-12-25 | 2024-05-07 | 143 | 770 | cold storage | 5 | Cylinder no.2,3 & 4 liners step cut marks , Piston rings wornout, Piston damaged. Welding slage found in cylinder. | null | closed | Replaced Liner3 , Piston rings 3 & Piston 2
2024-06-30 | Trade Links | Secunderabad | D | Krishndhu Ice Industries | null | KCX3 | 3374K3142 | 4518567663 | 2024-05-07 | 451856 | 2024-05-06 | oil lifting | 2023-03-29 | 2023-06-16 | 1649 | 800 | cold storage | 3 | Liner & piston ring worn out | null | closed | Replaced Cylinder Liner & Piston Ring Set
2024-06-30 | Multivista Global Pvt Ltd | Bulandshahar Uttar Pradesh | D | Mahadev Cold Storage | Deesa | KC4 | 338K5904 | 4526287674 | 2024-05-09 | 452628 | 2024-05-28 | oil pressure problem | 2024-01-17 | 2024-02-28 | 264.9 | 750 | cold storage | 1 | Cut mark on pump body from inside & gear | null | closed | Replace Oil Pump Assly
2024-06-30 | Parag Marketing Services | null | D | Bafna Cold Storage Pvt Ltd | Maharashtra | KCX2 | 3364K2388 | 4500227620 | 2024-04-22 | 450022 | 2024-04-20 | over heating | 2022-12-09 | 2023-03-18 | 567 | 800 | cold storage | 14 | Delivery valve leakage. | null | closed | Replaced delivery valve leakage.
2024-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Ma Luxmi Traders | Prayagraj | KC4 | 338K5889 | 4539047719 | 2024-05-22 | 453904 | 2024-05-22 | solenoid coil issue | 2023-12-30 | 2024-04-16 | 96 | 768 | cold storage | 14 | Solenoid Coil Burnt | null | closed | Replaced solenoid coil
2024-06-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Larsen & Toubro Ltd | Tamil Nadu | KCX6 | 3394K2483 | 4547387762 | 2024-06-06 | 454738 | 2024-06-20 | oil pump tang broken | 2024-05-18 | 2024-06-20 | 10 | 811 | construction | 1 | Oil pump tang broken 2 times in Zero hr. Analysis not mentioned in FSR. | null | closed | Replaced Pump assly.
2024-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Sangwan Milk Chilling Plant | Haryana | KCX2 | 3364K2655 | 4572887804 | 2024-06-18 | 457288 | 2024-06-18 | hour meter not working | 2024-03-12 | 2024-06-18 | 2.5 | 750 | dairy / ice cream | 3 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-06-30 | Kalp Marketing | Gujrat | D | Kanubhai Jajada | Gujrat | KCX2 | 3364K2560 | 4564347774 | 2024-06-11 | 456434 | 2024-06-10 | oil carry over | 2023-10-26 | 2024-02-01 | 532 | 874 | dairy / ice cream | 4 | 2 nos ORV Leakage | null | closed | Replaced ORV
2024-06-30 | Parag Marketing Services | null | D | Shrinivasa Milk & Milk Products | Sangli | KCX3 | 3374K3109 | 4562047765 | 2024-06-08 | 456204 | 2024-06-07 | oil pump purging | 2023-02-21 | 2023-06-27 | 4089 | 767 | dairy / ice cream | 4 | Air purging problem & thrust ring wornout. Detail analysis not mentioned. | null | closed | Replaced pump assly & thrust ring.
2024-06-30 | Parag Marketing Services | null | D | Sai Amrut Milk And Milk Products | Maharashtra | KCX2 | 3364K2578 | 4497127604 | 2024-04-10 | 449712 | 2024-04-17 | over heating | 2023-11-27 | 2024-01-04 | 1019 | 750 | dairy / ice cream | 2 | Cylinder no.1 overheating due to delivery valve leak. Liner piston seized. Delivery stroke limitor step cut mark. | null | closed | Replaced liner , piston , piston ring set , buffer spring , delivery valve assly & Gudgeon pin.
2024-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mannat Ice Industries | null | KCX4 | 3384K3401 | 4516887810 | 2024-06-18 | 451688 | 2024-06-02 | oil carry over | 2023-07-31 | 2024-01-14 | 2038 | 750 | ice plant | 6 | 9L per24 Hrs oil consumption & Defective Liner-4 Piston-2, Piston Ring Set-4, Gasket set & O-Ring set | null | closed | Replaced Piston Piston Ring Set, Cylinder Liner, set of Gasket, Set of Oring
2024-06-30 | Kalp Marketing | Gujrat | D | Shree Natraj Ice Factory | Gujrat | KCX4 | 3384K3293 | 4561387808 | 2024-06-18 | 456138 | 2024-06-18 | oil carry over | 2023-02-07 | 2023-04-25 | 2250 | 877 | ice plant | 3 | Oil Carry Over | null | closed | Replaced Cylinder Liner, piston ring Set
2024-06-30 | Gargi Engineering Enterprices Pvt Ltd | null | D | Suraj Cold Storage | Alibaug | KCX3 | 3374K3031 | 4513967780 | 2024-06-12 | 451396 | 2024-06-11 | oil carry over | 2022-12-31 | 2023-04-02 | 7319 | 750 | ice plant | 4 | Oil consumption 8L/24 Hr. Open oil throw observed. LP Cut in 1.5 is incorrect. | null | closed | Replaced piston rings 3 , Liners 2 & Piston 1
2024-06-30 | Kalp Marketing | Gujrat | D | S K Foods | Gujrat | KCX72 | 3474K666 | 4560707763 | 2024-06-06 | 456070 | 2024-06-06 | abnormal noise & shaft seal leakage | 2023-07-17 | 2023-08-28 | 3618 | 991 | meat/fish process | 1 | DV ring found broken, shaft seal mating face is damaged due to flattern O-Ring | null | closed | Replaced Shaft Seal Assly & Discharge Valve Assly
2024-06-30 | Kalp Marketing | Gujrat | D | S S International | null | KCX72 | 3374K665 | 4545227752 | 2024-06-03 | 454522 | 2024-06-01 | over heating | 2023-07-17 | 2023-08-14 | 3558 | 990 | meat/fish process | 1 | H.P cyl DV rig Broken | null | closed | Replaced Needle roller bearing, Spacer for needle roller bearing,gudgeon pin, piston,piston ring set, bearing bush big end con rod, discharge valve assly
2024-06-30 | Parag Marketing Services | null | D | Finolex Industries Limited | Urse, Pune | KCX6 | 3394K2195 | 4552387753 | 2024-06-04 | 455238 | 2024-06-03 | oil carry over | 2023-02-20 | 2023-09-30 | 4578 | 850 | others | 7 | 3 cylinders liner step cut mark | null | closed | Replaced liners 3 & Piston rings 3
2024-06-30 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX6 | 3394K2351 | 4530947696 | 2024-05-15 | 453094 | 2024-05-15 | over heating | 2023-12-08 | 2024-01-22 | 1225 | 771 | chemical / pharma | 2 | DV rings found Broken of cyl 1 & 3, | null | closed | Replace cylinder Liner, Piston, Piston ring set, Bearing Bush big end con rod, Discharge Valve Assly, Bush connecting rod & gudgeon Pin
2024-06-30 | Trade Links | Secunderabad | D | Salvo Explosive & Chemicals | Telangana | KCX2 | 3364K2518 | 4589607819 | 2024-06-22 | 458960 | 2024-06-21 | shaft seal leakage | 2023-08-29 | 2024-05-24 | 8 | 750 | chemical / pharma | 9 | R22 gas application - Repeated Shaft seal leakage | null | closed | Replaced shaft seal
2024-07-17 | Cool Comfort Private Limited | West Bengal | D | Gadang Cold Storage Llp | null | KCX4 | 3384K3359 | 4576247798 | 2024-06-17 | 457624 | 2024-06-29 | abnormal noisedel valve spring broken | 2024-01-06 | 2024-03-30 | 1005 | 850 | cold storage | 3 | DV spring broken | null | closed | Replaced valve kit
2024-07-17 | Cool Comfort Private Limited | West Bengal | D | Gadang Cold Storage Llp | null | KCX4 | 3384K3560 | 4623587852 | 2024-07-01 | 462358 | 2024-07-02 | abnormal noisedel valve spring broken | 2024-01-06 | 2024-03-30 | 1005 | 850 | cold storage | 3 | DV spring broken | null | closed | Replced valve kit
2024-07-17 | Cool Comfort Private Limited | West Bengal | D | Gadang Cold Storage Llp | null | KCX3 | 3374K3354 | 4623567849 | 2024-07-01 | 462356 | 2024-07-02 | abnormal noisedel valve spring broken | 2024-01-06 | 2024-03-30 | 475 | 850 | cold storage | 3 | DV spring broken | null | closed | Replaced valve kit
2024-07-17 | Cool Comfort Private Limited | West Bengal | D | S S Sea FoodsDigha | West Bengal | KCX72 | 3474K673 | 4604667827 | 2024-06-25 | 460466 | 2024-06-25 | abnormal noisedel valve kit broken | 2023-07-28 | 2023-09-16 | 1966 | 850 | meat/fish process | 2 | DV kit broken | null | closed | Replaced DV kit
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Dooars Kanya Cold Storage | West Bengal | KCX6 | 3394K2376 | 4626687855 | 2024-07-03 | 462668 | 2024-07-14 | abnormal noisecylinder liner worn out | 2023-12-25 | 2024-03-09 | 340 | 850 | cold storage | 3 | Cylinder Liner Worn out, Piston & Piston ring set Damage | null | closed | Replaced Cylinder Liner , Piston, Piston Ring set
2024-07-30 | Multivista Global Pvt Ltd | null | D | RLSharma Sheetgrah | Uttar Pradesh | KC4 | 338K5885 | 4623747862 | 2024-07-05 | 462374 | 2024-07-08 | abnormal noisecylinder liner worn out | 2023-12-23 | 2024-02-28 | 1128 | 750 | cold storage | 2 | Liner & Piston Ring Worn Out | null | closed | Replaced Cylinder Liner & Piston, Piston Ring, Discharge Valve Assly
2024-07-30 | Multivista Global Pvt Ltd | null | D | Shri Jay Prakash Cold Storage | null | KCX6 | 3394K2326 | 4576207825 | 2024-06-25 | 457620 | 2024-07-07 | abnormal noisecylinder liner worn out | 2023-11-16 | 2024-02-21 | 174 | 750 | cold storage | 3 | Piston & Liner Worn Out | null | closed | Replaced Cylinder Liner, Piston , Piston ring Set
2024-07-30 | Multivista Global Pvt Ltd | null | D | Tirupati Cold Storage & Ice Factory | null | KC6 | 339K3741 | 4566507777 | 2024-06-11 | 456650 | 2024-06-11 | abnormal noisecylinder liner worn out | 2023-12-15 | 2024-03-01 | 450 | 750 | cold storage | 3 | The problem of liner rubbing with sharp edge of the piston rings | null | closed | Replaced Cylinder Liner, Piston, Piston ring set
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Shri Bishnu Cold Storage | null | KCX4 | 3384K3467 | 4658887898 | 2024-07-15 | 465888 | 2024-07-18 | abnormal noisedel valve spring broken | 2023-10-31 | 2024-03-08 | 690 | 858 | cold storage | 5 | DV Spring Failure with Piston Marks | null | closed | Replaced Cylinder Liner, Piston, Piston ring set, Kit Delivery Valve
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Shri Bishnu Cold Storage | null | KCX3 | 3374K3272 | 4662687910 | 2024-07-18 | 466268 | 2024-07-19 | abnormal noisepiston ring set worn out | 2023-10-31 | 2024-03-08 | 691 | 850 | cold storage | 5 | Piston ring set worn out | null | closed | Replaced Piston Ring Set
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Shri Bishnu Cold Storage | null | KCX4 | 3384K3466 | 4662707912 | 2024-07-18 | 466270 | 2024-07-19 | cylinder overheating | 2023-10-31 | 2024-03-08 | 182 | 850 | cold storage | 5 | DV rings springs Broken | null | closed | Replaced Kit Delivery Valve
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3602 | 4653687890 | 2024-07-13 | 465368 | 2024-07-21 | cylinder overheating | 2024-01-27 | 2024-03-07 | 675 | 850 | cold storage | 2 | DV ring & Spring Broken | null | closed | Replaced Kit Del Valve, Discharge Valve Assly
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3600 | 4653707891 | 2024-07-13 | 465370 | 2024-07-21 | cylinder overheating | 2024-01-27 | 2024-03-30 | 763 | 990 | cold storage | 2 | DV ring & Spring Broken | null | closed | Replaced Kit Del Valve, Discharge Valve Assly
2024-07-30 | Cool Comfort Private Limited | West Bengal | D | Netal Charan Dey Cold Storage | null | KCX4 | 3384K3555 | 4651127883 | 2024-07-11 | 465112 | 2024-07-20 | cylinder overheating | 2024-01-02 | 2024-02-23 | 1488 | 850 | cold storage | 1 | Piston Ring cease, Piston damage, DV spring broken, | null | closed | Replaced Piston ring set, Piston, Kit delivery valve, Discharge valve assly
2024-07-30 | Multivista Global Pvt Ltd | null | D | Radha Rani Cold Storage | null | KCX6 | 3394K2402 | 4658587900 | 2024-07-15 | 465858 | 2024-07-16 | cylinder overheating | 2024-01-16 | 2024-03-23 | 1151 | 750 | cold storage | 2 | DV Spring ring found brokrn | null | closed | Replaced Discharged Valve Assly
2024-07-30 | Multivista Global Pvt Ltd | null | D | Vishwanath Bhagwati Cold Storage | null | KC6 | 339K3776 | 4636367863 | 2024-07-05 | 463636 | 2024-07-05 | kc oil pump low oil pressure | 2024-01-27 | 2024-04-08 | 803 | 750 | cold storage | 3 | Pump Damage | null | closed | Replaced Oil Pump Assly
2024-07-30 | Multivista Global Pvt Ltd | null | D | Sodhi Bodhi Farmer Producer Company Pvt Ltd | null | KC3 | 337K4860 | 4604407823 | 2024-06-24 | 460440 | 2024-07-21 | kcx oil pump low oil pressure | 2023-11-29 | 2024-02-23 | 1358 | 746 | cold storage | 3 | Pump Damage, Oil pressure not develop more than 1.5 kg/cm2 | null | closed | Replaced Oil Pump
2024-07-30 | Multivista Global Pvt Ltd | null | D | Shri Mahadev Enterprises | Uttar Pradesh | KC4 | 338K5932 | 4570887785 | 2024-06-13 | 457088 | 2024-06-13 | oil carry over | 2024-02-19 | 2024-03-17 | 920.6 | 750 | cold storage | 1 | Ring set found worn out, 3ltr oil lift in 24hrs | null | closed | Replaced Piston Ring Set, Cylinder Liner
2024-07-30 | Multivista Global Pvt Ltd | null | D | Jain Cold Staorage | Karnataka | KCX4 | 3384K3357 | 4549987772 | 2024-06-10 | 454998 | 2024-06-23 | oil carry over | 2024-05-04 | 2023-09-02 | 1635 | 750 | cold storage | 4 | Liner & Piston Ring Worn Out, Delivery Valve Leakage | null | closed | Replaced Cylinder Liner, Piston, Piston ring set, Kit Delivery Valve
2024-07-30 | Multivista Global Pvt Ltd | null | D | Jeet Cold Storage& Ice Plant | null | KCX6 | 3394K2412 | 4607267830 | 2024-06-25 | 460726 | 2024-06-25 | solenoid coil burnt | 2024-01-22 | 2024-04-06 | 50 | 750 | cold storage | 3 | Solenoid Coil Burnt | null | closed | Replaced solenoid coil
2024-07-30 | Multivista Global Pvt Ltd | null | D | Larsen & Toubro Ltd | Tamil Nadu | KCX6 | 3394K2483 | 4596687816 | 2024-06-21 | 459668 | 2024-06-21 | oil pressure not buildup | 2024-05-18 | 2024-06-20 | 10 | 811 | construction | 1 | Oil Pump element failure | null | closed | Replaced pump element oil pump
2024-07-30 | Multivista Global Pvt Ltd | null | D | Heritage Foods Ltd | null | KCX4 | 3384K3459 | 4662607915 | 2024-07-18 | 466260 | 2024-07-18 | krms display not working | 2023-10-27 | 2024-04-05 | 1291 | 824 | dairy / ice cream | 6 | KRMS Display not Working | null | closed | Replaced KRMS Touch Screen
2024-07-30 | Multivista Global Pvt Ltd | null | D | Gagan Dairy | Uttar Pradesh | KCX6 | 3394K2318 | 4552547747 | 2024-06-03 | 455254 | 2024-06-03 | discharge stop valve issue | 2023-10-25 | 2024-05-02 | 415 | 750 | ice plant | 6 | Flange is out Balance | null | closed | Replaced Stop Valve
2024-07-30 | Multivista Global Pvt Ltd | null | D | R V Ice Plant | null | KCX6 | 3394K2480 | 4586127843 | 2024-06-29 | 458612 | 2024-06-28 | leakage observed from tah8 valve | 2024-05-06 | 2024-06-28 | 14 | 783 | ice plant | 2 | Leakage observed from TAH8 | null | closed | Replaced Float Valve Assly oil SEP, TAH8 Valve Assly, Solenoid Valve, Extended Female Adaptor
2024-07-30 | Multivista Global Pvt Ltd | null | D | Katlego Foods India Pvt Ltd | Haryana | KCX72 | 3474K717 | 4546467737 | 2024-05-29 | 454646 | 2024-06-27 | shaft seal leakage | 2023-11-30 | 2024-05-07 | 67.8 | 750 | meat/fish process | 5 | Main Bearing Cut | null | closed | Replaced Bearing Bush Plane Flywheel End
2024-07-30 | Multivista Global Pvt Ltd | null | D | M G Pterochem Pvt Ltd | Haryana | KCX72 | 3474K576 | 4649187929 | 2024-07-22 | 464918 | 2024-07-22 | abnormal noisecylinder liner worn out | 2022-09-27 | 2023-06-06 | 3575 | 900 | chemical / pharma | 11 | Liner & Piston Worn out | null | closed | Replaced Cylinder Liner, Piston, Piston ring set
2024-07-31 | Parag Marketing Services | null | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3539 | email | 2024-07-27 | null | 2024-07-27 | connecting rod nut loose & step on del valve kit | 2023-12-26 | 2024-07-26 | 0 | 830 | cold storage | 7 | Connecting rod nut loose & step on del valve kit | null | closed | Delivery valve kit
2024-07-31 | Hss Solution Pvt Ltd | null | D | Bikaner Agro Food Industries Pvt Ltd | Rajastan | KCX2 | 3364K2566 | 4640127932 | 2024-07-23 | 464012 | 2024-07-23 | oil carry over | 2023-11-09 | 2024-05-30 | 167 | 767 | cold storage | 7 | Abnormal Sound | null | closed | Replaced Cylinder Liner, piston ring Set
2024-07-31 | Hss Solution Pvt Ltd | null | D | Shekhawati Chilling Plant | Rajastan | KCX4 | 3384K3684 | 4494507603 | 2024-04-18 | 449450 | 1900-01-09 | hour meter not working | 2024-03-30 | 2024-04-16 | null | 660 | dairy / ice cream | 1 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-07-31 | Hss Solution Pvt Ltd | null | D | Ajanta Dairy Milk & Foods Pvt Ltd | Uttar Pradesh | KCX3 | 3374K3383 | 4526027684 | 2024-05-10 | 452602 | 2024-05-09 | loading/unloding issue | 2024-01-25 | 2024-05-04 | 4 | 762 | dairy / ice cream | 4 | Solenoid Valve is not Working | null | closed | Replaced Solenoid Valve
2024-07-31 | Kalp Marketing | Gujrat | D | Mehsana Dist CoOp Producers Union Ltd | Mehsana Dist | KCX4 | 3384K3402 | 4586007813 | 2024-06-20 | 458600 | 2024-06-20 | oil carry over | 2023-08-05 | 2023-08-12 | 3601 | 750 | dairy / ice cream | 1 | Abnormal wear & tear of liner & piston ring set | null | closed | Replaced Cylinder Liner, piston ring Set
2024-07-31 | Kalp Marketing | Gujrat | D | Nestle India Ltd | null | KCX6 | 3394K2229 | 4616407848 | 2024-07-01 | 461640 | 2024-07-29 | oil carry over | 2023-03-29 | 2024-01-03 | 576 | 750 | food processing | 12 | VLD piston o-ring got flattern | null | closed | Replaced ORing VLD Piston, ORing VLD
2024-07-31 | Kalp Marketing | Gujrat | D | Nestle India Ltd | null | KCX6 | 3394K2232 | 4653847894 | 2024-07-15 | 465384 | 2024-07-14 | vibration issue | 2023-03-29 | 2024-01-03 | 502 | 750 | food processing | 12 | Vibration Issue | null | closed | Replaced Bearing Bush Plane Flywheel End, Bearing Bush Flange pump end
2024-07-31 | Trade Links | Secunderabad | D | Sri Siva Sai Industries | null | KCX4 | 3384K3429 | 4573447793 | 2024-06-14 | 457344 | 2024-06-13 | kcx oil pump tang broken | 2023-09-27 | 2024-01-12 | 2121 | 800 | ice plant | 4 | Oil Pump element tank broken | null | closed | Replaced pump element oil pump
2024-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Mannat Ice Industries | null | KCX4 | 3384K3400 | 4516867809 | 2024-06-18 | 451686 | 2024-06-02 | oil carry over | 2023-07-31 | 2024-01-14 | 1917 | 750 | ice plant | 6 | Oil Throw, Piston worn out, cylinder liner cut, | null | closed | Replaced Piston Ring Set, Piston, Cylinder Liner, Set of Gasket, Set of O Ring
2024-07-31 | Kirloskar South East Asia Co Ltd | Thailand | D | Kirloskar South East Asia Co Ltd | null | KCX12 | 3415K089 | email | 2024-07-11 | null | 2024-07-11 | manifold bolt broken | 2024-05-28 | 2024-07-11 | 0 | 750 | meat/fish process | 1 | Bolt broken M10 X 120 L | null | closed | Replaced bolts M10 X 120 L
2024-07-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | M/S Singhson C S | null | KCX31 | 3434K0256 | email | 2024-07-26 | null | 2024-07-26 | manifold bolt broken | 2024-07-24 | 2024-07-26 | 0 | 750 | meat/fish process | 1 | Bolt broken M10 X 120 L | null | closed | Replaced bolts M10 X 120 L
2024-07-31 | Trade Links | Secunderabad | D | Salvo Explosive & Chemicals | Telangana | KCX2 | 3364K2518 | 4558967769 | 2024-06-10 | 455896 | 2024-06-05 | shaft seal leakage | 2023-08-29 | 2024-05-24 | 4 | 750 | chemical / pharma | 9 | Multiple Shaft Seal Leakage | null | closed | Replaced Shaft Seal Assly
2024-08-22 | Multivista Global Pvt Ltd | null | D | Carlsberg India Pvt Ltd | Haryana | KCX6 | 3394K2304 | 4661867926 | 2024-07-22 | 466186 | 2024-07-23 | over heating | 2023-10-28 | 2023-12-30 | 1570 | 950 | beverage / breweries | 2 | Discharge Valve failure | null | closed | replaced Cylinder liner, Piston, Piston ring set, Discharge Valve asly, kit delivery Valve, Gudgeon pin, Buffer spring, Bush connecting rod
2024-08-22 | Multivista Global Pvt Ltd | null | D | Bhoop Singh Cold Storage | null | KC6 | 339K3780 | 4564867828 | 2024-06-25 | 456486 | 2024-07-31 | abnormal noise | 2024-01-31 | 2024-03-23 | 42 | 750 | cold storage | 2 | Liner rubbing due to sharp edge of piston ring | null | closed | replaced Cylinder liner, Piston, Piston Ring set, Bearing Bush con rod , Oil pump assly, lock plate conrod, Gudgeon pin
2024-08-22 | Multivista Global Pvt Ltd | null | D | Anabia Cold Storage & General Mills | Uttar Pradesh | KCX6 | 3394K2403 | 4607167831 | 2024-06-26 | 460716 | 2024-06-29 | abnormal noise | 2024-01-15 | 2024-02-29 | 1361 | 750 | cold storage | 2 | Discharge Valve failure | null | closed | replaced Cylinder liner, Piston, Piston ring set, Discharge Valve asly, kit delivery Valve, Gudgeon pin, Buffer spring, Bush connecting rod
2024-08-22 | Cool Comfort Private Limited | West Bengal | D | Gitadevi Cold Storage | West Bengal | KCX4 | 3384K3507 | 4662087914 | 2024-07-18 | 466208 | 2024-07-30 | abnormal noise | 2023-12-09 | 2024-03-09 | 490 | 850 | cold storage | 3 | Liner seize into piston, Piston ring set wornout | null | closed | Replaced Cylinder Liner, Piston Ring Set
2024-08-22 | Hss Solution Pvt Ltd | null | D | Bikaner Agro Food Industries Pvt Ltd | Rajastan | KCX2 | 3364K2568 | 4702447995 | 2024-08-05 | 470244 | null | abnormal noise | 2023-11-09 | 2024-05-30 | 345 | 768 | cold storage | 7 | Liner & Ring Set Worn Out | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Kalp Marketing | Gujrat | D | Mittal Cold Storage | null | KCX3 | 3374K3335 | 4688507977 | 2024-07-31 | 468850 | 2024-07-31 | high oil consumption | 2023-12-25 | 2024-02-08 | 933 | 767 | cold storage | 2 | Cut mark on cyl liner | null | closed | Replaced Cylinder Liner, Piston Ring Set
2024-08-22 | Kalp Marketing | Gujrat | D | Madhusdan Cool Stores | null | KCX3 | 3374K3441 | 4653867922 | 2024-07-20 | 465386 | 2024-07-15 | high oil consumption | 2024-03-27 | 2024-04-09 | 226 | 764 | cold storage | 1 | Cut mark on cyl liner | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Multivista Global Pvt Ltd | null | D | Sugauti Cold Storage | Uttar Pradesh | KCX3 | 3374K3271 | 4633367861 | 2024-07-05 | 463336 | 2024-07-10 | knocking / abnormal sound | 2023-10-27 | 2024-03-28 | 145 | 746 | cold storage | 5 | Liner rubbing due to sharp edge of piston ring | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Multivista Global Pvt Ltd | null | D | Mahadev Cold Storage | Uttar Pradesh | KC4 | 338K5904 | 4570927868 | 2024-07-08 | 457092 | 2024-07-08 | knocking / abnormal sound | 2024-01-17 | 2024-02-28 | 316 | 750 | cold storage | 2 | Liner rubbing due to sharp edge of piston ring | null | closed | Replaced Cylinder liner, Piston, Piston ring set, Connecting rod with bolt, Bush Connecting rod, Solenoid coil
2024-08-22 | Multivista Global Pvt Ltd | null | D | Navaratana Cold Storage | null | KCX6 | 3394K2341 | 4707888010 | 2024-08-08 | 470788 | 2024-08-08 | loading/unloding issue | 2023-11-25 | 2024-03-24 | 950 | 750 | cold storage | 4 | Solenoid Coil Burnt | null | closed | Replaced Solenoid Coil
2024-08-22 | Hss Solution Pvt Ltd | null | D | Bikaner Agro Food Industries Pvt Ltd | Rajastan | KCX2 | 3364K2566 | 4640127932 | 2024-07-23 | 464012 | 2024-08-06 | oil carry over | 2023-11-09 | 2024-05-30 | 193 | 767 | cold storage | 7 | Liner & Ring Set Worn Out | null | closed | Replaced Cylinder Liner, Piston Ring Set
2024-08-22 | Pragya Industrial Supply | null | D | Shivanandi Cold Storage Llp | null | KCX3 | 3374K3273 | 4549307802 | 2024-07-18 | 454930 | 2024-07-02 | oil differtial pressure | 2023-10-28 | 2024-01-18 | 70 | 750 | cold storage | 3 | Gear Housing, Piston assly, Bearing Bush big end wornout | null | closed | Replaced Pump element , Piston assly, Bearing Bush Big end con rod
2024-08-22 | Cool Comfort Private Limited | West Bengal | D | Ganag Cold Storage | null | KCX6 | 3394K2305 | 4629967857 | 2024-07-03 | 462996 | 2024-07-15 | oil lifting | 2023-10-30 | 2024-03-25 | 670 | 850 | cold storage | 5 | Cylinder liner worn out, Piston damage, Close gap high, Scratch mark on bearing Bush, DV spring broken | null | closed | replaced Cylinder liner, Piston, Piston Ring set, Bearing Bush con rod , Kit delivery valve
2024-08-22 | Multivista Global Pvt Ltd | null | D | Jitendra Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2389 | 4708948014 | 2024-08-09 | 470894 | null | oil lifting | 2023-12-30 | 2024-03-08 | 1628 | 771 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Multivista Global Pvt Ltd | null | D | HS Chandel Cold Storage | Uttar Pradesh | KCX4 | 3384K3527 | 4658847916 | 2024-07-18 | 465884 | 2024-07-29 | oil lifting | 2023-12-20 | 2024-03-01 | 1051 | 750 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Multivista Global Pvt Ltd | null | D | Singhal Cold Storage & General Mill | Uttar Pradesh | KC3 | 337K4859 | 4706048002 | 2024-08-08 | 470604 | 2024-08-21 | oil pressure problem | 2023-11-28 | 2024-02-22 | 637 | 750 | cold storage | 3 | Bush is stuckin grae & whole thing is moving in gousing | null | closed | Replaced Oil pump Assly
2024-08-22 | Cool Comfort Private Limited | West Bengal | D | Nabadwip Cold Storage Pvt Ltd | West Bengal | KCX6 | 3394K2414 | 4665647921 | 2024-07-20 | 466564 | 2024-07-20 | over heating | 2024-01-23 | 2024-03-31 | 204 | 850 | cold storage | 3 | DV spring broken | null | closed | Replaced DV kit
2024-08-22 | Multivista Global Pvt Ltd | null | D | Gmc Associates & Cold Storage | null | KC3 | 337K4875 | 4682707967 | 2024-07-29 | 468270 | 2024-07-30 | solenoid coil issue | 2024-02-09 | 2024-04-06 | 864 | 750 | cold storage | 2 | Coil taking very high temprature | null | closed | Replaced Solenoid Coil
2024-08-22 | Multivista Global Pvt Ltd | null | D | Gmc Associates & Cold Storage | null | KC4 | 338K5908 | 4682687966 | 2024-07-29 | 468268 | 2024-07-30 | solenoid coil issue | 2024-01-19 | 2024-04-06 | 19.4 | 750 | cold storage | 3 | Solenoid Coil issue | null | closed | Replaced Solenoid Coil
2024-08-22 | Multivista Global Pvt Ltd | null | D | Om Namah Shivay Cold Storage | Uttar Pradesh | KC3 | 337K4866 | 4688427998 | 2024-08-06 | 468842 | 2024-08-06 | solenoid coil issue | 2024-01-03 | 2024-08-06 | 20 | 750 | cold storage | 7 | Solenoid Coil Malfuction | null | closed | Replaced Solenoid Coil
2024-08-22 | Multivista Global Pvt Ltd | null | D | Larsen & Toubro Ltd | Tamil Nadu | KCX6 | 3394K2493 | 4671147942 | 2024-07-24 | 467114 | 2024-07-31 | crack in oil pimp body | 2024-06-12 | 2024-07-31 | 7 | 632 | construction | 1 | Crack in Oil Pimp Body | null | closed | Replaced Oil pump Assly
2024-08-22 | Trade Links | Secunderabad | D | Manju Traders | null | KCX2 | 3364K2662 | 466767876 | 2024-07-10 | 456676 | 2024-06-10 | hour meter not working | 2024-03-28 | 2024-06-10 | 5 | 750 | dairy / ice cream | 2 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-08-22 | Hss Solution Pvt Ltd | null | D | Ajanta Dairy Milk & Foods Pvt Ltd | Uttar Pradesh | KCX3 | 3374K3383 | 4526027684 | 2024-05-10 | 452602 | 2024-05-09 | loading/unloding issue | 2024-01-25 | 2024-05-04 | 4 | 762 | dairy / ice cream | 4 | Solenoid coil not working & tight fitting | null | closed | Replaced Solenoid Coil
2024-08-22 | Kalp Marketing | Gujrat | D | Kanubhai Jajada | Gujrat | KCX2 | 3364K2560 | 4706748011 | 2024-08-08 | 470674 | 2024-08-08 | oil carry over | 2023-10-26 | 2024-02-01 | 632 | 874 | dairy / ice cream | 3 | Piston Ring closed gap Incresed at higher side | null | closed | Replaced piston ring Set
2024-08-22 | Multivista Global Pvt Ltd | null | D | Anig Dairy | Uttar Pradesh | KC3 | 337K4890 | 4689007978 | 2024-08-01 | 468900 | 2024-08-14 | oil pressure problem | 2024-04-30 | 2024-07-30 | 4 | 750 | dairy / ice cream | 3 | Oil pump failed to buid desire pressutre | null | closed | Replaced Oil pump Assly
2024-08-22 | Trade Links | Secunderabad | D | Blue Earth Food Processing | null | KCX72 | 3374K693 | 4644947870 | 2024-07-08 | 464494 | 2024-07-08 | over heating | 2023-10-21 | 2024-01-24 | 1041 | 950 | food processing | 4 | Buffer Spring height Shrink, DV Leak | null | closed | Replaced Buffer Spring, delivery Valve Assly
2024-08-22 | Pragya Industrial Supply | null | D | Vasuki Ice Plant | null | KCX6 | 3394K2264 | 4670667946 | 2024-07-25 | 467066 | 2024-07-25 | abnormal noise | 2023-07-12 | 2023-08-21 | 3990 | 1000 | ice plant | 1 | Piston crack in center, Discharge sensor tip Broken | null | closed | Replaced Piston, Piston ring set, discharge temprature zsensor
2024-08-22 | Trade Links | Secunderabad | D | Vani Marines P Ltd | null | KCX4 | 3384K3654 | 4606887837 | 2024-06-26 | 460688 | 2024-06-26 | hour meter not working | 2024-02-29 | 2024-06-26 | 3 | 850 | ice plant | 4 | Hour Meter not working | null | closed | Replaced Hour Meter
2024-08-22 | Multivista Global Pvt Ltd | null | D | MNIce Plant | Tamil Nadu | KCX4 | 3384K3438 | 4699187997 | 2024-08-05 | 469918 | null | l.p cut out not functioning | 2023-09-29 | 2024-08-08 | 12 | 825.5 | ice plant | 11 | L.P cut out not functioning | null | closed | Replaced Pressure switch L.P
2024-08-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Dnyanjyot Ice Factory | null | KRC4 | 3206K005 | 4669507955 | 2024-07-27 | 466950 | 2024-07-30 | minor leakage from stop valve | 2024-02-27 | 2024-07-30 | 5 | 1480 | ice plant | 4 | Minor leakage from stop Valve | null | closed | Replaced Stop Valve
2024-08-22 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sonia Fisheries Pvt Ltd | null | KCX72 | 3474K762 | 4597047833 | 2024-06-26 | 459704 | 2024-06-24 | dv assly leakage | 2024-03-18 | 2024-05-21 | 60 | 950 | meat/fish process | 2 | Cylinder overheat, DV assly change temp comes under control | null | closed | Replaced Discharge Valve asly
2024-08-22 | Kalp Marketing | Gujrat | D | Shree Niddhi Export | null | KCX72 | 3474K650 | 4661367937 | 2024-07-23 | 466136 | 2024-07-20 | high oil consumption | 2023-05-20 | 2023-08-11 | 1605 | 990 | meat/fish process | 3 | Cut mark on cyl liner 4 | null | closed | Replaced Cylinder Liner, Piston Ring Set
2024-08-22 | Trade Links | Secunderabad | D | Seasaga Enterprices | Andhra Pradesh | KCX3 | 3374K3464 | 4671067956 | 2024-07-27 | 467106 | 2024-07-27 | oil pressure problem | 2024-06-03 | 2024-07-02 | 7 | 750 | others | 1 | Oil Element Tang Broken | null | closed | replaced Pump Element oil pump
2024-08-22 | Multivista Global Pvt Ltd | null | D | MG Pterochem Pvt Ltd | null | KCX72 | 3474K576 | 4698907988 | 2024-08-04 | 469890 | 2024-08-10 | abnormal noise | 2022-09-27 | 2023-06-06 | 3641 | 900 | chemical / pharma | 9 | Liner rubbing due to sharp edge of piston ring | null | closed | replaced Piston ring, Cylindre liner, Piston
2024-08-22 | Trade Links | Secunderabad | D | Luc4U Eximsky | null | KCX3 | 3374K3410 | 4631187889 | 2024-07-13 | 463118 | 2024-07-13 | low oil pressure | 2024-02-21 | 2024-06-22 | 91 | 850 | chemical / pharma | 5 | Shaft Seal Leakage | null | closed | replaced Shaft Seal Assly
2024-08-22 | Trade Links | Secunderabad | D | Srinija Drug Pltd | null | KCX2 | 3364K2659 | 4578627841 | 2024-06-27 | 457862 | 2024-06-27 | shaft seal leakage | 2024-03-22 | 2024-06-05 | 27 | 600 | chemical / pharma | 3 | repeated shaft seal leakage | null | closed | replaced shaft seal aasly with viton oring
2024-08-22 | Trade Links | Secunderabad | D | Salvo Explosive & Chemicals | Telangana | KCX2 | 3364K2518 | 4653967927 | 2024-07-22 | 465396 | 2024-07-22 | shaft seal leakage | 2023-08-29 | 2024-05-24 | 167 | 750 | chemical / pharma | 9 | Shaft Seal Leakage | null | closed | replaced Shaft eal, ORing stationary, oring Rotary
2024-08-22 | Trade Links | Secunderabad | D | Sapla Organic Pvt Ltd | null | KCX1 | 3354K321 | 4677407976 | 2024-07-31 | 467740 | 2024-07-31 | shaft seal leakage | 2023-12-11 | 2024-02-23 | 1500 | 750 | chemical / pharma | 3 | Shaft Seal Leakage | null | closed | replaced Shaft Seal Assly
2024-08-31 | Cool Comfort Private Limited | West Bengal | D | Nefa Breweries PvtLtd | Arunachal Pradesh | KCX6 | 3394K2488 | 4705108003 | 2024-08-06 | 470510 | 2024-08-19 | oil lifting | 2024-05-28 | 2024-07-11 | 305 | 850 | beverage / breweries | 1 | Liner CEASED INTO THE PISTON, Liner step formation and piston ring wear out Piston WORN OUT | null | closed | Replaced PISTON RING SET KC/KCX, CYLINDER LINER KC/KCX
2024-08-31 | Multivista Global Pvt Ltd | Gurgaon | D | RLSharma Sheetgrah | Uttar Pradesh | KC6 | 339K3648 | 4739308067 | 2024-08-26 | 473930 | 2024-08-26 | abnormal noise | 2022-11-22 | 2023-03-05 | 665.4 | 750 | cold storage | 4 | New B liner worn out within 8 hours, The problem of liner rubbing due to sharp edges of the piston rings oc curred | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX, PISTON RING SET KC/KCX, OIL PUMP ASSEMBLY KC, BEARING BUSH BIG END CON ROD KC/KCX, BEARING BUSH DRIVE END KC BEARING BUSH PUMP END KC, BEARING INTER. HALF KC/KCX.
2024-08-31 | Kalp Marketing | Gujrat | D | Ronak Agro Foods | Gujrat | KCX3 | 3374K3234 | 4684807972 | 2024-07-30 | 468480 | 2024-07-30 | knocking / abnormal sound | 2023-09-25 | 2024-03-05 | 1262 | 767 | cold storage | 6 | Ring Cut mark on Liner, Damage Piston, | null | closed | Replaced Cylinder liner, Piston
2024-08-31 | Trade Links | Secunderabad | D | The Krishna Dairy Milk Union Co-Operative Society | Andhra Pradesh | KCX9 | 3404K323 | 4684828005 | 2024-08-07 | 468482 | 2024-08-05 | sensor error issue | 2023-02-24 | 2023-11-29 | 2528 | 800 | dairy / ice cream | 9 | cables for suction & discharge , during visit observer that malfunctioning of suction & discharge pressure while operating of of comp. The control also malfunctioning & Rs485 J11 part BMS 2 port is not working. | null | closed | Replaced PRESSURE SENSOR CABLE WITH CONNECTOR, 12 MTR LENGTH, ONTROLLER BOARD pCOOEM+
2024-08-31 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2321 | 4648947878 | 2024-07-10 | 464894 | 2024-07-22 | abnormal noise in single piston | 2023-10-26 | 2024-03-14 | 396 | 800 | food processing | 5 | Piston sized, Linner was sized so replaces it, Discharge valve assly was broken, Linner was sized | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, LEVER CYLINDER LINER KC/KCX, GUDGEON PIN KC/KCX, DISCHARGE VALVE ASSEMBLY KCX, CYLINDER LINER KC/KCX
2024-08-31 | Kalp Marketing | Gujrat | D | Deepvijay Ice Factory | Gujrat | KCX4 | 3384K3682 | 4724708046 | 2024-08-20 | 472470 | 2024-08-31 | oil carry over | 2024-03-27 | 2024-08-11 | 325 | 880 | ice plant | 5 | Ring Cut mark on Liner, Damage Piston, | null | closed | Replaced Cylinder liner, Piston
2024-08-31 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3498 | 4624487860 | 2024-07-05 | 462448 | 2024-07-04 | oil lifting | 2023-11-24 | 2024-03-06 | 2156 | 800 | ice plant | 4 | Oil lifting | null | closed | Replaced DISCHARGE VALVE ASSEMBLY KCX
2024-08-31 | Kalp Marketing | Gujrat | D | Shree Niddhi Export | Gujrat | KCX72 | 3474K651 | 4662987938 | 2024-07-23 | 466298 | 2024-07-20 | high oil consumption | 2023-05-20 | 2023-08-11 | 1590 | 990 | meat/fish process | 3 | Light Leakage at pisto Ring | null | closed | replaced Piston ring set
2024-08-31 | Kalp Marketing | Gujrat | D | Winsor World Exports | Gujrat | KCX72 | 3474K802 | 4731388047 | 2024-08-21 | 473138 | 2024-09-01 | oil pressure problem | 2024-07-20 | 2024-08-14 | 2 | 990 | meat/fish process | 1 | The tang of pump element found broken | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2024-09-20 | Cool Comfort Private Limited | West Bengal | D | Goswami Agro Storage Pvt Ltd | null | KCX4 | 3384K3522 | 4730468051 | 2024-08-22 | 473046 | 2024-08-22 | abnormal noise | 2023-12-15 | 2024-03-22 | 756 | 850 | cold storage | 4 | Liner Ceased, Piston Damage, Piston ring worn out, Solenoid valve leakage | null | closed | Replaced Liner, Piston, Piston Ring Set, Solenoid Valve
2024-09-20 | Kalp Marketing | Gujrat | D | Radhakrishna Agri Cold Storage | Gujrat | KCX3 | 3374K3342 | 4705148007 | 2024-08-08 | 470514 | 2024-08-08 | abnormal noise | 2023-12-28 | 2024-03-26 | 487 | 640 | cold storage | 3 | Piston Ring & Liner Worn out | null | closed | Replaced Liner & Piston Ring SET
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Mahadev Cold Storage | Uttar Pradesh | KC3 | 337K4872 | 4733128053 | 2024-08-22 | 473312 | 2024-08-22 | abnormal noise | 2024-01-17 | 2024-02-28 | 1231 | 750 | cold storage | 1 | Liner rubbing due to sharp edge of piston ring | null | closed | Replaced Piston, Piston Ring Set , Liner
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | RLSharma Sheetgrah | Uttar Pradesh | KC6 | 339K3648 | 4653927902 | 2024-07-16 | 465392 | 2024-08-26 | abnormal noise | 2022-11-22 | 2023-03-05 | 665,4 | 750 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | Replace Cylinder Liner, Piston, Piston Ring Set, Thurst Ring Bearing Cover, Lock Plate Con Rod& Inner HSG Bolt
2024-09-20 | Model Pneumatic Co | Punjab | D | Khalsa Farm Cold Storage | Punjab | KCX6 | 3394K2075 | 4747168095 | 2024-09-02 | 474716 | 2024-09-02 | abnormal noise | 2022-11-01 | 2023-03-21 | 1664 | 750 | cold storage | 16 | Cyl no. 4 liner & piston rings wornout | null | closed | Replaced Liner & Piston ring set1
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | S S Yadav Old Storage | Uttar Pradesh | KC4 | 338K5870 | 4744948082 | 2024-08-29 | 474494 | 2024-08-29 | high oil carryover | 2023-11-30 | 2024-03-13 | 1856 | 768 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | Replaced Cylinder Liner & Piston
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Jitendra Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2389 | 4760728113 | 2024-09-05 | 476072 | 2024-09-05 | high oil carryover | 2023-12-30 | 2024-03-08 | 1869 | 771 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | Replaced Cylinder Liner & Piston
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Saurikh City Cold Storage | Uttar Pradesh | KC6 | 339K3710 | 4768448119 | 2024-09-09 | 476844 | 2024-09-09 | high oil carryover | 2023-10-10 | 2024-02-28 | 2012 | 759 | cold storage | 4 | All liner , Piston rings wornout. | null | closed | Replaced Liner6, Piston2 & Piston ring set6
2024-09-20 | Pragya Industrial Supply | null | D | Jain Cold Staorage | Karnataka | KCX3 | 3374K3337 | 4686827985 | 2024-08-02 | 468682 | 2024-08-02 | high oil carryover | 2023-12-27 | 2024-04-16 | 535 | 750 | cold storage | 7 | Liner & piston rings wornout | null | closed | Replaced Liners 3 & Piston rings 2
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Shivsharan Sheetalaya | Uttar Pradesh | KCX4 | 3384K3532 | 4748848094 | 2024-08-30 | 474884 | 2024-09-16 | knocking / abnormal sound | 2023-12-25 | 2024-03-23 | 1793 | 750 | cold storage | 3 | Liner rubbing due to sharp edge of piston ring | null | closed | Replaced Piston, Piston Ring Set
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Om Agro Cold Storage | Uttar Pradesh | KCX4 | 3384K3589 | 4724968039 | 2024-08-16 | 472496 | 2024-08-16 | knocking / abnormal sound | 2024-01-22 | 2024-06-13 | 171 | 900 | cold storage | 5 | Blakish Oil, New Batch Liner & Piston Worn Out | null | closed | Replaced Liner, Piston, Piston Ring Set
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Laxmi Sheetalaya | Uttar Pradesh | KCX4 | 3384K3516 | 4739028063 | 2024-08-26 | 473902 | 2024-08-26 | knocking / abnormal sound | 2023-12-12 | 2024-02-18 | 1294 | 768 | cold storage | 3 | Oil Got Blakiish | null | closed | Replaced Piston, Piston ring set
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Banke Bihari Sheetalaya | Uttar Pradesh | KC6 | 339K3757 | 4738928069 | 2024-08-26 | 473892 | 2024-09-20 | knocking / abnormal sound | 2023-12-20 | 2024-03-07 | 1702 | 771 | cold storage | 4 | Delivery valve ring spring broken , liner , piston , piston ring damaged. | null | closed | Replacedv delivery valve , liner , piston , piston ring damaged.
2024-09-20 | Multivista Global Pvt Ltd | Uttar Pradesh | D | Shri Shyam Lakshmi Cold Storage | Uttar Pradesh | KCX4 | 3384K3616 | 4734788085 | 2024-08-30 | 473478 | 2024-09-17 | knocking / abnormal sound | 2024-02-01 | 2024-03-15 | 2023 | 768 | cold storage | 1 | Delivery valve spring broken and liner rubbing. | null | closed | Replaced Liner 2 , piston 1, Piston ring set 2,Delivery valve 1 and kit 1
2024-09-20 | Cool Comfort Private Limited | West Bengal | D | Dooars Kanya Cold Storage | West Bengal | KCX4 | 3384K3535 | 4768848120 | 2024-09-09 | 476884 | 2024-09-09 | over heating | 2023-12-25 | 2024-03-09 | 1594 | 850 | cold storage | 3 | Cylinder no.3 seized due to delivery valve ring spring broken. | null | closed | Replaced piston , Gudgeon pin, piston ring set , kit delivery valve & discharge valve assly1
2024-09-20 | Multivista Global Pvt Ltd | Uttar Pradesh | D | Banker Cold Storage & Agro | Uttar Pradesh | KC6 | 339K3739 | 4734608055 | 2024-08-23 | 473460 | 2024-08-23 | over heating | 2023-12-15 | 2024-03-04 | 1259 | 750 | cold storage | 3 | Delivery valve spring broken CYL.NO.5 | null | closed | Replaced delivery valve assembly
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Radha Cold Storage | Uttar Pradesh | KCX6 | 3394K2402 | 4706588009 | 2024-01-16 | 470658 | 2024-08-12 | over heating | 2024-01-16 | 2024-03-23 | 1333 | 750 | cold storage | 2 | overheating due to delivery valve ring spring broken. | null | closed | Replaced kit 4 , Delivery valve 1, piston ring set 1 & Piston 1
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Gmc Associates & Cold Storage | Uttar Pradesh | KC4 | 338K5907 | 4682747968 | 2024-07-29 | 468274 | 2024-08-20 | pressure guage leak | 2024-01-19 | 2024-04-06 | 2 | 750 | cold storage | 3 | Dicharge pressure gauge glycerine leak. | null | closed | Replaced Ammonia Pressure Guage 25Kg/cm2.
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | P N D Cold Storage | Uttar Pradesh | KC4 | 338K5858 | 4738908068 | 2024-08-26 | 473890 | 2024-08-26 | solenoid coil burnt | 2023-11-09 | 2024-03-28 | 3 | 750 | cold storage | 4 | solenoid valve coil burnt & Hour meter not working. | null | closed | Replaced solenoid valve coil & Hour meter
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Ram Cold & Agro Industries | null | KC6 | 339K3770 | 4757868109 | 2024-09-04 | 475786 | 2024-08-16 | solenoid coil issue | 2024-01-22 | 2024-03-18 | 150 | 750 | cold storage | 3 | Solenoid Coil Burnt | null | closed | Replaced Solenoid Valve Coil
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Surendra Babu Cold Storage | Uttar Pradesh | KCX4 | 3384K3599 | 4742928072 | 2024-08-27 | 474292 | 2024-09-15 | solenoid valve plunger leak | 2024-01-24 | 2024-03-01 | 904 | 750 | cold storage | 2 | Hole in solenoid Plunger - Solenoid Malfunction | null | closed | Replaced Solenoid Valve
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Parag Dairy | Uttar Pradesh | KCX8 | 3394K2489 | 4726268042 | 2024-08-17 | 472626 | 2024-09-17 | high oil carryover | 2024-05-28 | 2024-07-01 | 754 | 750 | dairy / ice cream | 2 | Piston Ringg & Liner Worn Out | null | closed | Replaced Piston, Piston Ring Set , Liner
2024-09-20 | Multivista Global Pvt Ltd | Uttar Pradesh | D | Deshrani Milk And Chilling Centre | Uttar Pradesh | KCX3 | 3374K3105 | 4735688084 | 2024-08-29 | 473568 | 2024-08-29 | high oil carryover | 2023-02-19 | 2023-12-04 | 1816 | 750 | dairy / ice cream | 10 | Piston rings wornout- 3nos. | null | closed | Replaced piston ring sets 3 nos
2024-09-20 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Aneja Food Products | J&K | KCX4 | 3384K3313 | 4674228100 | 2024-09-03 | 467422 | 2024-07-25 | oil pump issue | 2023-02-26 | 2023-10-19 | 479 | 826 | dairy / ice cream | 8 | Purging problem. | null | closed | Replaced pump assembly
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Sood Frozen Foods | Uttarakhand | KCX6 | 3394K2288 | 4690827984 | 2024-08-02 | 469082 | 2024-08-02 | abnormal noise | 2023-09-20 | 2024-01-07 | 1073 | 750 | food processing | 8 | Liner & piston rings wornout | null | closed | Replaced Liners 4, Piston 4 & Piston rings 6
2024-09-20 | Kalp Marketing | Gujrat | D | Nestle India Ltd | null | KCX6 | 3394K2234 | 4671267939 | 2024-07-23 | 467126 | 2024-07-23 | high oil carryover | 2023-03-29 | 2024-03-19 | 305 | 750 | food processing | 12 | Premature Wear & Tear of Piston, Liner O-ring VLD & O-ring VLD Piston | null | closed | Replaced Piston, Liner Oring VLD Pistion & Orong VLD
2024-09-20 | Kalp Marketing | Gujrat | D | Nestle India Ltd | null | KCX6 | 3394K2228 | 4671287940 | 2024-07-23 | 467128 | 2024-07-23 | high oil carryover | 2023-03-29 | 2024-03-19 | null | 750 | food processing | 12 | Premature Wear & Tear of Piston, Liner O-ring VLD & O-ring VLD Piston | null | closed | Replaced Piston, Liner Oring VLD Pistion & Orong VLD
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Sood Frozen Foods | Uttarakhand | KCX72 | 3474K681 | 4690587983 | 2024-08-02 | 469058 | 2024-08-17 | high oil carryover | 2023-09-20 | 2024-01-07 | 1088 | 850 | food processing | 4 | Piston Ring Worn Out | null | closed | Replaced Piston Ring
2024-09-20 | Multivista Global Pvt Ltd | Gurgaon | D | Sood Frozen Foods | Uttarakhand | KCX63 | 3364K192 | 4726968043 | 2024-08-17 | 472696 | 2024-08-23 | high oil carryover | 2023-09-20 | 2024-01-07 | 1753 | 850 | food processing | 4 | Piston Ring Worn Out | null | closed | Replaced Piston Ring
2024-09-20 | Trade Links | null | D | Sri Vishnu Smitha Ice Factory | Andhra Pradesh | KCX4 | 3384K3578 | 4546967854 | 2024-07-03 | 454696 | 2024-07-02 | abnormal noise | 2024-01-15 | 2024-04-06 | 1596 | 850 | ice plant | 3 | Shaft Seal & Piston Ring Worn OUT | null | closed | Replaced Lever, Piston Ring Set & Shaft Seal assly
2024-09-20 | Robin Refrigeration Works | null | D | Maa Sarala Ice Factory | null | KCX2 | 3364K2591 | 4698688019 | 2024-08-10 | 469868 | 2024-08-10 | high oil carry over & shaft seal lekage | 2023-12-12 | 2024-03-23 | 850 | 887 | ice plant | 4 | Shaft Seal Leakge Might be because of filter chocked | null | closed | Replaced Gsket Suction Staner, Gasket Head Cover & Piston Ring Set
2024-09-20 | Robin Refrigeration Works | null | D | Maa Sarala Ice Factory | Odisha | KCX2 | 3364K2590 | 4698648018 | 2024-08-10 | 469864 | 2024-08-10 | high oil carryover | 2023-12-12 | 2024-03-23 | 1656 | 880 | ice plant | 4 | High Closed GapINPiston Ring | null | closed | Replaced Liner, Piston, Piston Ring set, ORV, Gsket of Stainer & Head Covet
2024-09-20 | Geekay Pneumatic Pvt Ltd | null | D | Malabar Enterprises | Kerala | KCX4 | 3384K3510 | 4665047930 | 2024-07-22 | 466504 | 2024-07-22 | high oil carryover | 2023-12-11 | 2024-01-08 | 1876 | 825 | ice plant | 1 | oil Carry over | null | closed | Replaced Piston Ring Set & Liner
2024-09-20 | Geekay Pneumatic Pvt Ltd | null | D | Excel Ice Plant | Kerala | KCX2 | 3364K2461 | 4662867971 | 2024-07-30 | 466286 | 2024-07-30 | high oil carryover | 2023-04-22 | 2023-08-02 | 3965 | 760 | ice plant | 3 | Piston, Piston Ring Set, Liner wornout | null | closed | Replaced Piston Piston Ring Set, Liner & Safety Plate for Gudgeon Pin
2024-09-20 | Trade Links | null | D | Sri Lakshmi Jyoti Ice Fatory | Andhra Pradesh | KCX4 | 3384K3547 | 4502827670 | 2024-05-08 | 450282 | 2024-05-08 | high oil carryover | 2023-12-28 | 2024-02-10 | 19708 | 880 | ice plant | 2 | iner Piston Ring Worn Out | null | closed | Replaced Cylinder Liner Piston Ring Set
2024-09-20 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Fair Export Pvt Ltd | Punjab | KCX4 | 3384K3541 | 4692787982 | 2024-08-02 | 469278 | 2024-08-02 | abnormal noise | 2023-12-26 | 2024-03-03 | 1034 | 934 | meat/fish process | 3 | Gudgeon pin, Piston, Piston Ring Set, liner, Discharege Valve Damage | null | closed | Replaced Piston Liner Piston Ring Set, Gudgeon pin, DischargeValve assly
2024-09-20 | Geekay Pneumatic Pvt Ltd | null | D | Abm Marine Products | Kerala | KCX42 | 3444K340 | 4436687726 | 2024-05-24 | 443668 | 2024-12-20 | high oil carryover | 2022-03-21 | 2023-12-20 | 1049 | 930 | meat/fish process | 21 | High Discharge Temp | null | closed | Replace Cylinder Liner, Piston, Piston Ring Set, Lock Plate Con Rod& Inner HSG Bolt
2024-09-20 | Gargi Engineering Enterprices Pvt Ltd | null | D | Seasaga Enterprices | Mumbai | KCX72 | 3474K654 | 4589407872 | 2024-07-09 | 458940 | 2024-07-06 | high oil carryover | 2023-06-16 | 2023-08-14 | 1711 | 985 | meat/fish process | 3 | CC rate 18ml/cyl/hr. All liners and piston rings wornout. | null | closed | Replaced liners9, Piston 9, Piston rings 9 Gudgeon pin3 , Bearings & Thrust ring.
2024-09-20 | Trade Links | null | D | Srini Pharmaceuticals P Ltd | null | KCX42 | 3444K475 | 4702388013 | 2024-08-09 | 470238 | 2024-08-06 | pressure guage not working | 2024-08-02 | 2024-08-06 | 18 | 750 | chemical / pharma | 1 | Pressure Guage not working. Pointer not moved. | null | closed | Replaced Pressure Guage 16 Kg/cm2
2024-09-20 | Trade Links | Secunderabad | D | Salvo Explosive & Chemicals | Telangana | KCX2 | 3364K2518 | 4719568035 | 2023-08-29 | 471956 | 2024-08-14 | shaft seal leakage | 2023-08-29 | 2024-05-24 | 450 | 750 | chemical / pharma | 9 | R22 Aplication - Repititive failure of shaft seal. | null | closed | Replaced seal assly .
2024-09-24 | Hss Solution Pvt Ltd | null | D | Bikaner Agro Food Industries Pvt Ltd | Rajastan | KCX3 | 3374K3290 | 4757908106 | 2024-09-04 | 475790 | 2024-09-04 | abnormal noise | 2023-11-09 | 2024-08-02 | 25 | 665 | cold storage | 9 | Cylinder liner and piston rings wornout. | null | closed | Replaced all 3 liners & piston ring sets and 1 piston.
2024-09-24 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | SR Agro | Nagpur | KCX4 | 3384K3488 | 4776828164 | 2024-09-17 | 477682 | 2024-09-17 | knocking / abnormal sound | 2023-11-20 | 2024-02-23 | 1312 | 750 | cold storage | 3 | High oil carry over , liner & piston rings wornout. | null | closed | Replaced Liner4, Piston rings 4, disc holding & thrust ring1
2024-09-24 | Gargi Engineering Enterprices Pvt Ltd | null | D | Dlecta Foods Pvt Ltd | Khalapur | KCX3 | 3374K3140 | 4748888166 | 2024-09-17 | 474888 | 2024-09-17 | shaft seal leakage | 2023-03-28 | 2024-03-26 | 883 | 950 | food processing | 12 | Leakage from shaft seal due to Oring wornout. | null | closed | Replaced Oring kit.
2024-09-24 | Trade Links | Secunderabad | D | Sai Srinivasa Enterprises | Andhra Pradesh | KCX4 | 3384K3524 | 4640527924 | 2024-07-21 | 464052 | 2024-07-21 | high oil carryover | 2023-12-16 | 2024-01-05 | 2213 | 914 | ice plant | 1 | Liner & Piston rings wornout. | null | closed | Replaced liner4, Piston rings 4, Piston 2 , ORV1, Bearing half1
2024-09-24 | Trade Links | Secunderabad | D | Lakshmi Ganapthi Ice Factory | Andhra Pradesh | KCX6 | 3394K2328 | 4646547934 | 2024-07-23 | 464654 | 2024-07-09 | high oil carryover | 2023-11-20 | 2024-02-16 | 2772 | 850 | ice plant | 3 | Cylinder liners & piston rings wornout | null | closed | Replaced 4 liners , 6 piston ring sets and 1 delivery valve assly.
2024-09-24 | Robin Refrigeration Works | null | D | Capital Freezing Complex | Odisha | KCX21 | 3424K170 | 4733208079 | 2024-08-28 | 473320 | 2024-08-28 | cylinder overheating | 2024-07-24 | 2024-08-28 | 3 | 875 | meat/fish process | 1 | Delivery valve leakage due to the machining chips trapped. | null | closed | Replaced liner , piston ring , discharge valve , valve ring & spring1
2024-09-24 | Multivista Global Pvt Ltd | Gurgaon | D | M G Pterochem Pvt Ltd | Haryana | KCX72 | 3474K576 | 4791008205 | 2024-09-21 | 479100 | 2024-09-21 | knocking / abnormal sound | 2022-09-27 | 2023-06-06 | 4057 | 900 | chemical / pharma | 9 | Liners and piston rings wornout. | null | closed | Replaced all 9 liners and piston rings.
2024-09-30 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Bharat Milk Products Pvt Ltd | Punjab | KCX4 | 3384K3680 | 4739488071 | 2024-08-27 | 473948 | 2024-08-27 | oil carry over | 2024-03-26 | 2024-05-08 | 2334 | 770 | dairy / ice cream | 2 | Found all liner worn out. piston no 1 and 3 also found worn out. | null | closed | Replaced Liners4, Piston2 & Piston ring set4
2024-09-30 | Parag Marketing Services | null | D | Quality Ice Factory | Paithan | KCX1 | 3354K316 | 4636407923 | 2024-07-20 | 463640 | 2024-07-20 | oil carry over | 2023-09-25 | 2024-04-04 | 1076 | 850 | ice plant | 7 | Liner , piston and piston rings wornout. | null | closed | Replaced Liner2, Piston 2 & Piston ring set3
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Vaishno Enterprises | Uttar Pradesh | KC6 | 339K3734 | 4784728173 | 2024-09-18 | 478472 | 2024-09-18 | abnormal noise suc spring stuck | 2023-12-12 | 2024-02-04 | 1547 | 750 | cold storage | 3 | Found that section spring got damaged due to getting stuck in the stroke limiter and line due to which sound was coming from the compressor. | null | closed | Replaced suction spings1
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | New Kisan Cold Storage And Agro Industries | Uttar Pradesh | KC6 | 339K3746 | 4806168259 | 2024-11-08 | 480616 | 2024-11-08 | knocking / abnormal sound | 2023-12-21 | 2024-03-08 | 1563 | 750 | cold storage | 3 | liner and piston rings wornout. | null | closed | Replaced liner1, piston 1 , piston ring set1
2024-10-17 | Kalp Marketing | Gujrat | D | Shivam Cold Storage | Gujrat | KCX2 | 3364K2574 | 4795028211 | 2024-09-24 | 479502 | 2024-09-24 | knocking / abnormal sound | 2023-11-21 | 2024-02-16 | 2152 | 766 | cold storage | 3 | liner and piston rings wornout. | null | closed | Replaced liner and piston rings1.
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Baba Cold Storage | Uttar Pradesh | KC6 | 339K3750 | 4739008153 | 2024-09-15 | 473900 | 2024-09-15 | knocking / abnormal sound | 2023-12-26 | 2024-03-07 | 106 | 750 | cold storage | 3 | Cylinder liner wornout | null | closed | Replaced liner 1 no.
2024-10-17 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K3258 | 4768388170 | 2024-09-17 | 476838 | 2024-09-17 | oil carry over | 2023-10-19 | 2024-02-05 | 1905 | 770 | cold storage | 4 | Cylinder liners , piston rings wornout | null | closed | Replaced liner2 & Piston rings 3 sets , ORV3 & VLD Orings 3
2024-10-17 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K3257 | 4768408194 | 2024-09-20 | 476840 | 2024-09-19 | oil pressure problem | 2023-10-19 | 2024-02-05 | 672 | 770 | cold storage | 4 | Pump tang broken. | null | closed | Replaced pump element.
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Laddu Gopal Cold Storage | Uttar Pradesh | KC6 | 339K3758 | 4788788195 | 2024-09-20 | 478878 | 2024-09-21 | overheating & knocking sound. | 2024-01-03 | 2024-03-07 | 2142 | 750 | cold storage | 2 | Discharge valve spring broken and piston and piston ring wornout. | null | closed | Replaced piston 1 , piston ring set1 & delivery valve 1
2024-10-17 | Parag Marketing Services | null | D | Jai Jinendra Cold Storage Pvt Ltd | Vadaki Pune | KCX6 | 3394K2292 | 4776488152 | 2024-09-14 | 477648 | 2024-09-14 | shaft seal leakage | 2023-09-27 | 2024-09-14 | 216 | 850 | cold storage | 11 | Shaft seal leakage , Oring cut mark | null | closed | Replaced shaft seal assembly
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Vishnukanti Cold Storage | Uttar Pradesh | KC4 | 338K5929 | 4803288247 | 2024-10-03 | 480328 | 2024-10-03 | solenoid coil burnt | 2024-02-15 | 2024-03-04 | 119 | 750 | cold storage | 1 | Solenoid Coil Burnt | null | closed | Replaced solenoid coil1
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Jitendra Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2389 | 4799208221 | 2024-09-27 | 479920 | 2024-09-27 | solenoid coil burnt | 2023-12-30 | 2024-03-08 | 1869 | 771 | cold storage | 3 | Solenoid Coil Burnt in 40 hrs. | null | closed | Replaced solenoid coil1
2024-10-17 | Parag Marketing Services | null | D | Spruha Milk Chilling Center | Solapur | KCX4 | 3384K3587 | 4761448117 | 2024-09-06 | 476144 | 2024-09-06 | knocking / abnormal sound | 2024-01-20 | 2024-06-01 | 45 | 750 | dairy / ice cream | 5 | Liner , piston rings and piston wornout. | null | closed | Replaced liner2, Piston 2 & Piston ring set1
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KC6 | 339K2269 | 4808088258 | 2024-10-08 | 480808 | 2024-10-08 | krms issue | 2023-07-28 | 2023-09-07 | 2245 | 750 | dairy / ice cream | 14 | KRMS Display are not working. | null | closed | Replaced display
2024-10-17 | Trade Links | Secunderabad | D | The Krishna Dairy Milk Union Co-Operative Society | Andhra Pradesh | KCX9 | 3404K324 | 4797368229 | 2024-09-30 | 479736 | 2024-09-30 | shaft seal leakage | 2023-02-24 | 2023-02-05 | 591 | 800 | dairy / ice cream | 12 | Shaft seal assly leak | null | closed | Replaced shaft seal assly
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Desi Cook | Haryana | KCX63 | 3464K178 | 4786988183 | 2024-09-19 | 478698 | 2024-09-19 | cylinder overheating | 2023-05-31 | 2024-09-04 | 103 | 800 | food processing | 4 | Cylinder no.4 delivery valve leak due to cut mark in stroke limitor. | null | closed | Replaced delivery valve 1
2024-10-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Bankey Bihari Foods | Uttar Pradesh | KCX6 | 3394K2300 | 4786788181 | 2024-09-18 | 478678 | 2024-09-18 | krms panel problem | 2023-10-11 | 2024-02-12 | 201 | 850 | food processing | 4 | Site visited for Discharge temperature high trip problem in KRMS panel Discharge temperature sensor Damaged compressor. Discharge Temp sensor stuck up and wire broken. | null | closed | Replaced discharge temp sensor.
2024-10-17 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Dlecta Foods Pvt Ltd | Khalapur | KCX2 | 3364K2445 | 4757388169 | 2024-09-17 | 475738 | 2024-09-17 | shaft seal leakage | 2023-03-28 | 2024-03-08 | 879 | 935 | food processing | 11 | Oil leakage from seal Oring | null | closed | Replaced seal Oring kit.
2024-10-17 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Dlecta Foods Pvt Ltd | Khalapur | KCX31 | 3434K0201 | 4757408168 | 2024-09-17 | 475740 | 2024-09-17 | shaft seal leakage | 2023-03-28 | 2024-03-08 | 755 | 900 | food processing | 11 | Oil leakage from seal Oring | null | closed | Replaced seal Oring kit.
2024-10-17 | Trade Links | Secunderabad | D | Lakshmi Ganapthi Ice Factory | Andhra Pradesh | KCX6 | 3394K2328 | 4794888228 | 2024-09-30 | 479488 | 2024-09-30 | oil carry over | 2023-11-20 | 2024-02-16 | 4176 | 850 | ice plant | 3 | Liner wornout | null | closed | Replaced liners2
2024-10-17 | Geekay Pneumatic Pvt Ltd | Kerala | D | Nettos Ice Plant | Kerala | KCX4 | 3384K3533 | 4756888114 | 2024-09-05 | 475688 | 2024-09-05 | oil pressure not buildup | 2023-12-25 | 2024-09-05 | 2 | 930 | ice plant | 8 | Insulation not done and float valve not fitted. Oil pump pressure drop after 2 hors. OP TRIP. Pump gear jammed. | null | closed | Replaced pump assembly
2024-10-17 | Geekay Pneumatic Pvt Ltd | Kerala | D | Hic Abf Special Foods Pvt Ltd | Kerala | KCX72 | 3474K685 | 4797728218 | 2024-09-27 | 479772 | 2024-09-27 | cylinder overheating | 2023-08-22 | 2023-11-08 | 5188 | 818 | meat/fish process | 3 | Discharge valve leakage, delivery stroke limitor cut mark. | null | closed | Replaced delivery valve 1
2024-10-17 | Kalp Marketing | Gujrat | D | Raunak Ice & Cold Storage | Gujrat | KCX72 | 3474K795 | 4799868230 | 2024-09-30 | 479986 | 2024-09-30 | knocking / abnormal sound | 2024-06-27 | 2024-08-23 | 527 | 990 | meat/fish process | 3 | Cylinder no. 1 liner and piston rings wornout. | null | closed | Replaced liner and piston rings1.
2024-10-23 | Parag Marketing Services | Chhattisgarh | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3539 | 4813268279 | 2024-10-11 | 481326 | 2024-10-11 | filter housing damaged/crack | 2023-12-26 | 2024-08-03 | 21051900 00:00:00 | 750 | cold storage | 7 | Filter housing crack observed | null | closed | Manifold filter housing1
2024-10-23 | Trade Links | Secunderabad | D | Primary Agricultural Co-Operative Society | Andhra Pradesh | KCX3 | 3374K3191 | 4774668151 | 2024-09-14 | 477466 | 2024-09-14 | low oil pressure | 2023-07-19 | 2023-12-12 | 753 | 1000 | cold storage | 5 | Low oil pressure problem. | null | closed | CONTROL OIL PRESSURE REGULATOR ASSLY1, LUBRICATING OIL PRESSURE REGULATOR ASSLY1
2024-10-23 | Trade Links | Secunderabad | D | D J Exports Pvt Ltd | Telangana | PCX2 | 3106K0246 | 4789188185 | 2024-09-19 | 478918 | 2024-09-19 | shaft seal leakage | 2023-08-31 | 2024-05-18 | 668 | 750 | cold storage | 9 | shaft seal leakage | null | closed | SHAFT SEAL ASSEMBLY PC2/AC701
2024-10-23 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3497 | 4788908215 | 2024-09-26 | 478890 | 2024-09-26 | oil lifting | 2023-11-24 | 2024-03-06 | 3305 | 800 | ice plant | 4 | Oil Lifting problem | null | closed | PISTON RING SET KC/KCX3
2024-10-23 | Trade Links | Secunderabad | D | Sri Vishnu Smitha Ice Factory | Andhra Pradesh | KCX4 | 3384K3578 | 4778668171 | 2024-09-17 | 477866 | 2024-09-17 | oil lifting | 2024-01-15 | 2024-04-06 | 3100 | 850 | ice plant | 4 | Oil Lifting problem | null | closed | PISTON RING SET KC/KCX3
2024-10-23 | Parag Marketing Services | Pune | D | Kwality Animal Feeds | Kolhapur | KCX72 | 3474K794 | 4789748200 | 2024-09-21 | 478974 | 2024-09-21 | 24v not receiving from smps card | 2024-06-18 | 2024-09-21 | 8 | 1000 | meat/fish process | 3 | KRMS Problem | null | closed | SMPS 24V
2024-10-23 | Trade Links | Secunderabad | D | Sapala Organics P Ltd | Telangana | KCX1 | 3354K321 | 4789128184 | 2024-09-19 | 478912 | 2024-09-19 | shaft seal leakage | 2023-12-11 | 2024-02-23 | 1500 | 750 | chemical / pharma | 2 | Shaft seal inner O ring had damaged | null | closed | SHAFT SEAL ASSEMBLY KC/KCX1
2024-10-23 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Hikal Ltd | Mahad | KCX6 | 3394K2466 | 4802608272 | 2024-10-09 | 480260 | 2024-10-02 | shaft seal leakage | 2024-04-17 | 2024-05-03 | 260 | 550 | chemical / pharma | 1 | Shaft seal leakage | null | closed | Kit Shaft seal1
2024-10-31 | Kirloskar South East Asia Co Ltd | Thailand | E | Thai Union | Ghana | KCX72 | 3474K782 | email | 2024-10-30 | null | 2024-10-30 | danfoss make stop valve arrow for flow direction is at opposite side | 2024-05-27 | 2024-10-29 | 0 | 800 | cold storage | 5 | stop valve arrow direction accepted by D&D | null | closed | stop valve arrow direction accepted by D&D
2024-10-31 | Multivista Global Pvt Ltd | Gurgaon | D | Chhote Patel Sheetlaya | Uttar Pradesh | KCX3 | 3374K3256 | 4757888110 | 2024-09-04 | 475788 | 2024-09-04 | solenoid coil issue | 2023-10-21 | 2024-03-18 | 203 | 750 | cold storage | 6 | Soilenoid Coil Burnt | null | closed | Replace Solenoid Coil
2024-10-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Vijay Dairy Products | Gujrat | KCX4 | 3384K3676 | 4770608137 | 2024-09-11 | 477060 | 2024-09-11 | discharge temp sensor malfunction | 2024-03-19 | 2024-08-30 | 200 | 770 | dairy / ice cream | 5 | Discharge Temp Sensor Malfunction | null | closed | Replaced Discharge Temp Sensor
2024-10-31 | Trade Links | null | D | The Krishna Dairy Milk Union Co-Operative Society | Andhra Pradesh | KCX6 | 3394K2200 | 4662627950 | 2024-07-26 | 466262 | 2024-07-18 | shaft seal leakage | 2023-02-24 | 2024-02-19 | 470 | 800 | dairy / ice cream | 12 | Mating Face Wornout & O-ring becaome Hard | null | closed | Replaced Shaft Seal Assly
2024-10-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | New Velenkani Enterprises | Thane | KCX4 | 3384K3249 | 4739508077 | 2024-08-28 | 473950 | 2024-08-27 | oil carry over | 2023-01-10 | 2023-04-13 | 7010 | 800 | ice plant | 3 | Oil carryover | null | closed | Cylinder liner,piston ring set,piston
2024-10-31 | Multivista Global Pvt Ltd | Tamil Nadu | D | MNIce Plant | Tamil Nadu | KCX4 | 3384K3438 | 4726948049 | 2024-08-21 | 472694 | 2024-08-17 | shaft seal leakage | 2024-09-29 | 2024-08-08 | 226 | 825 | ice plant | 1 | Shaft seal Oring damaged. | null | closed | Replaced Oring kit.
2024-10-31 | Trade Links | null | D | Thomas Ice Plant | Goa | KCX3 | 3374K3182 | 4719648044 | 2024-08-19 | 471964 | 2024-08-14 | shaft seal leakage | 2023-07-13 | 2023-08-09 | 4418 | 700 | ice plant | 1 | Shaft Seal Leakage | null | closed | Replaced Oring kit.
2024-10-31 | Geekay Pneumatic Pvt Ltd | Kerala | D | Hic Abf Special Foods Pvt Ltd | Kerala | KCX31 | 3434K0227 | 4795468292 | 2024-10-17 | 479546 | 2024-09-23 | coupling disk pack broken | 2023-10-20 | 2024-02-16 | 4621 | 988 | meat/fish process | 4 | Coupling disk pack | null | closed | Coupling disk pack
2024-10-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sonia Fishries Pvt Ltd | Raigad | KCX72 | 3474K762 | 4746688101 | 2024-09-03 | 474668 | 2024-08-30 | discharge temp sensor malfunction | 2024-03-18 | 2024-05-21 | 356 | 950 | meat/fish process | 2 | Discharge Temp Sensor Malfunction | null | closed | Replaced Discharge Temp Sensor
2024-10-31 | Gargi Engineering Enterprices Pvt Ltd | null | D | Sonia Fisheries Pvt Ltd | Maharashtra | KCX72 | 3474K763 | 4746648102 | 2024-09-03 | 474664 | 2024-08-30 | discharge temp sensor malfunction | 2024-03-18 | 2024-05-21 | 338 | 950 | meat/fish process | 2 | Discharge Temp Sensor Malfunction | null | closed | Replaced Discharge Temp Sensor
2024-10-31 | Trade Links | Secunderabad | D | Kader Exports Pvt Ltd | Andhra Pradesh | KCX72 | 3474K729 | 4732828057 | 2024-08-23 | 473282 | 2024-08-25 | over heating | 2023-12-28 | 2024-04-06 | 2152 | 950 | meat/fish process | 4 | Cyl no. 7 delivery valve leakage. | null | closed | Replaced delivery valve ,Piston , piston ring set , gudgeon pin & liner.
2024-10-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Astec Life Science Ltd | Raigad | KCX42 | 3444K398 | 4809368271 | 2024-10-09 | 480936 | 2024-10-09 | shaft seal leakage | 2023-03-14 | 2023-08-24 | 1966 | 900 | chemical / pharma | 5 | Shaft seal oring kit replaced | null | closed | Shaft seal oring kit
2024-11-18 | Parag Marketing Services | Saswad | D | Varneshvar Doodh Sankalan Kendra | Maharashtra | PCX2 | 3106K0305 | 4843268380 | 2024-11-12 | 484326 | 2024-11-12 | gauge board fittings leakage | 2024-07-27 | 2024-11-12 | 0 | 1000 | null | 4 | Gauge board fittings leakage | null | open | Required fittings to rectifiy. Frerrule set & union nuts 6 nos.
2024-11-18 | Parag Marketing Services | Saswad | D | Pravin Masalewale | Satara | KCX2 | 3364K2397 | 4801068308 | 2024-10-21 | 480106 | 2024-10-21 | abnormal noise & oil carry over | 2022-12-23 | 2024-02-12 | 870 | 770 | cold storage | 14 | Liners and piston rings wornout. | null | closed | Replaced liners & Piston rings
2024-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Saurikh City Cold Storage | Uttar Pradesh | KC6 | 339K3710 | 4800708227 | 2024-09-30 | 480070 | 2024-10-04 | high oil consumption | 2023-10-16 | 2024-02-28 | 2232 | 759 | cold storage | 4 | Liners and piston rings wornout. | null | closed | Replaced Liners6 & Piston ring set6
2024-11-18 | Kalp Marketing | Gujrat | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3539 | 4812888276 | 2024-10-10 | 481288 | 2024-10-10 | krms issue | 2023-12-26 | 2024-08-03 | 136 | 750 | cold storage | 1 | KRMS Issue- SMPS 24VDC_ 2.5A supply issue at output end. | null | closed | Replaced SMPS
2024-11-18 | Parag Marketing Services | Saswad | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3539 | 4735648182 | 2024-09-18 | 473564 | 2024-09-18 | oil pressure problem | 2023-12-26 | 2024-08-03 | 30 | 750 | cold storage | 1 | Oil pressure issue due to pump scoring. | null | closed | Replaced pump assly
2024-11-18 | Model Pneumatic Co | Punjab | D | Green Preserve | J&K | KCX2 | 3364K2737 | 4765248226 | 2024-09-30 | 476524 | 2024-09-30 | required 24 vdc against 230 v | 2024-08-26 | 2024-09-30 | 1 | 800 | cold storage | 1 | Required 24 VDC Against 230 V | null | closed | No complaint.
2024-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Indian Pesticides Ltd | Uttar Pradesh | KCX6 | 3394K2438 | 4769248123 | 2024-09-09 | 476924 | 2024-10-01 | high oil consumption | 2024-02-12 | 2024-06-29 | 1158 | 771 | dairy / ice cream | 4 | Liners and piston rings wornout. | null | closed | Replaced Liners2 & Piston ring set6
2024-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Vrs Foods Ltd | Uttar Pradesh | KCX9 | 3404K339 | 4834228345 | 2024-10-29 | 483422 | 2024-10-29 | krms hmi display not working | 2023-07-28 | 2023-11-11 | W | 750 | dairy / ice cream | 4 | KRMS HMI Display not working, Damaged. | null | closed | Replaced HMI Display 7"
2024-11-18 | Parag Marketing Services | Saswad | D | Govind Milk & Milk Products Pvt Ltd | Phaltan | KCX72 | 3474K758 | 4799188220 | 2024-09-27 | 479918 | 2024-09-27 | manufold fitting leakage | 2024-02-29 | 2024-07-31 | 927 | 900 | dairy / ice cream | 5 | M10 Allan bolts broken . | null | closed | Replaced bolts M10 X 120 L 2 nos.
2024-11-18 | Pragya Industrial Supply | Karnataka | D | Shashi Sidnal Food Pvt Ltd | Karnataka | KCX72 | 3474K724 | 4821268296 | 2024-10-18 | 482126 | 2024-10-18 | shaft seal leakage | 2023-12-19 | 2024-04-18 | 530 | 1000 | dairy / ice cream | 4 | Shaft seal leakage, 2 times Orings replaced but not stopped. | null | closed | Replaced shaft seal assembly.
2024-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Desi Cook | Haryana | KCX63 | 3464K178 | 4826608316 | 2024-11-08 | 482660 | 2024-11-08 | cylinder overheating | 2023-05-31 | 2024-09-04 | 287 | 800 | food processing | 15 | Cylinder overheatong due to delivery valve leakage. | null | closed | Replaced valve assly.
2024-11-18 | Parag Marketing Services | Saswad | D | Mapro Foods Pvt Ltd | Wai | KCX42 | 3444K368 | 4778468199 | 2024-09-20 | 477846 | 2024-09-20 | high oil consumption | 2022-12-27 | 2023-03-07 | 385 | 1000 | food processing | 3 | Float valve assly problem . Not getting return oil. | null | closed | Replaced float valve
2024-11-18 | Pragya Industrial Supply | Karnataka | D | B P Uchil & Sons | Karnataka | KCX6 | 3394K2276 | 4850028393 | 2024-11-14 | 485002 | 2024-11-14 | high oil consumption | 2023-08-07 | 2023-08-15 | 4726 | 750 | ice plant | 1 | Liners and piston rings wornout. | null | closed | Replaced Liners4, Piston1 & Piston ring set6
2024-11-18 | Parag Marketing Services | Saswad | D | Real Aqua Multi Services | null | KRC4 | 3206K006 | 4815728340 | 2024-10-28 | 481572 | 2024-10-28 | knocking / abnormal sound | 2024-03-30 | 2024-04-27 | 1632 | 815 | ice plant | 1 | Knocking sound from cylinders. | null | closed | Replaced all liners , piston rings , gudgeon pins
2024-11-18 | Pragya Industrial Supply | Karnataka | D | Karthik Marine | Karnataka | KCX6 | 3394K2019 | 4730648070 | 2024-09-19 | 473064 | 2024-09-19 | abnormal noise | 2022-08-27 | 2023-03-29 | 3755 | 1000 | meat/fish process | 7 | Liners and piston rings wornout. | null | closed | Replacded all Liners and piston rings.
2024-11-18 | Multivista Global Pvt Ltd | Tamil Nadu | D | Monsoon Bounty Foods Manufacturing (P) Ltd | Tamil Nadu | KCX93 | 3485K165 | 4810448289 | 2024-10-15 | 481044 | 2024-10-15 | abnormal noise dv leak | 2023-06-19 | 2023-11-20 | 3872 | 980 | meat/fish process | 5 | HP Cylinder abnormal sound , delivery valve leakage hence all spares dagamed. | null | closed | Replaced cylinder assly
2024-11-18 | Pragya Industrial Supply | Karnataka | D | Malpefresh Marine Export Pvt Ltd | Karnataka | KCX93 | 3485K0209 | 4806348252 | 2024-10-06 | 480634 | 2024-10-06 | cylinder overheating | 2024-06-14 | 2024-09-26 | 40 | 950 | meat/fish process | 3 | Delivery valve leakage. | null | closed | Replaced delivery valve assly
2024-11-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises Pvt Ltd | Raigad | KCX72 | 3474K657 | 4825428307 | 2024-10-21 | 482542 | 2024-10-21 | knocking / abnormal sound | 2023-06-16 | 2023-08-14 | 2059 | 983 | meat/fish process | 2 | HP Cylinder no. 4 liner, piston , piston rings wornout. | null | closed | Replaced liner , piston , piston ring, DV & Bearings.
2024-11-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises Pvt Ltd | Raigad | KCX72 | 3474K654 | 4820288293 | 2024-10-17 | 482028 | 2024-10-17 | shaft seal leakage | 2023-06-16 | 2023-08-14 | 2910 | 985 | meat/fish process | 2 | Shaft seal leakage not arrested by Oring replacement & Relapping. | null | closed | Replaced shaft seal assly
2024-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | M G Pterochem Pvt Ltd | Haryana | KCX72 | 3474K576 | 4770628141 | 2024-09-16 | 477062 | 2024-09-16 | abnormal noise & oil carry over | 2022-09-27 | 2023-06-06 | 4051 | 900 | chemical / pharma | 9 | HP Cylinders liner & piston rings wornout 2 nos. | null | closed | Replaced liners & Piston rings 2 nos
2024-11-18 | Kalp Marketing | Gujrat | D | Life First Pharma Pvt Ltd | Madhya Pradesh | KC4 | 338K5809 | 4804708249 | 2024-10-05 | 480470 | 2024-10-05 | shaft seal leakage | 2022-12-31 | 2023-09-23 | 350 | 877 | chemical / pharma | 9 | Shaft seal leakage not arrested by Oring replacement & Relapping. | null | closed | Replaced shaft seal assly
2024-11-18 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Astec Life Science Ltd | Raigad | KCX42 | 3444K396 | 4811028277 | 2024-10-10 | 481102 | 2024-10-17 | shaft seal leakage | 2023-03-14 | 2023-08-24 | 2009 | 900 | chemical / pharma | 7 | Shaft seal oring kit replaced | null | closed | Shaft seal oring kit replaced
2024-11-18 | Trade Links | Secunderabad | D | Raveez Pharma P Ltd | Andhra Pradesh | KCX2 | 3364K2670 | 4773108198 | 2024-09-20 | 477310 | 2024-09-20 | shaft seal leakager22 | 2024-04-30 | 2024-09-20 | 11 | 750 | chemical / pharma | 5 | R22 Gas , seal leak within 11 hrs, used Viton Oring and found ok. | null | closed | Replaced Oring
2024-11-27 | Model Pneumatic Co | Punjab | D | Green Preserve | J&K | KCX2 | 3364K2737 | 4833488343 | 2024-10-28 | 483348 | 2024-10-28 | oil pressure issuetang broken. | 2024-08-26 | 2024-09-30 | 70 | 800 | cold storage | 1 | Compressor is not developing oil pressure. After that air purgeing done. No success | null | closed | Replaced pump assembly.
2024-11-27 | Trade Links | Secunderabad | D | Sri Geetha Dairy Products | Telangana | KCX2 | 3364K 2575 | 4819068288 | 2024-10-15 | 481906 | 2024-10-15 | high oil consumption | 2023-11-30 | 2024-03-22 | 509 | 750 | dairy / ice cream | 5 | Liner , piston rings wornout. | null | closed | Replaced liner , piston and piston ring set2
2024-11-27 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX72 | 3474K735 | 4827788366 | 2024-11-08 | 482778 | 2024-11-08 | knocking sound and overheating | 2024-01-25 | 2024-02-15 | 670 | 880 | food processing | 1 | Delivery valve rings broken & overheating. | null | closed | Replaced liner , piston & DV1
2024-11-27 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2320 | 4820928297 | 2024-10-18 | 482092 | 2024-10-18 | over heating | 2023-11-26 | 2024-03-12 | 1171 | 800 | food processing | 4 | Cylinder no. 6 Delivery valve leakage. | null | closed | Replaced piston , liner, piston rings, delivery valve , bearings etc
2024-11-27 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K078 | 4813048342 | 2024-10-28 | 481304 | 2024-10-28 | vbelt broken | 2023-10-31 | 2024-10-28 | 35 | 746 | food processing | 1 | V-Belt broken - 1 | null | closed | Replaced VBelt1
2024-11-27 | Multivista Global Pvt Ltd | Tamil Nadu | D | R V Ice Plant | Tamil Nadu | KCX6 | 3394K2480 | 4798108223 | 2024-09-28 | 479810 | 2024-09-28 | cylinder overheating | 2024-05-06 | 2024-06-28 | 1030 | 783 | ice plant | 1 | One cylinder seized. Liner , Piston , buffer spring , suction valve ring , spring & delivery valve damaged. | null | closed | Replaced liner , piston , piston ring set , suction valve ring & springs , delivery valve kit & aslly.
2024-11-27 | Pragya Industrial Supply | Karnataka | D | John Lawrence Ice And Cold Storage | Karnataka | KCX6 | 3394K2388 | 4800848239 | 2024-10-02 | 480084 | 2024-10-02 | high oil consumption | 2023-12-30 | 2024-06-18 | 1044 | 850 | ice plant | 6 | Liner , piston rings wornout. | null | closed | Replaced liner4, piston ring set6
2024-11-27 | Trade Links | Secunderabad | D | Sai Srinivasa Enterprises | Andhra Pradesh | KCX4 | 3384K3523 | 4778548242 | 2024-10-02 | 477854 | 2024-10-02 | high oil consumption | 2023-12-16 | 2024-01-05 | 1139 | 914 | ice plant | 1 | 3 litres oil in 10 hrs.All 4 liners and piston rings wornout. | null | closed | Replaced liners & piston rings 4
2024-11-27 | Trade Links | Secunderabad | D | Srinivasa Ice Factory | Andhra Pradesh | KCX6 | 3394K2511 | 4778568196 | 2024-09-20 | 477856 | 2024-09-20 | high oil consumption | 2024-07-16 | 2024-08-19 | 595 | 850 | ice plant | 1 | Liner , piston rings wornout. 6 lit/24 hrs. | null | closed | Replaced liners5 , Piston rings 5
2024-11-27 | Trade Links | Secunderabad | D | Teja Ice Factory | Andhra Pradesh | KCX6 | 3394K2214 | 4671088192 | 2024-09-20 | 467108 | 2024-09-20 | high oil consumption | 2023-03-19 | 2023-06-02 | 5164 | 850 | ice plant | 3 | Cylinder no.1 piston groove damaged due to rings wornout. | null | closed | Replaced piston.
2024-11-27 | Trade Links | Secunderabad | D | Kader Exports Private Limited Ap | null | KCX72 | 3474K729 | 4815468290 | 2024-10-15 | 481546 | 2024-10-15 | abnormal noise | 2023-12-28 | 2024-04-06 | 2691 | 950 | meat/fish process | 4 | HP Cyl1 & 4 liner , piston rings wornout. | null | closed | Replaced liner , piston , piston rings , bearings2 , & DV1
2024-11-27 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kottayam Dairy | Kerala | KCX3 | 3374K3409 | 4834148344 | 2024-10-29 | 483414 | 2024-10-29 | krms issuesuction temp sensor working. | 2024-02-21 | 2024-08-30 | 393 | 986 | meat/fish process | 6 | KRMS Issue-Suction temp sensor working. | null | closed | Sensor replaced.
2024-11-27 | Trade Links | Secunderabad | D | Apitoria Pharma Ltd ( Unit 1 ) | Telangana | KCX84 | 3305K037 | 4801708246 | 2024-10-03 | 480170 | 2024-10-03 | abnormal noise | 2024-04-27 | 2024-06-27 | 1050 | 850 | chemical / pharma | 2 | HP Cylinder discharge valve leakage & consequential failures. | null | closed | Replaced liner , piston , piston rings , Bearings & DV
2024-11-27 | Trade Links | Secunderabad | D | Chromo Laboratories India Pvt Ltd | Telangana | KCX21 | 3424K161 | 4815428282 | 2024-10-14 | 481542 | 2024-10-14 | krms issuesuction temp sensor cable not working. | 2023-06-24 | 2023-12-05 | 3414 | 750 | chemical / pharma | 6 | Suction Temp sensor cable is malfunctioning | null | closed | Cable replaced
2024-11-27 | Gargi Engineering Enterprices Pvt Ltd | Vadodara | D | Associated Dyestuff Pvt Ltd Unit-Iv | Gujrat | KCX63 | 3464K222 | 4815908332 | 2024-10-25 | 481590 | 2024-10-25 | manifold bolt broken | 2024-06-24 | 2024-10-25 | 18 | 930 | chemical / pharma | 4 | BOLT HEX SCREW SOCKET HD M10X1.5X120L broken | null | closed | Replaced BOLT HEX SCREW SOCKET HD M10X1.5X120L
2024-11-30 | Trade Links | Secunderabad | D | Jayalakshmi Sea Foods Private Limited | null | KCX6 | 3394K2217 | 4839568360 | 2024-11-07 | 483956 | 2024-11-07 | loading problem | 2023-03-27 | 2024-02-01 | 1092 | 700 | cold storage | 11 | Both regulator springs damaged due to this compressor i unloading frequently . New Regulator replaced form TL and restore the machine. | null | closed | Replaced OPRs
2024-11-30 | Kalp Marketing | Gujrat | D | Narmada Milk And Milk Products Pvt Ltd | Madhya Pradesh | KCX6 | 3394K2285 | 4843328374 | 2024-11-11 | 484332 | 2024-11-11 | cylinder overheating | 2023-08-31 | 2023-12-02 | 1306 | 650 | dairy / ice cream | 4 | Discharge valve leakage and overheated the cylinder | null | closed | Replaced DV
2024-11-30 | Pragya Industrial Supply | null | D | John Lawrence Ice And Cold Storage | Karnataka | KCX6 | 3394K2388 | 4855968413 | 2024-11-21 | 485596 | 2024-11-21 | discharge temperature sensor broken | 2023-12-30 | 2024-06-18 | 2060 | 850 | ice plant | 6 | Replaced discharge sensor | null | closed | Replaced discharge sensor
2024-11-30 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3498 | 4849208386 | 2024-11-13 | 484920 | 2024-11-13 | high oil consumption | 2023-11-24 | 2024-03-06 | 3886 | 800 | ice plant | 4 | Piston , piston rings , Liners wornout | null | closed | Replaced piston , liner, piston rings, delivery valve , bearings etc
2024-11-30 | Parag Marketing Services | null | D | Shifa Food Product | Maharashtra | KCX3 | 3374K3327 | 4837708414 | 2024-11-21 | 483770 | 2024-11-21 | shaft seal leakage | 2023-12-19 | 2024-04-03 | 1285 | 900 | ice plant | 4 | Rubbing and scoring on bronze ring | null | closed | Replaced shaft seal assembly
2024-11-30 | Trade Links | Secunderabad | D | Sapala Organics P Ltd | Telangana | KCX1 | 3354K321 | 4732788149 | 2024-09-13 | 473278 | 2024-09-13 | shaft seal leakager22 | 2023-12-11 | 2024-02-23 | 1350 | 750 | chemical / pharma | 2 | Shaft seal leakage | null | closed | Replaced shaft seal assembly
2024-11-30 | Trade Links | Secunderabad | D | Lvk Pharma P Ltd | Telangana | KCX3 | 3374K3224 | 4826368315 | 2024-10-22 | 482636 | 2024-10-22 | shaft seal leakager22 | 2023-09-13 | 2023-11-10 | 1098 | 750 | chemical / pharma | 2 | Freon 22 application system. Shaft seal leakage with in warranty | null | closed | Replaced shaft seal assembly
2024-12-02 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2320 | 4842328408 | 2024-11-20 | 484232 | 2024-11-14 | cylinder overheating | 2023-10-26 | 2024-03-12 | 1323.6 | 800 | food processing | 5 | Cylinder #1: DV valve ring and springs were broken. Head # 1: Overheating caused damage to the following components: - Liner - Piston - Piston rings - Connecting rod | null | closed | Replaced piston , piston rings , Gdgen pin and delivery valve.
2024-12-02 | Geekay Pneumatic Pvt Ltd | Kerala | D | R F Exports | Kerala | KCX72 | 3474K797 | 4799748231 | 2024-09-30 | 479974 | 2024-09-30 | kcx pump tang broken | 2024-06-21 | 2024-09-30 | 15 | 920 | meat/fish process | 3 | KCX Pump tang broken after 15 hrs | null | closed | Replaced pump assembly
2024-12-02 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Vkm Foods Pvt Ltd | Taloja, Mh | KCX3 | 3374K3573 | 4835208351 | 2024-11-04 | 483520 | 2024-11-01 | kcx pump tang broken | 2024-10-25 | 2024-11-01 | 6 | 800 | meat/fish process | 1 | KCX Pump tang broken after 6 hrs | null | closed | Replaced pump element.
2024-12-04 | Kalp Marketing | Gujrat | D | Minaz Export | Gujrat | KCX93 | 3485K184 | 4796488285 | 2024-10-14 | 479648 | 2024-10-14 | high oil consumption | 2024-02-10 | 2024-06-28 | 721 | 990 | meat/fish process | 4 | Open oil throw observed & one liner cut mark. | null | closed | Replaced piston ring sets 7 & Liner 1
2024-12-04 | Kalp Marketing | Gujrat | D | Alps Chemicals Pvt Ltd | Gujrat | KCX6 | 3394K2201 | 4584067879 | 2024-07-10 | 458406 | 2024-07-06 | high oil consumption | 2023-02-17 | 2023-07-31 | 3687 | 820 | chemical / pharma | 5 | cylinder liner number 1 and 3 are worn out , then replace cylinder liner for 1 and 3 , and replace 1 2 3 and 5 number cylinder piston rings then , refitted at the same , run the compressor and find every parameter is okay, compressor under observation for oil consumption | null | closed | Replaced Liners and piston rings.
2024-12-06 | Trade Links | Secunderabad | D | Pearl Beverages Ltd | Andhra Pradesh | KCX4 | 3384K3635 | 4827028327 | 2024-10-24 | 482702 | 2024-10-24 | abnormal noisedelivery valve leak | 2024-02-15 | 2024-03-13 | 2596 | 850 | beverage / breweries | 1 | TDV cylinder number 2 Delivery valve heavy back leakage due to this piston and liner sized | null | closed | Replaced liner , piston , piston rings , buffer spring and delivery valve.
2024-12-06 | Kalp Marketing | Gujrat | D | Advait Jns Agrotech | null | KCX3 | 3374K3305 | 4799708421 | 2024-11-23 | 479970 | 2024-10-02 | oil pressure regulator issue | 2023-11-27 | 2024-02-27 | 384 | 770 | cold storage | 3 | Oil pressure regulator not working. | null | closed | Replaced OPR Assly
2024-12-06 | Trade Links | Secunderabad | D | K V Reddy & Co Ice Factory | Andhra Pradesh | KCX4 | 3384K3652 | 4845148376 | 2024-11-11 | 484514 | 2024-11-11 | high oil consumption | 2024-02-27 | 2024-06-03 | 3491 | 878 | ice plant | 4 | Liner cut marks. | null | closed | Replaced liners and piston ring sets 4
2024-12-06 | Kalp Marketing | Gujrat | D | Sagar Drugs And Pharmaceuticals Pvt Ltd | Gujrat | KCX6 | 3394K2351 | 4828988336 | 2024-10-26 | 482898 | 2024-10-26 | over heating | 2023-12-08 | 2024-01-22 | 2638.5 | 771 | chemical / pharma | 1 | Cylinder no 4 overheating due to delivery valve ring spring broken. | null | closed | Replaced liner , piston , piston rings , buffer spring and delivery valve.
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Baba Cold Storage | Uttar Pradesh | KC4 | 338K5884 | 4805508264 | 2024-10-09 | 480550 | 2024-10-08 | high oil consumption | 2023-12-26 | 2024-03-07 | 2205 | 750 | cold storage | 3 | Liner cut marks. | null | closed | Replaced liners , piston and piston ring sets 4
2024-12-20 | Parag Marketing Services | Chhattisgarh | D | Raipur Logistics | Chhattisgarh | KCX4 | 3384K3168 | 4646688104 | 2024-09-03 | 464668 | 2024-08-14 | high oil consumption | 2022-11-18 | 2023-04-12 | 3293 | 750 | cold storage | 5 | Oil consumption rate 8 liter/50 hours/ 40CC. | null | closed | Replaced piston ring sets 4 , bearings and thrust ring etc.
2024-12-20 | Parag Marketing Services | null | D | Ecofresh Cold Storage & Warehousing PvtLtd | Pune | KCX2 | 3364K2487 | 4851608455 | 2024-11-29 | 485160 | 2024-12-01 | high oil consumption | 2023-07-07 | 2023-08-03 | 7833 | 800 | cold storage | 1 | Obseeved piston ,liner ,piston ring rubbing So require the all material . | null | closed | Replaced piston , piston ring & Liner
2024-12-20 | Kalp Marketing | Gujrat | D | Mittal Cold Storage Pvt Ltd | Gujrat | KCX3 | 3374K3335 | 4890728519 | 2024-12-17 | 489072 | 2024-12-17 | high oil consumption | 2023-12-25 | 2024-02-08 | PC | 767 | cold storage | 2 | Replaced liners - 2 & Piston ring set-3 | null | closed | Replaced liners2 , Piston ring sets3
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Anabia Cold Storage And General Mills | Uttar Pradesh | KCX6 | 3394K2403 | 4801648236 | 2024-10-01 | 480164 | 2024-10-25 | knocking / abnormal sound | 2024-01-15 | 2024-02-29 | 2120 | 750 | cold storage | 1 | Liner cut mark problem | null | closed | Replaced liner , piston , piston rings and delivery valves
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Saurikh City Cold Storage | Uttar Pradesh | KC6 | 339K3710 | 4806408250 | 2024-10-05 | 480640 | 2024-10-16 | knocking / abnormal sound | 2023-10-16 | 2024-02-28 | 2045 | 759 | cold storage | 4 | Liner cut mark problem | null | closed | Replaced piston , piston ring & Liner
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Jai Prakash Cold Storage | Uttar Pradesh | KCX6 | 3394K2326 | 4809008256 | 2024-10-07 | 480900 | 2024-10-15 | knocking / abnormal sound | 2023-11-16 | 2024-02-21 | 340 | 750 | cold storage | 3 | Liner cut mark problem | null | closed | Replaced piston , piston ring & Liner
2024-12-20 | Hss Solution Pvt Ltd | Rajasthan | D | Bansal Cold & Warehouse | Rajastan | KCX4 | 3384K3762 | 4854868466 | 2024-12-02 | 485486 | 2024-12-18 | op pressure switch malfunctioning | 2024-08-17 | 2024-12-18 | 1 | 760 | cold storage | 4 | OP Pressure switcmalfunctioning.. Tripping issue even if pressure developed | null | closed | Replaced OP Pressure switch
2024-12-20 | Cool Comfort Private Limited | West Bengal | D | Sethia Jain Himghar Pvt Ltd | West Bengal | KCX4 | 3384K3574 | 4878868496 | 2024-12-10 | 487886 | 2024-12-11 | over heating | 2024-01-12 | 2024-03-07 | 1856 | 850 | cold storage | 3 | Delivery valve spring broken | null | closed | Replaced kit delivery valve
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Ma Luxmi Traders | Uttar Pradesh | KC4 | 338K5889 | 4870988470 | 2024-12-03 | 487098 | 2024-12-03 | solenoid coil issue | 2023-12-30 | 2024-04-16 | 523 | 768 | cold storage | 4 | Solenoid valve coil burnt during commission | null | closed | Replaced coil
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Indian Pesticides Ltd | Uttar Pradesh | KCX6 | 3394K2439 | 4845248412 | 2024-11-21 | 484524 | 2024-12-18 | high oil consumption | 2024-02-12 | 2024-06-28 | 2396.2 | 771 | dairy / ice cream | 4 | Liner cut mark problem | null | closed | Replaced liner2 , Piston ring set 6
2024-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kozhikode Dairy | Kerala | KCX2 | 3364K2693 | 4858868440 | 2024-11-26 | 485886 | 2024-11-23 | high oil consumption | 2024-05-31 | 2024-09-22 | 814 | 980 | dairy / ice cream | 4 | No. 1 liner worn out. Changed the piston rings set 2 nos and one liner | null | closed | Replaced liners1 , Piston ring sets2
2024-12-20 | Kalp Marketing | Gujrat | D | Nestle India Limited | null | KCX6 | 3394K2228 | 4702528423 | 2024-11-23 | 470252 | 2024-08-07 | high oil consumption | 2023-03-29 | 2024-03-19 | 248 | 750 | food processing | 12 | VLD O-rings are flatten and liner number 4 found cutting marks. all other parts including liners and piston rings are found ok. As discussed with KPCL HO team we decided to replace all the VLD O-rings, liners and piston rings. | null | closed | Replaced VLD Piston and Orings
2024-12-20 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K083 | 4893168534 | 2024-12-20 | 489316 | 2024-12-20 | high oil consumption | 2023-11-30 | 2024-10-14 | PC | null | food processing | 11 | Liner cut mark problem | null | closed | Replaced liner & piston ring set12
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Frostar Foods Pvt Ltd | Uttar Pradesh | KCX63 | 3464K197 | 4861208447 | 2024-11-28 | 486120 | 2024-12-01 | knocking / abnormal sound | 2023-11-17 | 2024-02-16 | 1725 | 850 | food processing | 3 | Liner cut mark problem | null | closed | Replaced piston , piston ring & Liner
2024-12-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Dlecta Foods Pvt Ltd | Khalapur | KCX31 | 3434K0201 | 4866048493 | 2024-12-09 | 486604 | 2024-11-29 | purging issue in oil pump | 2023-03-28 | 2024-03-08 | 899 | 900 | food processing | 12 | OIL pump purging problem. | null | closed | Replaced pump assly
2024-12-20 | Parag Marketing Services | null | D | Swarajya Agro Products Llp | Maharashtra | KCX3 | 3374K 3480 | 4882228504 | 2024-12-13 | 488222 | 2024-12-13 | solenoid valve assembly malfunction. no type | 2024-06-26 | 2024-10-23 | 345 | 900 | food processing | 4 | CCSV no.1 was not getting loaded or unloaded electrically, on further investigation they found that CCSV coil no.1 was burned, | null | closed | Replaced solenoid valve assly
2024-12-20 | Trade Links | Secunderabad | D | Nk Marine Exports Llp | Andhra Pradesh | KCX6 | 3394K2379 | 4827808365 | 2024-11-08 | 482780 | 2024-11-08 | abnormal noise delivery valve leakage | 2023-12-27 | 2024-03-25 | 2423 | 850 | ice plant | 3 | Cylinder no. 1 & 2delivery valve leakage. | null | closed | Replaced liner , piston , piston rings and delivery valves
2024-12-20 | Kalp Marketing | Gujrat | D | Bhagyalaxmi Ice Factory | Gujrat | KCX4 | 3384K3370 | 4756968477 | 2024-12-05 | 475696 | 2024-09-03 | high oil consumption | 2023-06-10 | 2023-09-28 | 1640 | 770 | ice plant | 3 | VLD Oings flatened | null | closed | Replaced VLD Orings
2024-12-20 | Parag Marketing Services | null | D | Shifa Food Product | Maharashtra | KCX3 | 3374K3326 | 4837728415 | 2024-11-21 | 483772 | 2024-11-18 | high oil consumption | 2023-12-19 | 2024-04-01 | 1286 | 900 | ice plant | 4 | Liner cut marks. | null | closed | Replaced piston , piston ring & Liner
2024-12-20 | Kalp Marketing | Gujrat | D | Shri Himalay Ice & Cold Storage | Gujrat | KCX3 | 3374K3459 | 4805608499 | 2024-12-11 | 480560 | 2024-12-19 | high oil consumption | 2024-05-17 | 2024-07-19 | 2393 | 880 | ice plant | 2 | Liner cut marks. | null | closed | Replaced liners2 , Piston ring sets3
2024-12-20 | Pragya Industrial Supply | null | D | John Lawrence Ice And Cold Storage | Karnataka | KCX6 | 3394K2388 | 4840348363 | 2024-11-08 | 484034 | 2024-11-08 | oil pressure regulator issue | 2023-12-30 | 2024-06-18 | 1885 | 850 | ice plant | 6 | Lubrication oil pressure regulator spring was undersized. Replaced new lub regulator. | null | closed | Replaced OPR
2024-12-20 | Multivista Global Pvt Ltd | Gurgaon | D | Katlego Foods India Pvt Ltd | Haryana | KCX72 | 3474K717 | 4763148383 | 2024-11-13 | 476314 | 2024-11-13 | abnormal noise | 2023-11-30 | 2024-05-07 | 257 | 750 | meat/fish process | 6 | cylinder liner number 01. After that I opened the cylinder head and found that the Piston was seized. and damaged Crankshaft and Connecting Rod. | null | closed | Replaced liner , piston , piston ring set , crankshaft , bearings etc.
2024-12-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sesaga Enterprises Pvt Ltd | Raigad | KCX72 | 3474K654 | 4855728418 | 2024-11-22 | 485572 | 2024-11-21 | abnormal noisedelivery valve leak | 2023-06-16 | 2023-08-14 | 3374 | 985 | meat/fish process | 2 | On opening of Cy no. 4 DV assy internal springs found broken. Checked Piston, piston rings and Liner found worn out. Restoration work started by replacing Cylinder liner --1, Piston--1, Piston Rings--1, DV assy-1, Suction ring--1, suction springs--2, head Gaskets--1, side cover Gasket--2, Liner Gasket 1.5mm --1 . | null | closed | Replaced liner , piston ring set , delivery valve , suction ring springs
2024-12-20 | Kalp Marketing | Gujrat | D | Minaz Export | Gujrat | KCX93 | 3485K184 | 4871248473 | 2024-12-05 | 487124 | 2024-12-12 | high oil consumption | 2024-02-10 | 2024-06-28 | 764 | 990 | meat/fish process | 4 | oil consumption of approximately 10 liter per day., Liner cut marks. | null | closed | Replaced all liners & Piston ring sets
2024-12-20 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Gausia Cold Storage PvtLtd | Maharashtra | KCX72 | 3474K658 | 4849188409 | 2024-11-20 | 484918 | 2024-11-20 | high oil consumption | 2023-06-26 | 2023-09-10 | 1921 | 900 | meat/fish process | 3 | 1) Step cut marks on 4 cylinder liners 2) Oil thrown from all cylinders 3) Defective Cylinder #3 DV valve Replaced | null | closed | Replaced liner , piston , piston rings and delivery valves
2024-12-20 | Kalp Marketing | Gujrat | D | Perline Impex | Gujrat | KCX51 | 3454K223 | 4841048384 | 2024-11-13 | 484104 | 2024-11-15 | low oil pressurebearings wornout | 2023-06-27 | 2023-10-15 | 504 | 990 | meat/fish process | 4 | Replaced bearing halfs & Int Bearing hal | null | closed | Replaced bearing halfs & Int Bearing hal
2024-12-20 | Kalp Marketing | Gujrat | D | Favourite Exports Gujarat | null | KCX72 | 3474K793 | 4797688422 | 2024-11-23 | 479768 | 2024-09-26 | oil pressure regulator issue | 2024-06-17 | 2024-08-29 | 229 | 881 | meat/fish process | 2 | Oil pressure regulator not working. | null | closed | Replaced OPR Assly
2024-12-20 | Geekay Pneumatic Pvt Ltd | Kerala | D | Hic Abf Special Foods Pvt Ltd | Kerala | KCX31 | 3434K 0227 | 4848848397 | 2024-11-15 | 484884 | 2024-11-13 | shaft seal leakage | 2023-10-20 | 2024-02-16 | 4628 | 988 | meat/fish process | 4 | assembled the coupling with a new disc. The shaft seal was leak. Changed the O ring and lapped the face of the seal. Assembled the seal. Found that leaking again. So changed the seal and fixed it. | null | closed | Replaced coupling disk pack & shaft seal assly
2024-12-31 | Multivista Global Pvt Ltd | Gurgaon | D | Himilya Cold Storage & Ice Factory | Uttar Pradesh | KCX4 | 3384K3324 | 4855928465 | 2024-12-12 | 485592 | 2024-12-12 | high oil consumption | 2023-02-25 | 2024-03-13 | 951 | 750 | cold storage | 12 | Liner cut marks. | null | closed | Replaced liners, piston rings and piston4 nos
2024-12-31 | Kalp Marketing | Gujrat | D | Jalaram Cold Storage | Gujrat | KCX3 | 3374K3257 | 4856028460 | 2024-11-30 | 485602 | 2024-12-19 | knocking / abnormal sound | 2023-10-19 | 2024-02-05 | 854 | 770 | cold storage | 4 | Liner cut marks. | null | closed | Replaced liners2, Piston ring sets2 Buffer spring1
2024-12-31 | Multivista Global Pvt Ltd | Gurgaon | D | Indian Pesticides Ltd | Uttar Pradesh | KCX6 | 3394K2439 | 4891428525 | 2024-12-18 | 489142 | 2024-12-28 | high oil consumption | 2024-02-12 | 2024-06-28 | 2396.2 | 771 | dairy / ice cream | 4 | Liner cut mark problem | null | closed | Replaced aditional liner2
2024-12-31 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2320 | 4864228489 | 2024-12-09 | 486422 | 2024-12-04 | cylinder overheating | 2023-10-26 | 2024-03-12 | 1359.9 | 800 | food processing | 5 | Cylinder seize due to DV ring spring broken | null | closed | Replaced cyl assly
2024-12-31 | Kalp Marketing | Gujrat | D | Nestle India Limited | null | KCX12 | 3415K083 | 4853368449 | 2024-11-28 | 485336 | 2024-11-21 | shaft seal leakage | 2023-11-30 | 2024-10-14 | 82 | null | food processing | 12 | Oring flattend. | null | closed | Replaced Oring kit
2024-12-31 | Kalp Marketing | Gujrat | D | Shri Himalay Ice & Cold Storage | Gujrat | KCX3 | 3374K3460 | 4805628500 | 2024-12-11 | 480562 | 2024-12-19 | high oil consumption | 2024-05-17 | 2024-07-19 | 2157 | 874 | ice plant | 2 | Liner cut marks. | null | closed | Replaced liners2 & Piston ring set3
2024-12-31 | Kalp Marketing | Gujrat | D | Bhagyalaxmi Ice Factory | Gujrat | KCX4 | 3384K3370 | 4778708479 | 2024-12-05 | 477870 | 2024-09-21 | high oil consumption | 2023-06-10 | 2023-09-28 | 1889 | 770 | ice plant | 3 | Piston ring sets wornout | null | closed | Replaced piston ring sets4
2024-12-31 | Trade Links | Secunderabad | D | K V Reddy & Co Ice Factory | Andhra Pradesh | KCX4 | 3384K3652 | 4861068438 | 2024-11-25 | 486106 | 2024-11-25 | high oil consumption | 2024-02-27 | 2024-06-03 | 3712 | 878 | ice plant | 4 | Liner cut marks. | null | closed | Replaced shaft seal & Orings hardened
2024-12-31 | Geekay Pneumatic Pvt Ltd | null | D | Nettos Ice Plant | Kerala | KCX4 | 3384K3533 | 4900248552 | 2024-12-28 | 490024 | 2024-12-27 | high oil consumption | 2023-12-25 | 2024-09-05 | 528 | 930 | ice plant | 9 | Replaced liner & piston rings -4 due to wornout | null | closed | Replaced liner & piston rings 4 due to wornout
2024-12-31 | Multivista Global Pvt Ltd | Gurgaon | D | Pooja Ice Factory | Uttar Pradesh | KCX3 | 3374K3558 | 4890348526 | 2024-12-18 | 489034 | 2024-12-31 | op pressure switch malfunctioning | 2024-10-17 | 2024-12-31 | 6 | 750 | ice plant | 2 | OP Pressure switcmalfunctioning | null | closed | Replaced OP Pressure switch
2024-12-31 | Trade Links | Secunderabad | D | Ananda Foods Ltd | Andhra Pradesh | KCX6 | 3394K2164 | 4804388319 | 2024-10-23 | 480438 | 2024-10-17 | welding leakage | 2023-01-13 | 2023-10-13 | 7139 | 950 | ice plant | 10 | Suction strainer vertical pipe welding leakage. | null | closed | Rectified welding leakage . Planed to replaced the strainer housing
2024-12-31 | Kalp Marketing | Gujrat | D | Winsor World Exports | Gujrat | KCX72 | 3474K802 | 4891988532 | 2024-12-20 | 489198 | 2024-12-20 | high oil consumption | 2024-07-20 | 2024-08-14 | 1971 | 990 | meat/fish process | 1 | Piston rings wornout | null | closed | Replaced piston ring 9 & VLD Orings
2025-01-14 | Cool Comfort Private Limited | West Bengal | D | Sethia Jain Himghar Pvt Ltd | West Bengal | KCX6 | 3394K2416 | 4877348494 | 2024-12-09 | 487734 | 2024-12-11 | delivery valve leakage | 2024-01-23 | 2024-03-06 | 2765 | 850 | cold storage | 3 | Valve kit spring broken. | null | closed | Replaced kit1 & valve 2
2025-01-14 | Multivista Global Pvt Ltd | Gurgaon | D | Om Agro Cold Storage Llp | Uttar Pradesh | KCX4 | 3384K3571 | 4845228396 | 2024-11-15 | 484522 | 2024-11-15 | knocking / abnormal sound | 2024-01-10 | 2024-06-13 | 751 | 750 | cold storage | 6 | Liner cut mark | null | closed | Replaced Liner, Piston , Piston ring set.
2025-01-14 | Multivista Global Pvt Ltd | Gurgaon | D | Goodrich Carbohydrates Ltd | Haryana | PCX2 | 3106K0273 | 4891168539 | 2024-12-23 | 489116 | 2024-12-23 | high oil carryover | 2024-02-03 | 2024-07-11 | 2490 | 1200 | dairy / ice cream | 6 | Piston rings wornout | null | closed | Replaced piston ring sets2
2025-01-14 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Kolhapur Zila Sahakari Dudh Utpadak Sangh | Kolhapur | KCX6 | 3394K2193 | 4904768564 | 2025-01-01 | 490476 | 2025-01-01 | shaft seal leakage | 2023-02-07 | 2023-12-01 | 5630 | 750 | dairy / ice cream | 10 | checked mirror surface not matching.shaft seal one side pressing condition. Replace: Shaft seal assembly 1no.filter and oil. | null | closed | Replaced shaft seal assly
2025-01-14 | Geekay Pneumatic Pvt Ltd | Kerala | D | Rf Exports | Kerala | KCX3 | 3374K3537 | 4882448506 | 2024-12-16 | 488244 | 2024-12-16 | op pressure switch malfunctioning | 2024-09-26 | 2024-12-14 | 3 | 750 | ice plant | 3 | OP Pressure switcmalfunctioning | null | closed | Replaced OP Switch
2025-01-14 | Kalp Marketing | Gujrat | D | Minaz Export | Gujrat | KCX93 | 3485K184 | 4756988478 | 2024-12-05 | 475698 | 2024-12-05 | high oil carry over | 2024-02-10 | 2024-06-28 | 213 | 990 | meat/fish process | 5 | Replaced VLD Hsg & Piston Orings-9 | null | closed | Replaced VLD Hsg & Piston Orings9
2025-01-14 | Trade Links | Secunderabad | D | Siri Ice Links | Andhra Pradesh | KCX4 | 3384K3843 | 4894028580 | 2025-01-06 | 489402 | 2025-01-06 | oil pump tang broken | 2024-11-15 | 2025-01-07 | 2 | 750 | meat/fish process | 2 | Oil pump tang broken within 10 min. | null | closed | Replaced element
2025-01-14 | Geekay Pneumatic Pvt Ltd | Kerala | D | Kottayam Dairy | Kerala | KCX3 | 3374K3409 | 4889428531 | 2024-12-20 | 488942 | 2024-12-20 | tempearature sensor error | 2024-02-21 | 2024-08-30 | 863 | 986 | meat/fish process | 6 | Replaced temp sensor | null | closed | Replaced temp sensor
2025-01-14 | Trade Links | Secunderabad | D | Apitoria Pharma Ltd ( Unit 1 ) | Telangana | KCX42 | 3444K457 | 4849708420 | 2024-11-23 | 484970 | 2024-11-23 | cylinder overheating | 2024-04-27 | 2024-11-22 | 16 | 850 | chemical / pharma | 8 | HP Delivery valve leakage , Liner & piston ring set wornout | null | closed | Replaced DV , Liner , Piston & Piston ring 1
2025-01-14 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX72 | 3474K787 | 4901168561 | 2024-12-31 | 490116 | 2024-12-30 | low oil pressure | 2024-05-30 | 2024-12-14 | 8 | 850 | chemical / pharma | 6 | Tang broken | null | closed | Replaced pump element
2025-01-31 | Parag Marketing Services | null | D | Vrs Foods Limited | Maharashtra | KCX84 | 3305K041 | 4907368629 | 2025-01-17 | 490736 | 2025-01-17 | delivery valve leakage | 2024-07-30 | 2025-01-17 | 0 | 850 | dairy / ice cream | 6 | Replaced delivery valve | null | closed | Replaced delivery valve
2025-01-31 | Parag Marketing Services | null | D | Heritage Foods Ltd | Phaltan | KCX6 | 3394K2427 | 4877448548 | 2024-12-26 | 487744 | 2024-12-26 | knocking / abnormal sound | 2024-01-29 | 2024-05-24 | 3197 | 770 | dairy / ice cream | 4 | Discharge Valve (DV) leak and overheating | null | closed | Replaced liner, piston , piston ring set, gudgeon pin and discharge valve.
2025-01-31 | Pragya Industrial Supply | Karnataka | D | Mak Ice Plant | Karnataka | KCX4 | 3384K3327 | 4811508348 | 2024-10-31 | 481150 | 2024-10-31 | krms sensor problem | 2023-02-28 | 2023-08-18 | 4856 | 1000 | dairy / ice cream | 6 | KRMS sensor problem | null | closed | Replaced suction & discharge sensors.
2025-01-31 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX72 | 3474K739 | 4926608624 | 2025-01-16 | 492660 | 2025-01-24 | abnormal noise | 2024-01-25 | 2024-02-15 | 956 | 935 | food processing | 11 | The DV rings found broken in one cylinder resulting to damage the entire cylinder assembly. also in another cylinder premature faliure of liner has noticed. resulting to damage the piston and piston rings and subsequent spares. hence instruct service engineer to raise the FRR. The FRR is on hold and the compressor is under breakdown.. | null | closed | Replaced cylinder assembly
2025-01-31 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX63 | 3464K204 | 4926768623 | 2025-01-24 | 492676 | 2025-01-24 | abnormal noise | 2024-01-25 | 2024-02-15 | 803 | 935 | food processing | 11 | The DV rings found broken resulting to seized the entire cylinder assembly. hence instruct Service engineer to raised the FRR. The compressor is under breakdown and FRR is on hold. hence SR datas are not mentioned. | null | closed | Replaced cylinder assembly
2025-01-31 | Parag Marketing Services | null | D | Mapro Foods Pvt Ltd | Wai | KCX42 | 3444K368 | 4812988278 | 2024-10-10 | 481298 | 2024-10-10 | oil separator float valve problem. | 2022-12-27 | 2024-03-07 | 395 | 1000 | food processing | 25 | oil not return in oil separator so check manually found not return oil so check as per ocp float valve not working | null | closed | Replaced float valve
2025-01-31 | Multivista Global Pvt Ltd | Gurgaon | D | Aggarwal International | Uttar Pradesh | KCX6 | 3394K2578 | 4915908632 | 2025-01-18 | 491590 | 2025-01-18 | op pressure switch malfunctioning | 2024-10-29 | 2025-01-18 | 0 | 750 | food processing | 3 | Replaced OP Pressure switch | null | closed | Replaced OP Pressure switch
2025-01-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Harba Ice Factory | Raigad | KCX3 | 3374K3358 | 4923068608 | 2025-01-11 | 492306 | 2025-01-11 | high oil consumption | 2024-01-08 | 2024-09-06 | 2062 | 750 | ice plant | 9 | step cut marks on liner cylinder and piston rings are worn out. | null | closed | Replaced liner , piston 1& piston rings3
2025-01-31 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3496 | 4907828575 | 2025-01-03 | 490782 | 2025-01-03 | high oil consumption | 2023-11-24 | 2024-03-01 | 5077 | 800 | ice plant | 16 | No 3 & 4 cylinder liners and piston ring worn out | null | closed | Replaced liner & piston rings
2025-01-31 | Multivista Global Pvt Ltd | Tamil Nadu | D | Sangam Ice Factory And Cold Storage | Tamil Nadu | KC3 | 337K4898 | 4890208530 | 2024-12-20 | 489020 | 2024-12-20 | op pressure & pressure gauge switcmalfunctioning | 2024-07-22 | 2024-12-19 | 22 | 760 | ice plant | 5 | pressure gauge & OP switch out at atime indicates K5 Valve sleeve removed. | null | closed | Replaced pressure gauge & OP switch
2025-01-31 | Parag Marketing Services | null | D | Bhoomi Agro Bio Foods | Pune | KCX72 | 3474K725 | 4898008541 | 2024-12-24 | 489800 | 2024-12-24 | krms sensor problem | 2023-12-15 | 2024-07-09 | 2079 | 900 | others | 7 | The faulty suction temperature sensor was replaced. | null | closed | Replaced suction temperature seosor
2025-01-31 | Trade Links | Secunderabad | D | Kekule Pharma Ltd | Andhra Pradesh | KCX31 | 3434K0259 | 4902608563 | 2024-12-31 | 490260 | 2024-12-31 | over heating | 2024-09-13 | 2024-11-04 | 665 | 850 | chemical / pharma | 2 | No 1 cylinder discharge valve back leaking due to other parts were damaged | null | closed | Replaced liner, piston , piston ring set, gudgeon pin and discharge valve.
2025-02-19 | Thailand | null | E | Thai Union | Thailand | KCX4 | 3384K3718 | mail | 2025-02-19 | null | 2025-02-19 | compressor rusty | 2024-06-17 | null | WC | null | null | null | Compressor rusty within 4 month running of the compressor. | null | closed | null
2025-02-19 | Thailand | null | E | Thai Union | Thailand | KCX9 | 3404K364 | mail | 2025-02-19 | null | 2025-02-19 | oil pump isse | 2024-05-09 | null | WC | null | null | null | Oil pump scoring & tang broken. | null | closed | Replaced pump element & pump
2025-02-19 | Multivista Global Pvt Ltd | Gurgaon | D | RLSharma Sheetgrah | Uttar Pradesh | KC4 | 338K5885 | 4954848690 | 2025-02-06 | 495484 | 2025-02-06 | knocking / abnormal sound | 2023-12-23 | 2024-02-28 | 2031 | 750 | cold storage | 2 | Cylinder liner & piston wornout | null | closed | Replaced Cylinder liner1, Piston1, Piston ring set1
2025-02-19 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Amratlalaskokkumar Cold Storage And Ice Factory Pvt Ltd | Thane | KCX3 | 3374K3237 | 4944288675 | 2025-02-01 | 494428 | 2025-01-29 | over heating | 2023-09-28 | 2024-06-08 | 2051 | 900 | cold storage | 9 | Delivery valve spring broken. Noise from cyl. No.3 | null | closed | Replaced Delivery valve assembly1
2025-02-19 | Trade Links | Secunderabad | D | Sigma Sea Foods | Andhra Pradesh | KCX72 | 3474K783 | 4912488606 | 2025-01-11 | 491248 | 2025-01-29 | kcx pump tang broken | 2025-05-28 | null | 300 | 850 | food processing | 8 | Driving Gear Tang Broken within 15 min. | null | closed | Replaced Oil pump assly1
2025-02-19 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX6 | 3394K2423 | 4952888685 | 2025-02-05 | 495288 | 2025-02-05 | over heating | 2024-01-25 | 2024-02-15 | 1230 | 770 | food processing | 1 | Discharge valve leakage and overheated the cylinder | null | closed | Replaced Delivery valve assembly1
2025-02-19 | Kalp Marketing | Gujrat | D | Maikal Green Foods Pvt Ltd | Madhya Pradesh | KCX72 | 3474K832 | 4936788648 | 2025-01-25 | 493676 | 2025-01-25 | over heating | 2024-09-18 | 2024-12-27 | 908 | 767 | food processing | 3 | The Delivery valve found leak causing to overheat the cylinder | null | closed | Replaced Cylinder liner1, Piston ring set1, Delivery valve assembly1, Buffer spring1, Ring suction valve1, Valve spring suction2, Needle roller bearing2
2025-02-19 | Pragya Industrial Supply | Karnataka | D | Shree Sharadambika Ice Plant | Karnataka | KCX4 | 3384K3375 | 4927728628 | 2025-01-17 | 492772 | 2025-01-17 | high oil consumption | 2023-06-26 | 2023-09-04 | 6117 | 825 | ice plant | 3 | All Piston ring wornout | null | closed | Replaced Piston ring set4, Cylinder liner1
2025-02-19 | Parag Marketing Services | Pune | D | Shifa Food Product | Maharashtra | KCX3 | 3374K3326 | 4934608644 | 2025-01-23 | 493460 | 2025-01-23 | knocking / abnormal sound | 2023-12-19 | 2024-04-01 | 1757 | 900 | ice plant | 4 | Liner cut marks & piston ring wear out | null | closed | Replaced Piston ring set1, Piston1, Cylinder Liner1
2025-02-19 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Meherzeen Ice & Cold Storage Pvt Ltd | Mumbai | KCX3 | 3374K3378 | 4949148699 | 2025-02-10 | 494914 | 2025-02-04 | loading issue | 2024-01-22 | 2024-03-29 | 1362 | 750 | ice plant | 2 | Piston facing wornout & VLD was damaged | null | closed | Replaced Piston assembly VLD1
2025-02-19 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3496 | 4945168667 | 2025-01-30 | 494516 | 2025-01-29 | oil lifting | 2023-11-24 | 2024-03-01 | 5557 | 800 | ice plant | 3 | Premature wearing of Piston ring & Liner | null | closed | Replaced Piston ring set 2, Cylinder liner2
2025-02-19 | Cool Comfort Private Limited | West Bengal | D | Hindusthan Ice & Cold Storage Co Ltd | West Bengal | KCX6 | 3394K2437 | 4943428656 | 2025-01-28 | 494342 | 2025-02-01 | overheated & abnormal sound | 2025-02-12 | 2024-04-03 | 2901 | 850 | ice plant | 2 | Delivery valve spring broken | null | closed | Replaced Cylinder liner1, Piston1, Discharge valve assembly1, Kit delivery valve1, Piston ring set1, Gudgeon pin1, Bush connecting rod1, Buffer spring1
2025-02-19 | Cool Comfort Private Limited | West Bengal | D | Hindusthan Ice & Cold Storage Co Ltd | West Bengal | KCX6 | 3394K2434 | 4943448657 | 2025-01-28 | 494344 | 2025-02-01 | overheated & abnormal sound | 2024-02-12 | 2024-04-03 | 3195 | 850 | ice plant | 2 | Delivery valve spring broken & liner wornout | null | closed | Replaced Cylinder liner2, Piston1, Discharge valve assembly1, Kit delivery valve1, Piston ring set2, Gudgeon pin1, Bush connecting rod1, Buffer spring1
2025-02-19 | Parag Marketing Services | Pune | D | Shrinidhi Barf Karkhana | Chhatrapati Sambhajinagar | KCX1 | 3354K325 | 4939328650 | 2025-01-26 | 493932 | 2025-01-26 | shaft seal leakage | 2024-01-25 | 2025-01-17 | 59 | 700 | ice plant | 12 | Shaft seal damage | null | closed | Replaced Shaft seal assembly1
2025-02-19 | Trade Links | Goa | D | Thomas Ice Plant | Goa | KCX3 | 3374K3182 | 4892968559 | 2024-12-30 | 489296 | 2024-12-27 | shaft seal leakage | 2023-07-13 | 2023-08-09 | 6467 | 700 | ice plant | 1 | Shaft seal wormout | null | closed | Replaced Shaft seal assembly1
2025-02-19 | Multivista Global Pvt Ltd | Gurgaon | D | Mymeats Pvt Ltd | Haryana | KCX72 | 3474K866 | 4927988665 | 2025-01-29 | 492798 | 2025-02-08 | knocking / abnormal sound | 2024-11-29 | 2024-12-30 | 62 | 900 | meat/fish process | 1 | Cylinder liner & piston wornout | null | closed | Replaced Cylinder liner1, Piston1, Piston ring set1
2025-02-19 | Trade Links | Secunderabad | D | Kader Exports Private Limited Ap | null | KCX72 | 3474K729 | 4939108681 | 2025-02-03 | 493910 | 2025-02-03 | knocking / abnormal sound | 2023-12-28 | 2024-04-06 | 4247 | 950 | meat/fish process | 3 | Failure due to overheating of HP cylinder, piston seized due to overheating, premature wearing of piston ring | null | closed | Replaced Cylinder liner1, Piston1, Discharge valve assembly2, Piston ring set7, Gudgeon pin1, Needle roller bearing2, Spacer for needle roller bearing1
2025-02-19 | Kalp Marketing | Gujrat | D | S S International | Gujrat | KCX42 | 3444K477 | 4937328653 | 2025-01-26 | 493732 | 2025-01-24 | shaft seal leakage | 2024-08-13 | 2024-08-31 | 1593 | 880 | meat/fish process | 1 | Shaft seal damage | null | closed | Replaced Shaft seal assembly1
2025-02-19 | Multivista Global Pvt Ltd | Gurgaon | D | Indian Pesticides Ltd | Uttar Pradesh | KCX84 | 3305K048 | 4935368652 | 2025-01-28 | 493536 | 2025-01-27 | filter housing crack | 2024-12-27 | 2025-01-27 | 6 | 750 | chemical / pharma | 1 | Filter housing crack observed | null | closed | Replaced Filter Housing1
2025-02-26 | Cool Comfort Private Limited | West Bengal | D | Pronit Agro Products Storage & Marketing Pvt Ltd | West Bengal | KCX3 | 3374K3589 | 4969268730 | 2025-02-18 | 496926 | 2025-02-18 | op pressure switch malfunctioning | 2024-11-09 | 2025-02-18 | 0 | 850 | cold storage | 3 | OP Pressure switch tripping issue | null | closed | Replaced op switch.
2025-02-26 | Pragya Industrial Supply | null | D | Shashi Sidnal Food Pvt Ltd | Karnataka | KCX72 | 3474K724 | 4956268698 | 2025-02-08 | 495626 | 2025-02-07 | shaf seal leakage | 2023-12-19 | 2024-04-18 | 830 | 1000 | dairy / ice cream | 4 | Shaft seal leakage. Replaced new seal | null | closed | Replaced seal assly .
2025-02-26 | Parag Marketing Services | null | D | Spruha Milk Chilling Center | Solapur | KCX4 | 3384K3587 | 4963648715 | 2025-02-13 | 496364 | 2025-02-12 | solenoid valve leakage | 2024-01-20 | 2024-06-01 | 350 | 750 | dairy / ice cream | 5 | Solenoid valve leakage from bottom manual knob due to Oring damaged. | null | closed | Replaced S. valave
2025-02-26 | Kalp Marketing | Gujrat | D | Pepizo Foods | Gujrat | KCX93 | 3485K178 | 4961008702 | 2025-02-10 | 496100 | 2025-02-10 | over heating | 2023-11-08 | 2024-06-02 | 927 | 992 | food processing | 6 | Delivery valve leakage 01 no. Step cut mark to stroke limitor. | null | closed | Replaced delivery valve 1
2025-03-24 | Trade Links | Secunderabad | D | Sandhya Marines Limited | Telangana | KZX4 | 3206K002 | 4981448779 | 2025-02-26 | 498144 | 2025-02-26 | shaft seal leakage | 2024-05-23 | 2024-11-28 | 166 | 1480 | ac plant | 6 | KZX4 compressor shaft seal worn out within 166Hrs only. replaced new shaft seal and put back compressor into operation. | null | closed | SHAFT SEAL ASSEMBLY PC2/AC70
2025-03-24 | Trade Links | Secunderabad | D | Sandhya Marines Limited | Andhra Pradesh | KZX4 | 3206K002 | 4965448728 | 2025-02-18 | 496544 | 2025-02-14 | shaft seal leakage | 2024-05-23 | 2024-11-28 | 164 | 1480 | ac plant | 6 | New KZX 4compressor shaft seal leakage is observed and further inspection was done and found both seal faces worn out. | null | closed | Replaced shaft seal assly
2025-03-24 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Amratlalaskokkumar Cold Storage And Ice Factory Pvt Ltd | Thane | KCX3 | 3374K3237 | 4987748812 | 2025-03-04 | 498774 | 2025-03-04 | abnormal noise | 2023-09-28 | 2024-06-08 | 2215 | 900 | cold storage | 9 | Cyl no. 2 delivery valve spring broken. | null | closed | Replaced DV, liners, pistons & piston rings1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Amrit Cold Storage | Uttar Pradesh | KCX4 | 3384K3771 | 4992148836 | 2025-03-10 | 499214 | 2025-03-23 | filterhousing bolt broken | 2024-09-04 | 2025-03-23 | 2 | 750 | cold storage | 0 | Zero Hour Complaint, Found wire filter Bolt Broken | null | closed | BOLT HEX SCREW SOCKET HD M10X1.5X120L
2025-03-24 | Cool Comfort Private Limited | West Bengal | D | Sethia Cold Storage | null | KCX6 | 3394K2397 | 4995388842 | 2024-03-11 | 499538 | 2024-03-11 | high oil consumption | 2024-01-11 | 2024-02-22 | 1176 | 850 | cold storage | 1 | Liner , piston , piston rings wornout | null | closed | Replaced all liners, pistons & piston rings.
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | S S Yadav Cold Storage | Uttar Pradesh | KC4 | 338K5870 | 4925968619 | 2025-01-14 | 492596 | 2025-01-14 | high oil consumption | 2023-11-30 | 2024-03-13 | 2525 | 768 | cold storage | 16 | Liner , piston and piston rings wornout. | null | closed | Replaced Piston 4 nos.
2025-03-24 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Sanmargg Coldstorage Private Limited | Maharashtra | KCX3 | 3374K3526 | 4914528594 | 2025-01-09 | 491452 | 2025-01-08 | krms pressure transducer malfuctioning | 2024-08-19 | 2024-12-07 | 3 | 750 | cold storage | 4 | Oil pressure transducer not working. | null | closed | 12.8 bar pressure transducer replaced.
2025-03-24 | Kalp Marketing | Gujrat | D | Rajaram Cold Storage | Gujrat | KCX4 | 3384K3844 | 5003828854 | 2025-03-15 | 500382 | 2025-03-15 | oil pressure problem | 2024-11-15 | 2025-02-18 | 107 | 770 | cold storage | 3 | Verfied that there is no evidence of liquid entry or foreign particles. Suction Strainer, Oil and Oil Filters found clean and Also the alignment observed as per our standard.The Bronze thrust ring found worn out.hence instruct service engineer to replace the same | null | closed | Replaced THRUST RING PUMP END BEARING COVER KCX
2025-03-24 | Parag Marketing Services | null | D | Govind Milk & Milk Products Pvt Ltd | Phaltan | KCX4 | 3384K3655 | 4970108763 | 2025-02-22 | 497010 | 2025-02-22 | oil pump tang broken | 2024-02-29 | 2025-01-31 | 13 | 850 | cold storage | 11 | Pump element broken within 13 hours. | null | closed | Replaced pump element.
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Hanumant Cold Storage | Uttar Pradesh | KC4 | 338K5905 | 4927928696 | 2025-02-07 | 492792 | 2025-02-19 | shaft seal leakage | 2024-01-18 | 2024-04-14 | 2169 | 750 | cold storage | 3 | shaft seal complaint was resolved and during this found Gas leakage from Nob of Solenoid Valve | null | closed | SOLENOID VALVE (TEFLON), 3 WAY, 230V, 50HZ,NC
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Guru Gobind Singh Cold Mills | Uttar Pradesh | KCX4 | 338K6009 | 4987308808 | 2025-01-10 | 498730 | 2025-02-20 | solenoid coil issue | 2025-01-10 | 2025-02-20 | 341 | 750 | cold storage | 1 | 1. Solenoid Coil is burning 2. follow the service schedule timely the avoid liquid | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Hanumant Cold Storage | Uttar Pradesh | KC4 | 338K5905 | 4927928696 | 2025-02-07 | 492792 | 2025-02-19 | solenoid leakage from bottom knob | 2024-01-18 | 2024-04-14 | 2169 | 750 | cold storage | 3 | Leakage from solenoid valve bottom knob. | null | closed | Replaced solenoid valve1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Prakash Cold Storage | Uttar Pradesh | KCX6 | 3394K2445 | 4973308747 | 2025-02-20 | 497330 | 2025-02-20 | solenoid leakage from bottom knob | 2024-02-19 | 2024-03-08 | 3147 | 750 | cold storage | 1 | Solenoid valve due to leak from bottom knob | null | closed | Replaced solenoid valve
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Mansharam Cold Storage | Uttar Pradesh | KC4 | 338K5953 | 4971768732 | 2025-02-09 | 497176 | 2025-02-09 | solenoid valve coil burnt | 2024-10-26 | 2025-02-18 | 30 | 751 | cold storage | 4 | Solenoid valve coil-1 not working | null | closed | Replaced solenoid valve coil1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | D APAgro And Storage | Uttar Pradesh | KC6 | 339K3809 | 4987148807 | 2025-03-04 | 498714 | 2025-03-04 | solenoid valve not working | 2024-11-30 | 2025-03-02 | 2 | 750 | cold storage | 5 | Replaced solenoid valve-1 | null | closed | Replaced solenoid valve1
2025-03-24 | Model Pneumatic Co | Gurgaon | D | Datt Singh Cold Storage | Uttar Pradesh | KC6 | 339K3822 | 4957848738 | 2025-02-19 | 495784 | 2025-02-19 | sv coil burnt | 2024-12-18 | 2025-02-19 | 4 | 750 | cold storage | 2 | Zero Hour Complaint. Coil burnt. | null | closed | SOLENOID VALVE COIL 230 V AC
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Datt Singh Cold Storage | Uttar Pradesh | KC6 | 339K3822 | 4957848738 | 2025-02-19 | 495784 | 2025-02-19 | sv coil burnt | 2024-12-18 | 2025-02-19 | 4 | 750 | cold storage | 2 | Solenoid valve coil not working | null | closed | Replaced solenoid valve coil1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Parwana Cold Storage | Uttar Pradesh | KC4 | 338K5941 | 4963548711 | 2025-02-13 | 496354 | 2025-02-13 | sv coil burnt | 2024-05-11 | 2025-02-13 | 2 | 750 | cold storage | 9 | Solenoid valve coil not working | null | closed | Replaced solenoid valve coil1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Om Sai Cold Storage | Uttar Pradesh | KC6 | 339K3825 | 4973128804 | 2025-03-04 | 497312 | 2025-03-01 | sv coil burnt | 2024-12-19 | 2025-03-01 | 6 | 750 | cold storage | 3 | Solenoid valve coil not working | null | closed | Replaced solenoid valve coil2
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Avantibai Lodhi Cold Storage | Uttar Pradesh | KCX6 | 3394K2646 | 4985008806 | 2025-03-04 | 498500 | 2025-03-04 | sv coil burnt | 2025-01-23 | 2025-02-28 | 4 | 750 | cold storage | 1 | Replaced solenoid valve coil not working | null | closed | Replaced solenoid valve coil1
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Dropadi Cold Storage And Allied | Uttar Pradesh | KC6 | 339K3814 | 4973408762 | 2025-02-22 | 497340 | 2025-02-22 | sv coil burnt | 2024-12-04 | 2025-02-13 | 18 | 750 | cold storage | 2 | Loading/unloading problem due to coils not working. | null | closed | Replaced solenoid valve coils 2 nos
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Mann Feeds Pvt Ltd | Haryana | KCX72 | 3474K748 | 4994028831 | 2025-03-07 | 499402 | 2025-03-13 | abnormal noise | 2024-02-08 | 2024-02-19 | 7204.6 | 850 | dairy / ice cream | 0 | Discharge Valve get leakage due to that other parts also damaged . | null | closed | Replaced CYLINDER LINER KC/KCX PISTON KC/KCX DISCHARGE VALVE ASSEMBLY KCX
2025-03-24 | Parag Marketing Services | null | D | Washishti Milk And Milk Product Pvt LtdChiplun | Maharashtra | KCX2 | 3364K2521 | 4955908720 | 2025-02-15 | 495590 | 2025-02-15 | knocking / abnormal sound | 2023-09-02 | 2024-04-28 | 2200 | 750 | dairy / ice cream | 5 | Liner , piston , piston rings wornout & Cyl 2 DV leakage due to valve seat damaged. | null | closed | Replaced all liners, pistons & piston rings. DV1
2025-03-24 | Gargi Engineering Enterprices Pvt Ltd | Gujrat | D | Vijay Dairy Products | Gujrat | KCX6 | 3394K2459 | 4849228445 | 2024-11-26 | 484922 | 2024-11-21 | krms display not working | 2024-03-19 | 2024-11-21 | 5 | 770 | dairy / ice cream | 8 | Verified and found the display is not working hence replaced with new one | null | closed | 7 INCH TOUCH SCREEN HMI DISPLAY
2025-03-24 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K083 | 4980888776 | 2025-02-25 | 498088 | 2025-02-25 | abnormal noise | 2023-11-30 | 2024-10-14 | PC | null | food processing | 11 | Joint Visit has been made. Found buffer spring length shorten respect to the specified limit. hence intruct to replace the same. | null | closed | Replcaced BUFFER SPRING KC/KCX, ORING VLD PISTON KCX
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Ambrosia Natural Products India Pvt Ltd | Uttar Pradesh | KCX42 | 3444K450 | 4992748828 | 2025-03-07 | 499274 | 2025-03-07 | abnormal noise | 2024-02-24 | 2025-02-09 | 133 | 750 | food processing | 12 | Liners and piston rings wornout. | null | closed | Replaced liners2, Piston rings2.
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Bankey Bihari Foods | Uttar Pradesh | KCX9 | 3404K347 | 4989528818 | 2025-03-05 | 498952 | 2025-03-20 | abnormal noise dv leak | 2023-10-31 | 2024-02-21 | 718 | 850 | food processing | 16 | Delivery valve leak, liner wornout | null | closed | Replaced DV , Liner , Piston & Piston ring 1
2025-03-24 | Model Pneumatic Co | Punjab | D | Guru Nanak Agro Foods Pvt Ltd | Punjab | KCX72 | 3474K847 | 4982908781 | 2025-02-27 | 498290 | 2025-03-06 | delivery valve leakage | 2024-10-18 | 2025-01-11 | 551 | 950 | food processing | 3 | HP Cyl 1 , Delivery valve spring broken & leakages. | null | closed | Replaced DV1, Liner , Piston & Piston ring set.
2025-03-24 | Trade Links | Secunderabad | D | Nk Marine Exports Llp | Andhra Pradesh | KCX6 | 3394K2379 | 4984728798 | 2025-03-03 | 498472 | 2025-03-04 | abnormal noise | 2023-12-27 | 2024-03-25 | 2978 | 850 | ice plant | 3 | No 1 & 2 cylinders discharge valves back leakage due to the other part were damaged. Replaced damaged parts from TL stock and restore the machine | null | closed | Replaced PISTON KC/KCX PISTON RING SET KC/KCX GUDGEON PIN KC/KCX BUSH CONNECTING ROD KC/KCX BEARING BUSH BIG END CON ROD KC/KCX BUFFER SPRING KC/KCX SPRING CURTAIN, LINER ASSEMBLY KC/KCX CYLINDER LINER KC/KCX VALVE SPRING SUCTION KC RING SUCTION VALVE KC/KCX DISCHARGE VALVE ASSEMBLY KCX
2025-03-24 | Parag Marketing Services | null | D | Shifa Food Product | Maharashtra | KCX3 | 3374K3327 | 4867648544 | 2024-12-25 | 486764 | 2024-12-23 | abnormal noise | 2023-12-19 | 2024-04-03 | 1593 | 900 | ice plant | 4 | Liner , piston , piston rings wornout | null | closed | Replaced all liners, pistons & piston rings.
2025-03-24 | Trade Links | Secunderabad | D | Alnoor Ice Factory | Andhra Pradesh | KCX4 | 3384K3497 | 4872468482 | 2024-12-06 | 487246 | 2025-12-06 | high oil consumption | 2023-11-24 | 2024-03-06 | 4351 | 800 | ice plant | 4 | 5 liters of oil is consuming in 24 hours, inspected the compressor and found 4 liners cut marks is observed and piston rings worn out. 1 DV leaking noted | null | closed | Replaced liners4 & piston rings4, DV1
2025-03-24 | Trade Links | Secunderabad | D | Mahlakshmi Ice Factory | Andhra Pradesh | KCX4 | 3384K3278 | 4634107935 | 2024-07-23 | 463410 | 2024-07-05 | high oil consumption | 2023-01-28 | 2023-03-24 | 7969 | 850 | ice plant | 2 | Liner & piston rings wornout | null | closed | Replaced liners3 & piston rings4
2025-03-24 | Trade Links | Secunderabad | D | Sri Lakshmi Jyothi Ice Factory | Andhra Pradesh | KCX4 | 3384K3547 | 4869528481 | 2024-12-06 | 486952 | 2024-12-10 | high oil consumption | 2023-12-28 | 2024-02-10 | 4492 | 880 | ice plant | 2 | Liner & piston rings wornout | null | closed | Replaced all 4 liners & piston rings.
2025-03-24 | Trade Links | Secunderabad | D | Srinivasa Ice Factory | Andhra Pradesh | KCX6 | 3394K2511 | 4826628350 | 2024-11-03 | 482662 | 2024-11-03 | high oil consumption | 2024-07-16 | 2024-08-19 | 1405 | 850 | ice plant | 1 | 2nd time customer told that 6 liters oil is lifting per day , service engineer inspected all heads , All 6 liner worn out and 6 no piston rings out ,2 Nos piston cracked, 4nos Discharge valve leakage is observed and replaced all parts from TL stock and restore the machine. since 3 months compressor was running under observation and oil lifting is under control. | null | closed | Replaced liner6 , piston2, piston rings 6 & DV 4 .
2025-03-24 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Harba Ice Factory | Raigad | KCX3 | 3374K3367 | 4923088609 | 2025-01-11 | 492308 | 2025-01-15 | high oil consumption | 2024-01-17 | 2024-09-08 | 267 | 750 | ice plant | 9 | Cyl 1 & 2 liner wornout , one DV leak due to ring spring broken. | null | closed | Replaced liner , piston 2 nos , Piston ring 3 sets & DV1
2025-03-24 | Parag Marketing Services | null | D | Radhe Ice World | Maharashtra | KCX3 | 3374K3434 | 4874708598 | 2025-01-09 | 487470 | 2025-01-09 | high oil consumption | 2024-03-13 | 2024-06-11 | 3544 | 750 | ice plant | 3 | Liner , piston , piston rings wornout | null | closed | Replaced all liners, pistons & piston rings.
2025-03-24 | Parag Marketing Services | null | D | Atharva Milk And Milk Product | Maharashtra | KCX3 | 3374K3403 | 4874048612 | 2025-01-12 | 487404 | 2025-01-12 | high oil consumption | 2024-02-16 | 2024-05-16 | 4004 | 750 | ice plant | 3 | Liner , piston , piston rings wornout | null | closed | Replaced all liners, pistons & piston rings.
2025-03-24 | Pragya Industrial Supply | Karnataka | D | Indo Fisheries | Karnataka | KCX4 | 3384K3545 | 4903388607 | 2025-01-11 | 490338 | 2025-01-11 | high oil consumption | 2023-12-27 | 2024-01-23 | 1700 | 800 | ice plant | 13 | Liners and piston rings wornout. | null | closed | Replaced liners4, Piston rings4 & bearing bushes
2025-03-24 | Trade Links | Secunderabad | D | Teja Ice Factory | Andhra Pradesh | KCX6 | 3394K2214 | 4646447933 | 2024-07-23 | 464644 | 2024-07-10 | high oil consumption& shaft seal leakage | 2023-03-19 | 2023-06-02 | 4839 | 850 | ice plant | 1 | Liner & piston rings wornout | null | closed | Replaced all 6 liners & piston rings.
2025-03-24 | Kalp Marketing | Gujrat | D | Anar Chemicals Llp | Gujrat | KCX42 | 3444K478 | 5003588846 | 2025-03-13 | 500358 | 2025-03-13 | oil carry over | 2024-10-10 | 2024-11-07 | 1463 | 767 | ice plant | 0 | Verified that there is no issue from system side. The VLD piston O-ring found flatten from OD. hence instruct service engineer to replace the same. | null | closed | Replaced ORING VLD PISTON KCX, ORING VLD KCX
2025-03-24 | Trade Links | Goa | D | Thomas Ice Plant | Goa | KCX3 | 3374K3182 | 4945908672 | 2025-01-31 | 494590 | 2025-01-31 | oil carry over | 2023-07-13 | 2023-08-09 | 7074 | 700 | ice plant | 1 | The TLS Engineer attended to an oil carryover complaint and a sudden oil discoloration issue (blackish oil). Upon investigation, the engineer opened all head covers for inspection. They found that Cylinder No. 1 piston was damaged with scoring marks. Discovered scratch marks on the remaining three linear cylinders and Observed worn-out piston rings. To resolve the issue, the TLS Engineer replaced all defective parts and successfully restored the compressor to working condition., Previously site O rings and gasket set were consumed during complaints attended Relevant images and FSR are attached for FRR approval process,.d hence replace linear and piston ring | null | closed | Replaced GUDGEON PIN KC/KCX, PISTON KC/KCX, CYLINDER LINER KC/KCX, PISTON RING SET KC/KCX, GASKET SUCT STRAINER & SIDE COVER KC/KCX, GASKET HEAD COVER KC/KCX, OIL RETURN VALVE KC/KCX/PC2, FILTER PAPER, DISCH OIL FILTER AC, ORING OIL FILTER HOUSING KCX, ORING VLD KCX, ORING VLD PISTON KCX
2025-03-24 | Trade Links | Secunderabad | D | Sri Rama Ice Factory | Telangana | KCX4 | 3384K3642 | 4979988787 | 2025-02-28 | 497998 | 2025-02-25 | oil pressure trip | 2024-02-21 | 2024-04-27 | 3410 | 750 | ice plant | 2 | Both regulators malfunctioning due to compressor frequently tripping on low oil pressure. replaced new regulators from TL stock and restore the machine. | null | closed | Replaced CONTROL OIL PRESSURE REGULATOR ASSLY. KCX, LUBRICATING OIL PRESSURE REGULATOR ASSLY. KCX
2025-03-24 | Trade Links | Secunderabad | D | Sri Lakshmi Narasimha Ice Factory | Andhra Pradesh | KCX4 | 3384K3976 | 4979048767 | 2025-02-24 | 497904 | 2025-02-24 | shaft key loose | 2025-02-10 | 2025-02-18 | 200 | 700 | ice plant | 0 | During commissioning , the service engineer is observed that crack shaft key is found loose in keyway so replaced with new key form TL stock and completed commissioning work | null | closed | Replaced Key
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shourya Banana Raping Plant | Uttarakhand | KCX3 | 3374K3634 | 4979228770 | 2025-03-16 | 497922 | 2025-02-24 | solenoid coil issue | 2024-12-20 | 2025-02-06 | 329 | 750 | ice plant | 2 | 1.Went to site for loading unloading and found solenoid coil problem and replaced coil under warranty, after that started compressor. Compressor is running successfully. 2. Went to the site for loading unloading and found the problem of solenoid coil | null | closed | SOLENOID VALVE COIL 230 V AC
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Shourya Banana Raping Plant | Uttarakhand | KCX3 | 3374K3634 | 4979228770 | 2025-02-24 | 497922 | 2025-02-24 | solenoid valve coil burnt | 2024-12-20 | 2025-02-06 | 329 | 750 | ice plant | 2 | Replaced solenoid valve coil-1 not working | null | closed | Replaced solenoid valve coil1
2025-03-24 | Kalp Marketing | Gujrat | D | Silver Sea Food | Gujrat | KCX72 | 3474K734 | 4990208824 | 2024-01-19 | 499020 | 2025-03-05 | cylinder overheating | 2024-01-19 | 2024-04-03 | 1838 | 991 | meat/fish process | 2 | Verfied that there is no issue from system side. The DV RIngs has found Broken resulting to overheat the cyliner and damaged the Cylinder Liner alongwith the Piston rings set and Piston. Hence instruct service engineer to replace the required spares. | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, CYLINDER LINER KC/KCX,DISCHARGE VALVE ASSEMBLY KCX
2025-03-24 | Pragya Industrial Supply | Karnataka | D | Malpefresh Marine Export Pvt Ltd | Karnataka | KCX93 | 3485K0209 | 4962328707 | 2025-02-12 | 496232 | 2025-02-12 | discharge temperature sensor fail | 2024-06-14 | 2024-09-26 | 305 | 950 | meat/fish process | 3 | TEMERATURE SENSOR BROKEN | null | closed | DISCHARGE TEMPERATURE SENSOR, PT1000 WITH 12 MTR CABLE LENGTH. RANGE ( 50 to 250 Deg C)
2025-03-24 | Cool Comfort Private Limited | West Bengal | D | Sea Foods Pvt Ltd | West Bengal | KCX51 | 3454K244 | 4979948772 | 2025-02-25 | 497994 | 2025-02-25 | intermediate pressure high & compressor overheat | 2024-02-09 | 2024-03-29 | 3991 | 850 | meat/fish process | 1 | HP Cylinder delivery valve kit broken. | null | closed | Replaced DV kit1
2025-03-24 | Trade Links | Secunderabad | D | Kekule Pharma Ltd | Andhra Pradesh | KCX31 | 3434K0259 | 4801688352 | 2024-11-04 | 480168 | 2024-11-04 | abnormal noise | 2024-09-13 | 2024-11-04 | 29 | 850 | chemical / pharma | 2 | 1 HP cylinder and 1 LP Cylinder discharge valve back leaking is observed. | null | closed | Replaced liner1 , piston , piston ring set , gudgeon pin & DV2
2025-03-24 | Trade Links | Secunderabad | D | Archimedies Laboratories P Ltd | Andhra Pradesh | KCX6 | 3394K2409 | 4922808636 | 2025-01-20 | 492280 | 2025-01-18 | abnormal noise | 2024-01-19 | 2024-03-22 | 2818 | 880 | chemical / pharma | 2 | No 3 & No 5 cylinders discharge valves were back leaking is observed due to that other parts were damaged. Replaced with new parts from TL stock and restored machine. | null | closed | Replaced liner1 , piston , piston ring set , gudgeon pin & DV2
2025-03-24 | Multivista Global Pvt Ltd | Gurgaon | D | Prime Air Products ( C/O Superior Industries Ltd ) | Uttar Pradesh | KCX72 | 3474K743 | 4837568353 | 2024-11-05 | 483756 | 2024-11-10 | high oil consumption | 2024-01-31 | 2024-09-04 | 1077 | 850 | chemical / pharma | 8 | Liner , piston & piston rings wornout | null | closed | Replaced liner9 , piston3 & piston rings9.
2025-03-25 | Kalp Marketing | Gujrat | D | Om Cold Storage | Gujrat | KCX3 | 3374K3645 | 5007868889 | 2025-03-20 | 500786 | 2025-03-20 | high oil consumption | 2024-12-28 | 2025-02-24 | 188 | 770 | cold storage | 0 | Verfied that there is no issue from system side. The suction strainer also found clean. The liner has been cut in 360 degree pattern resuling to damage the piston rings set and rotory part of shaft seal. hence instruct FSE to replace the required spares. | null | closed | Replaced PISTON RING SET KC/KCX, CYLINDER LINER KC/KCX & SHAFT SEAL ASSEMBLY KC/KCX
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Ambe Agro And Cold Storage Pvt Ltd | Haryana | KCX3 | 3374K3201 | 4999588850 | 2025-03-13 | 499958 | 2025-03-10 | krms issue | 2023-08-01 | 2023-09-13 | 735 | 750 | cold storage | 1 | Found SMPS Faulty. | null | closed | Replaced SMPS 24VDC_ 2.5A SINGLE OUTPUT DIN RAIL MOUNTED
2025-03-25 | Kalp Marketing | Gujrat | D | Ananta Hi Tech Cold Storage | Gujrat | KCX4 | 3384K3840 | 5010148885 | 2025-03-19 | 501014 | 2025-03-23 | oil pressure problem | 2024-11-22 | 2025-02-28 | 32 | 770 | cold storage | 3 | Verified that there is no issue from system side. Suction strainer,oil,oil filters found clean. the driving gear shaft of oil pump found broken during the running of the compressor. these resulted to damaged the pump casing and bronze thrust ring as well. hence instruct to to replace the entire pump assembly | null | closed | Replaced OIL PUMP ASSEMBLY KCX & THRUST RING PUMP END BEARING COVER KCX
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | SGP Cold Storage | null | KC4 | 338K6002 | 5010108884 | 2025-03-19 | 501010 | 2025-03-19 | op pressure switch malfunctioning | 2025-01-07 | 2025-03-19 | 8 | 750 | cold storage | null | Oil pressure cut out found faulty during commissioning. | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-03-25 | Cool Comfort Private Limited | West Bengal | D | Mukti FirmspvtLtd | West Bengal | KCX4 | 3384K3585 | 5001408843 | 2025-03-11 | 500140 | 2025-03-12 | over heating | 2024-01-19 | 2024-03-14 | 1926 | 850 | cold storage | 2 | The overheating problem was discussed with our service engineer, he opened the head cover and checked the compressor thoroughly and found broken No. 2 ride spring and damaged 1 valve sheet. No foreign particles in cylinder, this is premature failure. | null | closed | Replaced DISCHARGE VALVE ASSEMBLY KCX & KIT DELIVERY VALVE KC/KCX
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Agnihotri Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2681 | 5011348910 | 2025-03-21 | 501134 | 2025-03-21 | pressure gauge not working | 2025-02-19 | 2025-03-21 | 4.5 | 750 | cold storage | 1 | Zero Hour Complaint, Needle found below Zero | null | closed | Replaced Pressure gauge 16 Kg/cm2
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Ji Coldstorage | Uttar Pradesh | KC3 | 337K4960 | 5013068918 | 2025-03-22 | 501306 | 2025-03-22 | pressure gauge not working | 2025-02-11 | 2025-03-22 | 6 | 750 | cold storage | 1 | Pressure gauge not working, its needle is sucked. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-03-25 | Trade Links | Secunderabad | D | Icycity Cold Storage P Ltd | null | KCX2 | 3364K2764 | 4952868734 | 2025-02-19 | 495286 | 2025-02-18 | shaft key loose | 2024-09-30 | 2025-02-18 | 2 | 750 | cold storage | 5 | Crank shaft key was freely sliding on the key way, replaced new key from TL stock and commissioned. | null | closed | Replaced CRANKSHAFT KEY KC/KCX
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Kisan Sheetgrah Up | null | KC4 | 338K5979 | 5010368898 | 2025-03-20 | 501036 | 2025-03-19 | solenoid coil issue | 2024-12-18 | 2025-02-25 | 253 | 750 | cold storage | 2 | SV Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Guru Gobind Singh Cold Mills | Uttar Pradesh | KC4 | 338K6009 | 5012788916 | 2025-03-22 | 501278 | 2025-03-22 | solenoid coil issue | 2025-01-10 | 2025-02-20 | 341 | 750 | cold storage | 1 | SV Coil Burnt. | null | closed | Replaced SOLENOID VALVE 3WAY
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Biharilal Cold Storage & Allied Industries | Uttar Pradesh | KC4 | 338K5995 | 5013108921 | 2025-03-23 | 501310 | 2025-03-23 | sv coil burnt | 2024-12-30 | 2025-03-23 | 3.8 | 750 | cold storage | 2 | S.V Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Pallavi Cold Storage & Ice Factory Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2656 | 5011428905 | 2025-03-20 | 501142 | 2025-03-20 | sv coil burnt | 2025-01-31 | 2025-03-12 | 0 | 750 | cold storage | 2 | Solenoid Coil burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | DK Cold Storage & General Mills | Uttar Pradesh | KC3 | 337K4952 | 4992908830 | 2025-03-07 | 499290 | 2025-03-06 | sv coil burnt | 2025-01-27 | 2025-02-19 | 163 | 750 | cold storage | 1 | Discharge Filter to shaft seal cover pipe broken and solinoid coil burning | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER & PIPE BEND, DISCH. FILTER TO SHAFT SEAL COVER. FOR KC3/KC21 MODE
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Sugandhi Preservation Pvt Ltd | Uttar Pradesh | KC4 | 338K5981 | 4992228920 | 2025-03-22 | 499222 | 2025-03-06 | sv coil burnt | 2024-12-19 | 2025-03-22 | 5 | 750 | cold storage | 3 | S V Coil Burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Dr Ghure Singh Cold Storage | Uttar Pradesh | KC4 | 338K5990 | 5010288886 | 2025-03-19 | 501028 | 2025-03-19 | sv coil burnt | 2024-12-31 | 2025-03-17 | 20 | 750 | cold storage | 3 | Solenoid Coil burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Sugandhi Preservation Pvt Ltd | Uttar Pradesh | KC6 | 339K3829 | 4992208919 | 2025-03-22 | 499220 | 2025-03-06 | sv coil burnt | 2024-12-24 | 2025-03-22 | 6.6 | 750 | cold storage | 3 | SV Coil Burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Mldc Cold Solutions Llp | Uttar Pradesh | KCX3 | 3374K3672 | 5009508881 | 2025-03-19 | 500950 | 2025-03-18 | sv coil burnt | 2025-01-30 | 2025-03-18 | 0 | 750 | cold storage | 2 | Solenoid Coil burnt and thread of the of adapter is damaged. | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER & EXTENDED FEMALE ADAPTER, 6MM OD X G 1/8" BSP(F), LIGHT, SS.
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Kisaan Bandhu Cold Storage Llp | Uttar Pradesh | KC6 | 339K3861 | 4979708873 | 2025-03-18 | 497970 | 2025-02-24 | sv coil burnt | 2025-01-28 | 2025-03-18 | 4 | 750 | cold storage | 2 | Solenoid coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | R D Cold Store | Uttar Pradesh | KC4 | 338K6021 | 4974588867 | null | 497458 | 2025-02-21 | sv coil burnt | 2025-01-21 | 2025-03-17 | 8 | 750 | cold storage | 2 | Solenoid coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-03-25 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K083 | 4866628461 | 2024-11-30 | 486662 | 2024-11-29 | shaft seal leakage | 2023-11-30 | 2024-10-14 | 336 | 750 | food processing | 11 | Verified that there is no issue from system side. Suction Strainer, Oil and Oil Filters found clean. Oil Leakage noticed from the shaft seal which has been tried to resolve it by replacing the O-ring. The leakage was still there. hence instruct Service Engineer to replace entire Shaft Seal assembly. | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-03-25 | Multivista Global Pvt Ltd | Chennai | D | Phillips Foods India Private Limited | Tamil Nadu | KCX2 | 3364K2776 | 5008828908 | 2025-03-21 | 500882 | 2025-03-21 | oil carry over | 2024-10-26 | 2024-11-11 | 27780 | 791 | ice plant | 1 | oil carry over complaint | null | closed | Replaced PISTON RING SET KC/KCX & CYLINDER LINER KC/KCX
2025-03-25 | Dicksons Engineering Co Pvt Ltd | Nagpur | D | Renuka Ice Factory | Maharashtra | KC2 | 336K3430 | 5010688906 | 2025-03-20 | 501068 | 2025-03-20 | oil pressure problem | 2024-02-22 | 2025-02-28 | 120 | 750 | ice plant | 0 | Dickson Engineer attended oil pressure is not developed During visit, they noticed that air purging issue in oil pump, and scoring marks on gears faces and plate. To resolve complaint, they need to replace complete oil pump assembly. Relevant images and FSR are attached fr FRR approval process | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-03-25 | Multivista Global Pvt Ltd | Gurgaon | D | Prime Air Products ( C/O Superior Industries Ltd ) | Uttar Pradesh | KCX72 | 3474K743 | 4989308866 | 2025-03-17 | 498930 | 2025-03-04 | abnormal noise | 2024-01-31 | 2024-09-04 | 2474 | 850 | chemical / pharma | 8 | Liner and Piston Ring worn-out. | null | closed | Replaced PISTON RING SET KC/KCX , PISTON KC/KCX & CYLINDER LINER KC/KCX
2025-03-25 | Kalp Marketing | Gujrat | D | Sakti Tech Tex Pvt Ltd | Gujrat | KCX4 | 3384K3713 | 5003668847 | 2025-03-13 | 500366 | 2025-03-13 | kcx pump air purging | 2024-06-12 | 2024-10-22 | PC | 780 | chemical / pharma | 4 | Verfied that there is no issue from System side. suction strain,oil and oil filters found clean. also checked the pump as per air purging OCP but issue was still there.hence instruct engineer to replace the entire pump assembly. | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-03-31 | Multivista Global Pvt Ltd | New Delhi | D | Darshan Foods Pvt Ltd | Haryana | KCX93 | null | Mail | 2025-03-21 | null | 2025-03-21 | base frame foundation hole missing | 2024-09-26 | 2025-03-21 | 0 | null | null | null | Base frame foundation one hole missing | null | closed | Rectification done by welding & drilling
2025-03-31 | Trade Links | Secunderabad | D | Sandhya Marines Limited | Telangana | KZX4 | 3206K002 | 5001008929 | 2025-03-24 | 500100 | 2025-03-27 | low oil pressure | 2024-05-23 | 2024-11-28 | 199 | 1480 | ac plant | 6 | Compressor tripping on low differential oil pressure and then inspected the pump gear and cover and found t e be crescent gear and cover worn out. Replaced new pump assmbly from TL stock and restored machine | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-03-31 | Gargi Engineering Enterprices Pvt Ltd | Mumbai | D | Amratlalaskokkumar Cold Storage And Ice Factory Pvt Ltd | Thane | KCX3 | 3374K3237 | 5009208911 | 2025-03-21 | 500920 | 2025-03-19 | abnormal noise | 2023-09-28 | 2024-06-08 | 2334 | 900 | cold storage | 9 | GEE Engineer attended abnormal sound complaint. During visit they noticed that Piston rings set -1no wear out and low top clearances was noticed at all liner cylinders. Replaced defective liner gaskets. Additionally shaft seal O rings found flatten. Relevant images and FSR attached for FRR approval process. | null | closed | Replaced PISTON RING SET KC/KCX & KIT SHAFT SEAL ORING KC/KCX
2025-03-31 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3600 | 5012548923 | 2025-03-24 | 501254 | 2025-03-24 | abnormal noise | 2024-01-27 | 2024-03-30 | 754 | 990 | cold storage | 2 | As per service engineer observation and found that as same problem in this compressor (discharge valve leakage). so, it is a premature failure. | null | closed | Replaced PISTON RING SET KC/KCX, KIT DELIVERY VALVE KC/KCX & SOLENOID VALVE (TEFLON), 3 WAY, 230V, 50HZ,NC
2025-03-31 | Kalp Marketing | Gujrat | D | Keshari Cold Storage | Gujrat | KCX3 | 3374K3328 | 5013448930 | 2025-03-24 | 501344 | 2025-03-24 | cylinder overheating | 2023-12-20 | 2024-02-23 | 696 | 770 | cold storage | 2 | Verified that there is no evidence of foreign particles. Suction strainer , oil , oil filters also found clean. The delivery valve found leak. Hence instruct service engineer to replace the DV kit. | null | closed | Replaced KIT DELIVERY VALVE KC/KCX
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Rana Enterprises | Uttar Pradesh | KC3 | 337K4972 | 4990368927 | 2025-03-24 | 499036 | 2025-03-28 | driven gear tang broken | 2025-02-21 | 2025-03-28 | 3 | 750 | cold storage | 1 | Zero hour Complaint- Driven Gear Tang broken | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Aan Ke Cold Storage | null | KCX4 | 3384K3519 | 5015948928 | 2025-03-24 | 501594 | 2025-03-30 | oil lifting | 2023-12-13 | 2024-03-16 | 1809 | 750 | cold storage | 3 | Found Liner And Piston ring Worn out | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX, PISTON RING SET KC/KCX, LOCK PLATE CON ROD & INTER. HSG BOLT KC/KCX
2025-03-31 | Parag Marketing Services | MH | D | Govind Milk & Milk Products Pvt Ltd | Phaltan | KCX4 | 3384K3656 | 4975488863 | 2025-03-17 | 497548 | 2025-03-17 | oil pressure problem due to oil pump tang brocken | 2024-02-29 | 2025-01-31 | null | 850 | cold storage | 11 | PMS Engineer attended complaint of oil pump oil pressure was not developing. During visit they noticed that Element Tang was broken and scoring marks on housing. Replaced oil pump assembly -1no. Relevant images and FSR attached for FRR approval process | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-03-31 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3601 | 5012528922 | 2025-03-24 | 501252 | 2025-03-24 | over heating | 2024-01-27 | 2024-03-07 | 893 | 850 | cold storage | 2 | As discussed with our service engineer that he checked compressor regarding customer overheat complaint and found discharge valve ring broken & damage liner as well as piston with their ring. As observed it is a premature failure. | null | closed | Replaced PISTON KC/KCX,PISTON RING SET KC/KCX,CYLINDER LINER KC/KCX, KIT DELIVERY VALVE KC/KCX
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Veer Krishna Cold Storage Pvt Ltd | null | KC6 | 339K3846 | 4972388933 | 2025-03-24 | 497238 | 2025-03-24 | pressure gauge swelled. | 2025-01-15 | 2025-03-24 | 4 | 750 | cold storage | 2 | Zero Hours Complaint, Pressure Gauge swelled. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 25 KG/CM2 , 100MM DIAL, GLYSERINE FILLED
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Lala Naval Kishore Refrigeration | Uttar Pradesh | KC4 | 338K6055 | 5015728935 | 2025-03-25 | 501572 | 2025-03-27 | shaft seal leakage | 2025-02-22 | 2025-03-27 | 2 | 850 | cold storage | 1 | Found Shaft seal Leakage During the commissioning, Leakage. There is still some leakage even after changing the new ring | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Sahab Ice & Cold Storage | Uttar Pradesh | KC6 | 339K3806 | 4987208938 | 2025-03-25 | 498720 | 2025-03-23 | sv coil burnt | 2024-11-22 | 2025-03-23 | 6 | 750 | cold storage | 4 | Zero Hour Complaint, SV Coil Burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Dhanraj Cold & Warehouse | Uttar Pradesh | KC6 | 339K3816 | 4971848940 | 2025-03-25 | 497184 | 2025-03-12 | sv coil burnt | 2024-12-06 | 2025-03-12 | 4 | 750 | cold storage | 3 | Zero Hour Problem , SV Coil Problem | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-31 | Multivista Global Pvt Ltd | Gurgaon | D | Sahab Ice & Cold Storage | Uttar Pradesh | KC6 | 339K3806 | 5010888912 | 2025-03-21 | 501088 | 2025-03-23 | sv coil burnt | 2024-11-22 | 2025-03-23 | 0 | 750 | cold storage | 4 | Zero Hour Complaint, SV Coil Burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-03-31 | Kbtl | Thailand | E | Kbtl | Thailand | KCX6 | 3394K2501 | email | 2025-03-27 | null | 2025-03-27 | weld leak at discharge pipe | 2024-06-10 | 2025-03-12 | 10 | 850 | cold storage | 9 | Rectification done by welding | null | closed | Rectification done by welding
2025-03-31 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX72 | 3474K738 | 5005588913 | 2025-03-21 | 500558 | 2025-03-21 | cylinder overheating | 2024-01-25 | 2024-02-15 | 903 | 935 | food processing | 1 | Verified that there is no issue from system side. The suction strainer, oil ,oil filter also found clean. Overheating issue noticed in one cylinder. Further checked and found DV rings broken. The FSE has tried to restore valve by replacing the DV kit but issue was there. Hence instruct service engineer to replace the entire valve assembly | null | closed | Replace DISCHARGE VALVE ASSEMBLY KCX
2025-03-31 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2320 | 4990328883 | 2025-03-19 | 499032 | 2025-03-19 | heating and knocking sound in cylinder. | 2023-10-26 | 2024-03-12 | 1887 | 800 | food processing | 5 | TLS Engineer attended knocking sound and overheating complaint. During visit they noticed that DV valve springs were broken and due to overheating spares damaged. Additionally another liner Lever For Valve Lifting Device damaged. Replaced defective spares as per attached relevant images and FSR for FRR approval process | null | closed | Replaced CYLINDER LINER ASSEMBLY KCX, CYLINDER LINER KC/KCX, PISTON RING SET KC/KCX, DISCHARGE VALVE ASSEMBLY KCX,RING SUCTION VALVE KC/KCX, VALVE SPRING SUCTION KC, OIL RETURN VALVE KC/KCX/PC2, OIL RETURN VALVE KC/KCX/PC2, GASKET HEAD COVER KC/KCX, GASKET SUCT STRAINER & SIDE COVER KC/KCX, GASKET LINER 1.5 mm KC/KCX, ORING VLD PISTON KCX, ORING VLD KCX,PISTON KC/KCX, GUDGEON PIN KC/KCX,BUSH CONNECTING ROD KC/KCX
2025-03-31 | Pragya Industrial Supply | Karnataka | D | Ukb Associates Pearl Ice And Cold Storage | Karnataka | KCX6 | 3394K2387 | 5012568931 | 2025-03-24 | 501256 | 2025-03-24 | oil carry over | 2023-12-30 | 2024-07-29 | null | 850 | ice plant | 7 | oil leakage from main bearing cover | null | closed | Replaced GUDGEON PIN KC/KCX,ORING VLD PISTON KCX,ORING VLD KCX & PISTON KC/KCX
2025-03-31 | Kalp Marketing | Gujrat | D | Winsor World Exports | Gujrat | KCX72 | 3474K802 | 5015548934 | 2025-03-25 | 501554 | 2025-03-24 | knocking / abnormal sound | 2024-07-20 | 2024-08-14 | 2958 | 990 | meat/fish process | 1 | Verified that there is no issue from system side. The cylinder liner has cut in 360 degree profile with ring cut pattern. Hence instruct service engineer to replace the required spares | null | closed | Replaced CYLINDER LINER KC/KCX & PISTON RING SET KC/KCX
2025-03-31 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX72 | 3474K786 | 5003368852 | 2025-03-14 | 500336 | 2025-03-13 | shaft seal leakage | 2024-05-30 | 2024-12-14 | 550 | 850 | chemical / pharma | 7 | Shaft seal mating faces worn out within 560 Hrs. Replaced new seal assembly. | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-03-31 | Gargi Engineering Enterprices Pvt Ltd | Gujrat | D | Sagar Lifesciences Pvt Ltd | Gujrat | KCX2 | 3364K2803 | 4993528834 | 2025-03-08 | 499352 | 2025-03-08 | shaft seal leakage due to oring fail | 2024-12-17 | 2025-03-08 | 6 | 700 | chemical / pharma | 3 | Compressor shaft seal leakage replace o ring and fitting compressor started with system working ok | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX
2025-03-31 | Trade Links | Secunderabad | D | Surya Ice Factory | null | KCX6 | 3394K2529 | 4943068679 | 2025-02-01 | 494306 | 2025-02-01 | oil lifting | 2024-08-30 | 2024-10-09 | 1371 | 850 | surya ice factory | 2 | Oil consumption issue, as per engineer observation per day 6 to 7 lifting. inspected the compressor and found all cylinders piston ring out No 1 & 4 cylinder liner worn out, No 4 cylinder discharge valve back leaking observed and piston seized. Replaced parts from Tl stock and restored machine. | null | closed | Replaced CYLINDER LINER KC/KCX,PISTON RING SET KC/KCX, PISTON KC/KCX & DISCHARGE VALVE ASSEMBLY KCX
2025-04-17 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Guru Gobind Singh Super Thermal Plant | Punjab | KCX4 | 3384K 3707 | 5020988961 | 2025-03-29 | 502098 | 2025-03-29 | shaft seal leakage | 2024-06-07 | 2025-01-29 | 295 | 990 | ac plant | 6 | Found Shaft Seal Leakage, So replace the o Ring but not worked so replaced the shaft seal with Viton O ring. | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-04-17 | M/S. Robin Refrigeration Works | Odisa | D | United Breweries Ltd | Khurdah, Odisha | KCX6 | 3394K 2468 | 5025048978 | 2025-04-02 | 502504 | 2025-04-10 | cylinder overheating | 2024-03-30 | 2024-09-11 | 1475 | 850 | beverage / breweries | 5 | Discharge valve ring broken and with seize liner and piston. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX, DISCHARGE VALVE ASSEMBLY KCX,RING SUCTION VALVE KC/KCX,VALVE SPRING SUCTION KC,PISTON RING SET KC/KCX, GUDGEON PIN KC/KCX.
2025-04-17 | S. B. Refrigeration Services | Bihar | D | Cool Comfort Private Limited | Bihar | KCX6 | 3394K2419 | 5020288951 | 2025-03-27 | 502028 | 2025-03-27 | cylinder overheating | 2024-01-23 | 2024-03-07 | 150 | 866 | cold storage | 2 | Delivery valve failed , overheating taken place and damages the other parts. Its a premature failure. | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, CYLINDER LINER KC/KCX,DISCHARGE VALVE ASSEMBLY KCX.
2025-04-17 | Cool Comfort Private Limited | West Bengal | D | Jaydeep Multi Cold Storage Llp | West Bengal | KCX4 | 3384K3647 | 5035008999 | 2025-04-08 | 503500 | 2025-04-08 | cylinder overheating | 2024-02-23 | 2024-03-28 | 1193 | 850 | cold storage | 1 | Discharge valve leakage. As observation that it is a premature failure | null | closed | Replaced KIT DELIVERY VALVE KC/KCX
2025-04-17 | Kalp Marketing | Gujrat | D | Rajaram Cold Storage | Gujrat | KCX31 | 3434K0265 | 5029328983 | 2025-04-04 | 502932 | 2025-04-04 | kcx pump tang broken | 2024-11-15 | 2025-02-18 | 12 | 770 | cold storage | 1 | The Driving gear shaft found broken due to the seizing of Driven gear | null | closed | Replced PUMP ELEMENT OIL PUMP KCX
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Pandit Pattan Lal Pandey Cold Storage Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2625 | 5003609003 | 2025-04-08 | 500360 | 2025-02-12 | kcx pump tang broken | 2024-12-28 | 2025-02-12 | 1.5 | 771 | cold storage | 2 | Zero Hours Complaint, Drive Gear Broken | null | closed | Replced PUMP ELEMENT OIL PUMP KCX
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Jai Mahadev Cold Storage & Ice Factory | Uttar Pradesh | KCX6 | 3394K2429 | 5017348943 | 2025-03-25 | 501734 | 2025-04-03 | knocking / abnormal sound | 2024-01-31 | 2024-03-17 | 2635 | 750 | cold storage | 2 | Discharge valve failed due to that other parts damaged | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, DISCHARGE VALVE ASSEMBLY KCX
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Magal Samridhi Industries Pvt Ltd | Uttar Pradesh | KCX6 | 3394K2680 | 5016088942 | 2025-03-25 | 501608 | 2025-03-25 | lp pressure switch malfulctioning | 2025-02-18 | 2025-02-18 | 1.2 | 750 | cold storage | 1 | Pressure switch mall fractioning and not tripping on LP | null | closed | Replaced PRESSURE SWITCH LP KP1A
2025-04-17 | Kalp Marketing | Gujrat | D | Maganlal Shivram & Co | Gujrat | PCX2 | 3106K0333 | 5023328981 | 2025-04-04 | 502332 | 2025-04-04 | pcx2 pump driving gear tang broken | 2025-03-06 | 2025-03-25 | 12 | 921 | cold storage | 1 | PCX2 Pump driving gear tang broken | null | closed | Replaced DRIVING GEAR OIL PUMP PC2, BEARING BUSH FOR OIL PUMP KC/PC2, BUSH SMALL OIL PUMP PC2, OIL PUMP ASSEMBLY PC2,DRIVEN GEAR ASSEMBLY PC2.
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Rama & Raj Ice Cold Storage | Uttar Pradesh | KC6 | 339K3857 | 4983848959 | 2025-03-28 | 498384 | 2025-03-28 | pressure gauge glycerin leakage | 2025-01-27 | 2025-03-28 | 4 | 750 | cold storage | 2 | Glycerin leakage found | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 25 KG/CM2 , 100MM DIAL, GLYSERINE FILLED
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Radha Rani Ice And Cold Storage | Uttar Pradesh | KCX3 | 3374K3662 | 4970148974 | 2025-04-01 | 497014 | 2025-04-01 | pressure gauge glycerin leakage | 2025-01-18 | 2025-04-01 | 4 | 750 | cold storage | 2 | Glycerin leakage found from pressure gauge | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-04-17 | Cool Comfort Private Limited | West Bengal | D | Nakunda Khan Cold Storage PvtLtd | West Bengal | KCX4 | 3384K4003 | 5004308917 | 2025-03-22 | 500430 | 2025-03-22 | pressure gauge not working | 2025-02-26 | 2025-03-22 | 2 | 850 | cold storage | 1 | It is premature failure and zero hour breakdown. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-04-17 | Kalp Marketing | Gujrat | D | Anand Cold Storage | Deesa | KCX3 | 3374K 3594 | 5031868984 | 2025-04-04 | 503186 | 2025-04-04 | shaft seal leakage | 2024-11-25 | 2025-02-22 | 429 | 770 | cold storage | 3 | The Shaft Seal O-ring Has noticed flatten from OD | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Vishan Swroop & Bhagat G Cold Storage Pvt Ltd | Uttar Pradesh | KC6 | 339K3848 | 4981968964 | 2025-03-29 | 498196 | 2025-03-29 | sv coil burnt | 2025-01-17 | 2025-03-29 | 4 | 750 | cold storage | 1 | SV Coil Problem | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Gurpushp Warehousing & Preservation | Uttar Pradesh | KC4 | 338K5996 | 4986848970 | 2025-03-31 | 498684 | 2025-03-31 | sv coil burnt | 2024-12-31 | 2025-03-31 | 4 | 750 | cold storage | 3 | SV Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Dr Ghure Singh Cold Storage | Uttar Pradesh | KC4 | 338K5990 | 5029108975 | 2025-04-02 | 502910 | 2025-04-04 | sv coil burnt | 2024-12-31 | 2025-03-17 | 23 | 750 | cold storage | 3 | SV Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Kirti Sheetgrah Pvt Ltd | Uttar Pradesh | KC6 | 339K3795 | 5020848963 | 2025-03-29 | 502084 | 2025-03-29 | sv coil burnt | 2024-09-30 | 2025-03-29 | 4 | 750 | cold storage | 6 | SV Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Krishna Cold Storage | Uttar Pradesh | KC6 | 339K3828 | 5029168976 | 2025-04-02 | 502916 | 2025-04-02 | sv coil burnt | 2024-12-23 | 2025-03-16 | 216 | 750 | cold storage | 3 | SV Coil Burnt. | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shanti Raj Agro Cold Storage Pvt Ltd | Uttar Pradesh | KC4 | 338K5955 | 5031288986 | 2025-04-05 | 503128 | 2025-04-05 | sv coil burnt | 2024-10-30 | 2025-02-10 | 520 | 750 | cold storage | 3 | SV COIL HAS BEEN BURNT WITH IN SOME HO URS AFTER RUNNING THE COMPRESSOR | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-04-17 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Shekhawati Chilling Centre | Rajastan | KC4 | 338K6047 | 5009068876 | 2025-03-18 | 500906 | 2025-03-18 | kc pump drive gear tang broken | 2025-02-11 | 2025-03-12 | 10 | 540 | dairy / ice cream | 1 | Zero Hour Complaint, Found Drive Gear Tang Broken | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-04-17 | Multivista Global Pvt Ltd | Gurgaon | D | Maheshwari Dairy | Uttar Pradesh | PCX2 | 3106K0299 | 5030248980 | 2025-04-03 | 503024 | 2025-04-12 | shaft seal leakage | 2024-07-04 | 2024-11-08 | 700 | 1500 | dairy / ice cream | 4 | Shaft Seal Leakage found ( No Any improvement found after replacement of O rings ) | null | closed | Replaced SHAFT SEAL ASSEMBLY PC2/AC70
2025-04-17 | Kalp Marketing | Gujrat | D | Shri Ram Frozen Foods | Madhya Pradesh | KCX72 | 3474K860 | 4975248764 | 2025-02-24 | 497524 | 2025-02-24 | cylinder overheating | 2024-11-14 | 2025-02-03 | 341 | 990 | food processing | 2 | The Delivery Valve rings observed broken resulting to damage the Sealing face of delivery valve. | null | closed | Replaced DISCHARGE VALVE ASSEMBLY KCX
2025-04-17 | Kalp Marketing | Gujrat | D | Zydus Wellness Ltd | Gujrat | KCX3 | 3374K3516 | 5028428972 | 2025-04-01 | 502842 | 2025-04-01 | kcx pump air purging | 2024-08-03 | 2024-09-30 | 276 | 766 | food processing | 1 | Air purging and oil pressure not develop issue was still there | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-04-17 | Kbtl | Thailand | E | T K Ice | Thailand | KCX6 | 3394K2500 | email | 2025-04-11 | null | 2025-04-11 | crank shaft damaged at taper portion. | 2024-07-01 | 2025-01-01 | 400 | 750 | ice plant | 6 | Crankshaft taper portion & key damaged , hitting of the flywheel on key and crank shaft due to improper fitment at site | null | closed | Flywheel Crank shaft & Key replaced from their stock
2025-04-17 | Kalp Marketing | Gujrat | D | Siddhnath Ice Factory | Gujrat | KCX4 | 3384K4015 | 5017428944 | 2025-03-26 | 501742 | 2025-03-25 | kcx pump tang broken | 2025-03-14 | 2025-03-25 | 0.5 | 880 | ice plant | 1 | The pump had stopped to develope oil pressure in running condition. Further checked and noticed that the shaft of driving gear has been broken | null | closed | Replced PUMP ELEMENT OIL PUMP KCX
2025-04-17 | Hss Solution Pvt Ltd | Rajasthan | D | Chandra Mouli Dairy Farm | Rajastan | KCX4 | 3384K3758 | 5008888965 | 2025-03-30 | 500888 | 2025-03-30 | op pressure switch malfunctioning | 2024-08-14 | 2025-03-29 | 30 | 746 | ice plant | 7 | OP switch Not working properly. | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-04-23 | Multivista Global Pvt Ltd | Gurgaon | D | Kisan Cold Storage Up | null | KC3 | 337K4965 | 5020869021 | 2025-04-11 | 502086 | 2025-04-22 | kc pump drive gear tang broken | 2025-02-12 | 2025-04-22 | 2 | 750 | cold storage | 2 | Zero Hour Complaint, Drive Gear Tang Broken | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-04-23 | Model Pneumatic Co | Punjab | D | GS Farm & Cold Store | Punjab | KCX6 | 3394K2579 | 5039109025 | 2025-04-12 | 503910 | 2025-04-12 | pressure gauge get swelled. | 2024-11-08 | 2025-02-21 | 346 | 800 | cold storage | 3 | Pressure Gauge get swelled. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 25 KG/CM2 , 100MM DIAL, GLYSERINE FILLED
2025-04-23 | Model Pneumatic Co | Punjab | D | S Mohinder Singh Cold Store | Punjab | KC6 | 339K3824 | 5039229027 | 2025-04-13 | 503922 | 2025-04-13 | sv coil burnt | 2024-12-18 | 2025-03-08 | 481 | 750 | cold storage | 3 | SV Coil Burnt | null | closed | Replaced SOLENOID VALVE COIL 230 V AC
2025-04-23 | Multivista Global Pvt Ltd | Gurgaon | D | Dairy/Ice Cream | Uttar Pradesh | PCX2 | 3106K0299 | 5039329026 | 2025-04-12 | 503932 | 2025-04-12 | shaft seal leakage | 2024-07-04 | 2024-11-08 | 700 | 1500 | dairy / ice cream | 4 | Found Liner and Piston ring worn out , Dur to that other parts also get damaged. | null | closed | Replaced SHAFT SEAL ASSEMBLY PC2/AC70,BEARING BUSH FL PC2/AC, OIL PUMP ASSEMBLY PC2, PISTON PC2, PISTON RING SET PC2, CYLINDER LINER PCX2, GASKET LINER 1.5 mm PC2.
2025-05-03 | Multivista Global Pvt Ltd | Gurgaon | D | SD Cold Storage | Uttar Pradesh | KC4 | 338K5956 | 5054669108 | 2025-04-30 | 505466 | 2025-04-30 | abnormal noise | 2024-10-30 | 2025-04-30 | 1.7 | 750 | cold storage | 6 | Liner & Piston Ring worn out. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX & PISTON RING SET KC/KCX.
2025-05-03 | Kalp Marketing | Gujrat | D | Mahavir Cold | Gujrat | KCX3 | 3374K3489 | 5053169106 | 2025-04-30 | 505316 | 2025-04-29 | cylinder overheating | 2024-07-15 | 2025-02-03 | 672 | 990 | cold storage | 7 | Delivery valve rings found in broken condition. This has caused to overheat the respective cylinder and damage the Liner,Piston and piston rings | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON RING SET KC/KCX, DISCHARGE VALVE ASSEMBLY KCX & PISTON KC/KCX
2025-05-03 | Cool Comfort Private Limited | West Bengal | D | Kishan Bandhu Himghar PvtLtd | West Bengal | KCX4 | 3384K3617 | 5036889011 | 2025-04-10 | 503688 | 2025-04-10 | cylinder overheating | 2024-02-02 | 2025-03-25 | 98 | 850 | cold storage | 12 | Compressor overheating due to discharge valve ring broken. This is a premature failure. | null | closed | Replaced KIT DELIVERY VALVE KC/KCX
2025-05-03 | Kalp Marketing | Gujrat | D | Adarsh Sheetgrah Pvt Ltd | Madhya Pradesh | KCX4 | 3384K3606 | 5031549000 | 2025-04-08 | 503154 | 2025-04-08 | cylinder overheating | 2024-01-29 | 2024-04-08 | 1965 | 767 | cold storage | 2 | After Opening the Cylinder head cover,the FSE noticed DV rings broken. This has resulted to overheat the subsequent cylinder and caused to damage the Piston,Liner , Piston rings etc | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX,DISCHARGE VALVE ASSEMBLY KCX, GUDGEON PIN KC/KCX & PISTON RING SET KC/KCX
2025-05-03 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Ambey Cold Storage | Uttar Pradesh | KC3 | 337K4947 | 5043129070 | 2025-04-23 | 504312 | 2025-04-26 | kc pump drive gear tang broken | 2025-01-21 | 2025-02-27 | 22 | 750 | cold storage | 1 | Drive Gear Tang Broken. | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-05-03 | Multivista Global Pvt Ltd | Gurgaon | D | Hsb Sharafat Ali Cold Storage | Uttar Pradesh | KC3 | 337K4934 | 5049309071 | 2025-04-23 | 504930 | 2025-04-29 | kc pump low oil pressure. | 2025-01-11 | 2025-02-26 | 115 | 750 | cold storage | 1 | There is a cut mark on the body behind the gear due to that pump not built up desire pressure. | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-05-03 | Kalp Marketing | Gujrat | D | Rajaram Cold Storage | Gujrat | KCX3 | 3374K3595 | 5043729046 | 2025-04-18 | 504372 | 2025-04-18 | kcx pump opr not working | 2024-11-15 | 2025-02-18 | 284 | 770 | cold storage | 2 | The ball & Spring assembly found lossen ,even if the tifghting of the same. this may be due to loss of spring tension. | null | closed | Replaced LUBRICATING OIL PRESSURE REGULATOR ASSLY. KCX & CONTROL OIL PRESSURE REGULATOR ASSLY. KCX.
2025-05-03 | Kalp Marketing | Gujrat | D | Dwarkesh Hi-Tech Cold Storage | Gujrat | KCX2 | 3364K 2815 | 5033868996 | 2025-04-08 | 503386 | 2025-04-08 | shaft seal leakage | 2025-01-11 | 2025-03-10 | 499 | 770 | cold storage | 2 | The shaft seal O-ring from flatten from OD caused to damaged the shaft seal facing | null | closed | Replaed SHAFT SEAL ASSEMBLY KC/KCX
2025-05-03 | Kalp Marketing | Gujrat | D | Pep Foods | Gujrat | KCX31 | 3434K0251 | 5039169028 | 2025-04-13 | 503916 | 2025-04-13 | kcx pump tang broken | 2024-06-27 | 2025-02-19 | 46 | 935 | food processing | 7 | Further checking to the compressor noticed that driving gear shaft has been broken. | null | closed | Replaced PUMP ELEMENT OIL PUMP KCX
2025-05-03 | Gargi Engineering Enterprices Pvt Ltd | Gujrat | D | Shankar Ice Factory | Gujrat | KCX4 | 3384K3987 | 5007428958 | 2025-03-28 | 500742 | 2025-03-28 | k5 valve thread damaged | 2025-02-13 | 2025-03-28 | 3 | 830 | ice plant | 1 | Need to address the issue as K-5 valve getting damaged unnecessary. | null | closed | Replaced K5 VALVE KC/KCX/PC2, ADAPTOR M12 X1.5P(F) X7/16" 20 UNF(M).
2025-05-03 | Multivista Global Pvt Ltd | Gurgaon | D | SM Ice & Cold Storage | Uttar Pradesh | KC3 | 337K4976 | 5049889076 | 2025-04-24 | 504988 | 2025-04-24 | kc pump drive gear tang broken | 2025-03-18 | 2025-04-21 | 5.7 | 750 | ice plant | 1 | Zero Hour Complaint, Oil Pump Tang Broken. | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-05-03 | Multivista Global Pvt Ltd | Tamil Nadu | D | Shakayam Ice Factory | Tamil Nadu | KCX6 | 3394K2469 | 5037069037 | 2025-04-15 | 503706 | 2025-04-20 | pressure gauge not working | 2025-06-20 | 2025-04-20 | 58 | 771 | ice plant | 9 | Zero Hr. complaint. Reviewed with HO and approving for replacement. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-05-05 | Kalp Marketing | Gujrat | D | Gopi Cold Storage | Mansa, Punjab | KCX3 | 3374K3249 | 5051029091 | 2025-04-26 | 505102 | 2025-04-26 | abnormal noise | 2024-10-16 | 2024-02-08 | 720 | 659 | cold storage | 3 | The Liner has been cut in 360 degree pattern. also found that the lubricating oil pressure regulator's assembly(Ball & Spring) is malfunctioning | null | closed | Replaced LUBRICATING OIL PRESSURE REGULATOR ASSLY. KCX, CYLINDER LINER KC/KCX & PISTON RING SET KC/KCX
2025-05-05 | Parag Marketing Services | Chhattisgarh | D | Bahubali Cold Storage And Logistics | Chhattisgarh | KCX4 | 3384K3664 | 5052229090 | 2025-04-26 | 505222 | 2025-04-26 | kcx pump tang broken | 2024-03-16 | 2024-05-20 | 1107 | 770 | cold storage | 2 | Pump tang was broken. | null | closed | Replaced PUMP ELEMENT OIL PUMP KCX
2025-05-05 | Multivista Global Pvt Ltd | Gurgaon | D | Bveg Foods Private Limited | Haryana | KCX51 | 3454K243 | 5051169092 | 2025-04-25 | 505116 | 2025-04-25 | discharge temperature alarm. | 2024-02-12 | 2024-07-23 | 1298 | 990 | food processing | 4 | Found ware damage of sensors | null | closed | Replaced DISCHARGE TEMPERATURE SENSOR, PT1000 WITH 12 MTR CABLE LENGTH. RANGE ( 50 to 250 Deg C)
2025-05-05 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K083 | 5050929078 | 2025-04-25 | 505092 | 2025-04-25 | high oil consumptionvld oring | 2023-11-30 | 2024-10-14 | 1055 | 850 | food processing | 9 | Joint Visit has been made with Kalp Team by our engineer Mr. Sachin Amarseda. The gasket sets and O-ring set have been consumed 2nd time to resolve the oil carry over issue. hence given approval for Free relacement | null | closed | Replaced SET OF O RINGS FOR KCX9, KCX63 & KCX72 DISH END COMPR., SET OF GASKETS FOR KCX12, ORING VLD PISTON KCX 3 nos , ORING VLD KCX 3 nos.
2025-05-05 | Trade Links | Secunderabad | D | Sri Vishnu Smitha Ice Factory | Andhra Pradesh | KCX4 | 3384K3578 | 5053209107 | 2025-04-30 | 505320 | 2025-04-30 | cylinder overheating | 2024-01-15 | 2024-04-06 | PC | 850 | ice plant | 2 | No 2 & 3 cylinders over heating observed, inspection was done & found discharge valve back leaking , spring also found broken in 2 pieces. Other 2 cylinders also inspection and found liner and piston ring worn out. other 2 No discharge valves spring also found weak and need to replaced with new one. | 2,3 | closed | Replaced VALVE SPRING SUCTION KC2nos , RING SUCTION VALVE KC/KCX, BUSH CONNECTING ROD KC/KCX,GUDGEON PIN KC/KCX,BUFFER SPRING KC/KCX, DISCHARGE VALVE ASSEMBLY KCX 4 nos, PISTON KC/KCX, PISTON RING SET KC/KCX 4nos, CYLINDER LINER KC/KCX 4nos.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Rama & Raj Ice Cold Storage | Uttar Pradesh | KC4 | 338K6052 | 5050949082 | 2025-04-25 | 505094 | 2025-05-03 | abnormal noise | 2025-02-20 | 2025-03-28 | 426 | 750 | cold storage | 1 | Found Liner and piston ring worn out, also found cut mark in oil pump body. | null | closed | Replaced PISTON KC/KCX1nos, CYLINDER LINER KC/KCX3nos , PISTON RING SET KC/KCX 4 nos, BEARING BUSH BIG END CON ROD KC/KCX 4nos & OIL PUMP ASSEMBLY KC1nos.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Ambey Cold Storage | Uttar Pradesh | KC3 | 337K4926 | 5043109069 | 2025-04-23 | 504310 | 2025-04-26 | abnormal noise | 2025-01-06 | 2025-02-27 | 472 | 750 | cold storage | 1 | Liner and Piston Ring worn out. | null | closed | Replaced CYLINDER LINER KC/KCX2nos & PISTON RING SET KC/KCX2nos
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Rasila Cold Storage Llp | Uttar Pradesh | KC4 | 338K6007 | 5045389055 | 2025-04-19 | 504538 | 2025-04-26 | abnormal noise | 2025-01-10 | 2025-03-21 | 496 | 750 | cold storage | 2 | Liner and piston ring worn out . | null | closed | Replaced CYLINDER LINER KC/KCX2nos, PISTON KC/KCX 2 nos, & PISTON RING SET KC/KCX2nos.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Rasila Cold Storage Llp | Uttar Pradesh | KC3 | 337K4942 | 5045369054 | 2025-04-19 | 504536 | 2025-04-26 | abnormal noise | 2025-01-16 | 2025-03-21 | 400 | 750 | cold storage | 2 | Liner and piston ring worn out, and one solenoid coil also found burnt. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON RING SET KC/KCX3NOS & SOLENOID VALVE 3WAY.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Mata Durga Cold Storage | Uttar Pradesh | KCX6 | 3394K 2621 | 5045069048 | 2025-04-18 | 504506 | 2025-04-23 | abnormal noise | 2024-12-30 | 2025-04-15 | 6 | 750 | cold storage | 3 | Liner and Piston ring worn out. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX & PISTON RING SET KC/KCX
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Ram Cold Storage | Uttar Pradesh | KC6 | 339K3865 | 5053289102 | 2025-04-29 | 505328 | 2025-05-07 | abnormal noise | 2025-02-08 | 2025-03-01 | 799 | 750 | cold storage | 1 | Liner and piston worn out | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX & PISTON RING SET KC/KCX.
2025-05-07 | Kalp Marketing | Gujrat | D | Mansadevi Cold Storage | Gujrat | KCX4 | 3384K 3805 | 5045129045 | 2025-04-26 | 504512 | 2025-04-26 | abnormal noise | 2024-10-21 | 2025-02-20 | 720 | 881 | cold storage | 4 | The liner has cut in 360 degree pattern while there is no evidence of liquid entry / Foreign Particles. | null | closed | Replaced PISTON RING SET KC/KCX & CYLINDER LINER KC/KCX.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Mahadev Enterprises | Uttar Pradesh | KC4 | 338K5932 | 5044849043 | 2025-04-17 | 504484 | 2025-04-17 | high oil consumption | 2024-02-19 | 2024-03-17 | 1860 | 750 | cold storage | 1 | This compressor had oil carry problem( later compressor was replaced), in which these 4 rings were provided by MVGL from their stock and forgot to raise FRR | null | closed | Replaced PISTON RING SET KC/KCX 4nos.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Vashisht Enterprises | Uttarakhand | KCX42 | 3444K500 | 5043429039 | 2025-04-16 | 504342 | 2025-05-05 | abnormal noise | 2024-11-28 | 2025-02-11 | 485 | 750 | food processing | 2 | Piston ring and liner get worn out. | null | closed | Replaced CYLINDER LINER KC/KCX3nos, PISTON KC/KCX2nos & PISTON RING SET KC/KCX3nos.
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Bankey Bihari Foods | Uttar Pradesh | KCX6 | 3394K2300 | 5038409022 | 2025-04-18 | 503840 | 2025-04-18 | high oil consumption | 2023-10-11 | 2024-02-12 | 857 | 850 | food processing | 3 | Piston ring worn out and close gap increase up to 1.2 mm | null | closed | Replaced PISTON RING SET KC/KCX 6nos
2025-05-07 | Kalp Marketing | Gujrat | D | Shree Kamal Nayan Frozen Food Llp | Madhya Pradesh | KCX21 | 3424K178 | 5049929085 | 2025-04-26 | 504992 | 2025-04-26 | knocking / abnormal sound | 2024-12-13 | 2025-03-28 | 155 | 760 | food processing | 3 | The Deleivery Valve rings found in broken condition resulting to damage the cylinder assembly | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, BUFFER SPRING KC/KCX, CYLINDER LINER KC/KCX, RING SUCTION VALVE KC/KCX, VALVE SPRING SUCTION KC 2nos & DISCHARGE VALVE ASSEMBLY KCX
2025-05-07 | Kalp Marketing | Gujrat | D | Malwa Frozen Food | Madhya Pradesh | KCX63 | 3464K205 | 5050209084 | 2025-04-26 | 505020 | 2025-04-26 | shaft seal leakage | 2024-01-25 | 2024-02-15 | 312 | 935 | food processing | 1 | Oil leakage by replacing the O-rings.The lekage was still there.hence given approval to replace the entire shaft seal assembly | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-05-07 | Trade Links | Secunderabad | D | Vabilisetty Ice Factory | Andhra Pradesh | KCX3 | 3374K3477 | 5047709086 | 2025-04-26 | 504770 | 2025-04-28 | cylinder overheating | 2024-06-22 | 2024-06-28 | 1199 | 850 | ice plant | 1 | No 2 cylinder discharge valve leaking due to the cylinder getting overheating and resulted damage of internal parts. | 2 | closed | Replaced PISTON KC/KCX, CYLINDER LINER KC/KCX, DISCHARGE VALVE ASSEMBLY KCX, GUDGEON PIN KC/KCX, BUSH CONNECTING ROD KC/KCX, & PISTON RING SET KC/KCX.
2025-05-07 | Parag Marketing Services | Chhattisgarh | D | HiAchal Ice Factory | Chhatisgarh | PCX2 | 3106K0302 | 5032669061 | 2025-04-21 | 503266 | 2025-04-18 | high oil consumption | 2024-07-17 | 2024-09-07 | 1681 | 1150 | ice plant | 1 | Engineer attended high oil consumption for 2.5 litres for 48 hrs. Upon further inspection, the head covers were opened, revealing: 1) Piston ring rubbed and close gap: 1.4 to 0.8 mm 2) Piston and cylinder liners showed signs of rubbing | null | closed | Replaced PISTON FLAT HEAD PCX2 2Nos , CYLINDER LINER PCX22 nos & PISTON RING SET PC22nos.
2025-05-07 | Parag Marketing Services | MH | D | Suman Ice Factory | Maharashtra | KCX2 | 3364K2731 | 5029249073 | 2025-04-23 | 502924 | 2025-04-23 | op pressure switch malfunctioning | 2024-08-07 | 2025-04-23 | 17 | 750 | ice plant | 6 | OP switch malfunctioning | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-05-07 | Hss Solution Pvt Ltd | Rajasthan | D | Rajgir Crrogenic Gases Llp | Rajastan | KCX84 | 3305K038 | 4994809088 | 2025-04-26 | 499480 | 2025-04-26 | kcx pump tang broken | 2024-05-27 | 2025-04-26 | 4 | 938 | others | 11 | Zero Hours Defect , Drive Gear Broken | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-05-07 | Kalp Marketing | Gujrat | D | Arvee Laboraties India Ltd | Gujrat | KCX4 | 3384K3798 | 5048069068 | 2025-04-23 | 504806 | 2025-04-23 | high oil consumptionvld oring | 2024-10-05 | 2024-12-24 | 1682 | 880 | chemical / pharma | 2 | On inspection of compressor for oil carry over complaint, Noticed that VLD piston O-rings have flatten from OD. this is resulting to oil carry over.Moreover ORVs also noticed were leaking | null | closed | Replaced ORING VLD PISTON KCX, ORING VLD KCX & OIL RETURN VALVE KC/KCX/PC2
2025-05-07 | Multivista Global Pvt Ltd | Gurgaon | D | India Pesticide Ltd | Uttar Pradesh | KCX84 | 3305K048 | 5048289087 | 2025-04-26 | 504828 | 2025-05-02 | kcx pump tang broken | 2024-12-27 | 2025-01-27 | 1166 | 750 | chemical / pharma | 1 | Drive Dear Tang Broken | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-05-19 | Cool Comfort Private Limited | West Bengal | D | Jaydeep Multi Cold Storage Llp | West Bengal | KCX4 | 3384K3643 | 5060189136 | 2025-05-06 | 506018 | 2025-05-06 | cylinder overheating | 2024-02-23 | 2024-03-28 | 1048 | 850 | cold storage | 1 | Discharge valve ring is broken (2No). As observation that it is a premature failure. | null | closed | Replaced KIT DELIVERY VALVE KC/KCX 2Nos
2025-05-19 | Multivista Global Pvt Ltd | Gurgaon | D | Kumar-Milk Protein Private Limited | Uttar Pradesh | KC2 | 336K3443 | 5050009077 | 2025-04-24 | 505000 | 2025-04-24 | high oil consumptionorv malfuction | 2024-12-20 | 2025-03-20 | 159 | 750 | dairy / ice cream | 3 | ORV mall functioning. | null | closed | Replaced OIL RETURN VALVE KC/KCX/PC2
2025-05-19 | Multivista Global Pvt Ltd | Gurgaon | D | Maheshwari Dairy | Uttar Pradesh | PCX2 | 3106K0299 | 5059109134 | 2025-05-05 | 505910 | 2025-05-05 | sv coil burnt | 2024-07-04 | 2024-11-08 | 203 | 1500 | dairy / ice cream | 4 | Solenoid coil burnt | null | closed | Replaced SOLENOID VALVE (TEFLON), 3 WAY, 230V, 50HZ,NC
2025-05-19 | Gargi Engineering Enterprices Pvt Ltd | MH | D | Global Gourme Pvt Ltd | Vadodara , Gujarat | KCX72 | 3474K771 | 5052889097 | 2025-04-28 | 505288 | 2025-04-28 | kcx manifold fitting leak | 2024-05-14 | 2025-02-07 | 80 | 990 | food processing | 8 | Identical failure due soft material of housing.Thread on bolt & housing worn out | null | closed | Replaced BOLT HEX SCREW SOCKET HD M10X1.5X65L, BOLT HEX SOCKET HEAD, M10 X 1.5 X 40L & FILTER HOUSING.
2025-05-19 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K080 | 5055609129 | 2025-05-05 | 505560 | 2025-05-05 | kcx pump air purging | 2023-10-31 | 2024-10-28 | 1527 | 800 | food processing | 12 | Air purging issue were reported in the each start of the compressor | null | closed | Replaced MALE RUN TEE (POSITIONAL), 6MM OD X 6MM OD X 1/4'' BSP(M), LIGHT, SS., THRUST RING PUMP END BEARING COVER KCX & OIL PUMP ASSEMBLY KCX
2025-05-19 | Trade Links | Secunderabad | D | Kmc Ice Factory | Andhra Pradesh | KCX4 | 3384K3863 | 5037829029 | 2025-04-13 | 503782 | 2025-04-13 | abnormal noise | 2024-11-28 | 2025-03-24 | 679 | 750 | ice plant | 3 | All cylinders liners and piston rings worn out , No 4 cylinder discharge valve back leaking and other parts also found damaged | null | closed | Replaced VALVE SPRING SUCTION KC 2nos, RING SUCTION VALVE KC/KCX1nos, DISCHARGE VALVE ASSEMBLY KCX 1nos, BUFFER SPRING KC/KCX 1nos, GUDGEON PIN KC/KCX1nos, BUSH CONNECTING ROD KC/KCX1nos, PISTON RING SET KC/KCX4nos, PISTON KC/KCX1nos & CYLINDER LINER KC/KCX 4nos.
2025-05-19 | Cool Comfort Private Limited | West Bengal | D | Jharna Enterprise | West Bengal | PCX2 | 3106K0274 | 5043749047 | 2025-04-18 | 504374 | 2025-04-18 | cylinder overheating | 2024-02-12 | 2024-03-18 | 2491 | 1100 | ice plant | 1 | Discharge valve broken with shaft seal leakage. As observation its premature failure. | null | closed | Replaced DELIVERY VALVE ASSLY PCX2 & SHAFT SEAL ASSEMBLY PC2/AC70.
2025-05-19 | Trade Links | Secunderabad | D | Ananda Fisheries | Telangana | KCX6 | 3394K2601 | 5056389127 | 2025-05-03 | 505638 | 2025-05-03 | high oil consumption | 2024-11-26 | 2024-12-07 | 629 | 850 | ice plant | 1 | Oil lifting due to Premature wearin g of Liners & Piston rings, ORV back leaking. | null | closed | Replaced CYLINDER LINER KC/KCX 2nos , PISTON KC/KCX1nos, PISTON RING SET KC/KCX 3nos OIL ,RETURN VALVE KC/KCX/PC21nos.
2025-05-19 | Gargi Engineering Enterprices Pvt Ltd | MH | D | Jay Jalaram Lifesciences Pvt Ltd | Gujrat | KCX3 | 3374K3528 | 5049009098 | 2025-04-29 | 504900 | 2025-04-28 | kcx pump air purging | 2024-08-29 | 2025-01-17 | 56 | 767 | chemical / pharma | 4 | Air Purging issue. oil pump need to replace. | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-05-19 | Trade Links | Secunderabad | D | Arene Life Science Pvt Ltd | Telangana | KCX6 | 3394K2499 | 5036669010 | 2025-04-10 | 503666 | 2025-04-10 | shaft seal leakage | 2024-06-15 | 2024-10-30 | 2636 | 850 | chemical / pharma | 3 | Shaft seal leakage issue on KCX 6 compressor and this compressor is working on R22 Refringent gas. | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-05-19 | Gargi Engineering Enterprices Pvt Ltd | MH | D | Sagar Lifesciences Pvt Ltd | Gujrat | KCX9 | 3404K385 | 5044329060 | 2025-04-21 | 504432 | 2025-04-21 | v belt loose | 2024-12-17 | 2025-03-08 | 120 | 660 | chemical / pharma | 3 | V-belts get loosened. needs to replace. Total running hours 120. | null | closed | Replaced V BELT SPACESAVER SPC 4000
2025-05-22 | Trade Links | Secunderabad | D | Kurnool Dist Milk Producers Mutually Aided Co-Op Union Ltd | Andhra Pradesh | KCX3 | 3374K3493 | 5052509135 | 2025-05-06 | 505250 | 2025-04-28 | high oil consumption | 2024-07-16 | 2024-10-10 | 1955 | 850 | cold storage | 2 | Oil lifting issue and inspected and found liners and piston ring out | null | closed | Replaced CYLINDER LINER KC/KCX3nos & PISTON RING SET KC/KCX3nos
2025-05-22 | Multivista Global Pvt Ltd | Tamil Nadu | D | G K Dairy | Tamil Nadu | KCX2 | 3364K2727 | 5068469157 | 2025-05-12 | 506846 | 2025-05-14 | kcx pump tang broken | 2024-07-31 | 2025-04-24 | 191 | 988 | dairy / ice cream | 9 | OIL PUMP HOUSING DAMAGE. TANG BROKE N. | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-05-22 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Andhra Pradesh | KCX4 | 3384K3830 | 5058309151 | 2025-05-09 | 505830 | 2025-05-05 | high oil consumption | 2024-11-07 | 2024-12-27 | 1365 | 850 | ice plant | 1 | No 1 &3 cylinder liners 7 piston ring worn out | null | closed | Replaced CYLINDER LINER KC/KCX2nos & PISTON RING SET KC/KCX2nos
2025-05-22 | Trade Links | Secunderabad | D | Godavari Ice & Cold Storage | Andhra Pradesh | KCX4 | 3384K3659 | 5052989103 | 2025-04-29 | 505298 | 2025-04-29 | high oil consumption | 2024-03-12 | 2024-05-31 | 4194 | 800 | ice plant | 2 | No 2 cylinder and piston rings worn out | null | closed | Replaced PISTON RING SET KC/KCX1nos & CYLINDER LINER KC/KCX 1nos.
2025-05-22 | Trade Links | Secunderabad | D | Kader Exports Private Limited Ap | null | KCX72 | 3474K729 | 5059989147 | 2025-05-07 | 505998 | 2025-05-07 | knocking / abnormal sound | 2023-12-28 | 2024-04-06 | 5671 | 950 | meat/fish process | 3 | NO 1 cylinder discharge valve leaking & other parts damaged. | 1 | closed | Replaced DISCHARGE VALVE ASSEMBLY KCX & PISTON RING SET KC/KCX
2025-05-31 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Carlsberg India Pvt Ltd | Haryana | KCX6 | 3394K2304 | 5089989220 | 2025-05-27 | 508998 | 2025-05-27 | high oil consumption | 2023-10-28 | 2023-12-30 | 3810 | 950 | beverage / breweries | 2 | Liner and piston ring set worn out. | null | closed | Replaced CYLINDER LINER KC/KCX6nos, PISTON RING SET KC/KCX 6nos & PISTON KC/KCX 4nos.
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Parwana Cold Storage | Uttar Pradesh | KC4 | 338K5942 | 5086109206 | 2025-05-20 | 508610 | 2025-05-23 | abnormal noise | 2024-05-30 | 2025-02-12 | 386 | 750 | cold storage | 8 | Cylinder & Liner Piston Worn out. | null | closed | Replaced CYLINDER LINER KC/KCX3nos, PISTON KC/KCX1nos, PISTON RING SET KC/KCX4nos.
2025-05-31 | Kalp Marketing | Gujrat | D | Radhakrishna Agri Cold Storage | Gujrat | KCX3 | 3374K3342 | 5075329212 | 2025-05-26 | 507532 | 2025-05-23 | abnormal noise | 2023-12-28 | 2024-03-26 | 526 | 640 | cold storage | 3 | The liner has cut in 360 degree profile resulting to damage the piston rings as well | null | closed | Replaced CYLINDER LINER KC/KCX1nos & PISTON RING SET KC/KCX1nos
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Bihari Cold Storage | Uttar Pradesh | KC4 | 338K6008 | 5074949178 | 2025-05-16 | 507494 | 2025-05-24 | abnormal noise | 2025-01-10 | 2025-03-28 | 1123 | 750 | cold storage | 2 | Liner and Piston Ring Worn Out. | null | closed | Replaced CYLINDER LINER KC/KCX4nos, PISTON RING SET KC/KCX4nos, PISTON KC/KCX2nos.
2025-05-31 | Kalp Marketing | Gujrat | D | Anand Cold Storage | Deesa | KCX3 | 3374K3594 | 5056469130 | 2025-05-05 | 505646 | 2025-05-05 | bearing cover fitting leak | 2024-11-25 | 2025-02-22 | 526 | 770 | cold storage | 3 | The Shaft Seal O-ring found flatten from OD resulting to Oil leakage. The FSE also noticed that OPR O-rings have flatten ans Oil leakage from bearing cover | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX1nos, ORING OPR KCX1nos, & ORING BEARING COVER KCX1nos
2025-05-31 | Parag Marketing Services | MH | D | Royal Foodstuffs Pvt Ltd | Maharashtra | KCX42 | 3444K493 | 5086669209 | 2025-05-24 | 508666 | 2025-05-24 | high oil consumption | 2024-10-19 | 2025-02-08 | 1310 | 850 | cold storage | 3 | High oil consumption complaint.. During visit they had taken open air trail and found oil throw from cylinder no. cylinder liner no. 1,3,4,5 and step cut marks on these liners. Also., Piston ring close gap was found near 0.80mm | null | closed | Replaced PISTON RING SET KC/KCX4nos, PISTON KC/KCX4nos, PISTON RING SET KC/KCX4nos.
2025-05-31 | Cool Comfort Private Limited | West Bengal | D | Vivekananda Himghar Pvt Ltd | West Bengal | KCX4 | 3384K3520 | 5051369083 | 2025-04-24 | 505136 | 2025-04-26 | high oil consumption | 2023-12-14 | 2024-03-12 | 1738 | 825 | cold storage | 2 | Found that the liner was worn out and extracting oil from all cylinders | null | closed | Replaced PISTON RING SET KC/KCX4nos, PISTON KC/KCX2nos, CYLINDER LINER KC/KCX2nos.
2025-05-31 | Cool Comfort Private Limited | West Bengal | D | Nirbhar Multipurpose Cold Storage Pvt Ltd | West Bengal | KCX4 | 3384K3930 | 5068489170 | 2025-05-14 | 506848 | 2025-05-25 | knocking / abnormal sound | 2025-01-09 | 2025-03-18 | 378 | 850 | cold storage | 2 | All discharge valve ring and spring damage , but there are no foreign particles , As observation that it is a premature failure. | null | closed | Replaced DISCHARGE VALVE ASSEMBLY KCX
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | DK Cold Storage & General Mills | Uttar Pradesh | KC3 | 337K4952 | 5079069195 | 2025-05-20 | 507906 | 2025-05-20 | pressure gauge leak | 2025-01-27 | 2025-02-19 | 260.2 | 750 | cold storage | 1 | Glycine leakage and needle out from scale. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Rastogi Cold Storage And Allied Industries | Uttar Pradesh | KC6 | 339K3820 | 5071849168 | 2025-05-14 | 507184 | 2025-05-15 | sv coil burnt | 2024-12-17 | 2025-03-09 | 1016 | 750 | cold storage | 2 | Coil Has Been Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-05-31 | Kalp Marketing | Gujrat | D | Gwala Dairy Utpad | Madhya Pradesh | KCX3 | 3374K3432 | 5068689184 | 2025-05-17 | 506868 | 2025-05-17 | air purging problem | 2024-03-09 | 2025-04-04 | 364 | 767 | dairy / ice cream | 1 | Air purging issue was noticed from the commissioning | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-05-31 | Multivista Global Pvt Ltd | Tamil Nadu | D | Ar Dairy Food Pvt Ltd | Tamil Nadu | KCX4 | 3384K3733 | 5070409186 | 2025-05-17 | 507040 | 2025-05-17 | high oil consumption | 2024-07-11 | 2024-10-17 | PC | 933 | dairy / ice cream | 1 | Heavy wear and tear observed in liner and piston ring | null | closed | Replaced CYLINDER LINER KC/KCX4nos, PISTON RING SET KC/KCX4nos, OIL RETURN VALVE KC/KCX/PC21nos, ORING VLD PISTON KCX4nos, ORING VLD KCX4nos.
2025-05-31 | Hss Solution Pvt Ltd | Rajasthan | D | Dharampal Satyapal Ltd | Udaipur,Rajastan | KCX4 | 3384K3701 | 5078349192 | 2025-05-19 | 507834 | 2025-05-19 | krms sensor not working | 2024-05-15 | 2025-04-08 | 683 | 768 | dairy / ice cream | 12 | Discharge sensor mall functioning. | null | closed | Replaced DISCHARGE TEMPERATURE SENSOR, PT1000 WITH 12 MTR CABLE LENGTH. RANGE ( 50 to 250 Deg C)
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Bveg Foods Private Limited | Haryana | KCX51 | 3454K243 | 5085189201 | 2025-05-26 | 508518 | 2025-05-30 | abnormal noise | 2024-02-12 | 2024-07-23 | 1308 | 990 | food processing | 5 | HP Liner And Ring Set worn Out. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX,PISTON RING SET KC/KCX, GUDGEON PIN KC/KCX,DISCHARGE VALVE ASSEMBLY KCX,NEEDLE ROLLER BEARING KC/KCX2nos,RING SUCTION VALVE KC/KCX.
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Galaxy Agro Frozen Foods | Uttarakhand | KCX42 | 3444K517 | 5078289191 | 2025-05-19 | 507828 | 2025-05-25 | abnormal noise | 2025-02-21 | 2025-03-17 | 258 | 750 | food processing | 1 | HP Liner And Ring Set worn Out. | null | closed | Replaced CYLINDER LINER KC/KCX2nos, PISTON KC/KCX2nos, PISTON RING SET KC/KCX2nos.
2025-05-31 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K082 | 5085109208 | 2025-05-23 | 508510 | 2025-05-23 | cylinder overheating | 2023-11-30 | 2024-10-14 | 1759 | 746 | food processing | 8 | The DV rings found broken result in to damage the liners,pison,piston rings,gudgeon pin | null | closed | Replaced CYLINDER LINER KC/KCX, GUDGEON PIN KC/KCX, PISTON KC/KCX, PISTON RING SET KC/KCX,LOCK PLATE CON ROD & INTER. HSG BOLT KC/KCX2nos, BEARING BUSH BIG END CON ROD KC/KCX ,DISCHARGE VALVE ASSEMBLY KCX.
2025-05-31 | Multivista Global Pvt Ltd | Gurgaon | D | Vedant Edible Products Pvt Ltd | Uttar Pradesh | KCX84 | 3305K033 | 5078269190 | 2025-05-19 | 507826 | 2025-05-26 | high oil consumption | 2023-08-29 | 2023-12-30 | 1234 | 950 | food processing | 4 | Piston Ring Worn Out. | null | closed | Replaced PISTON RING SET KC/KCX 5nos
2025-05-31 | Parag Marketing Services | MH | D | Royal Foodstuffs Pvt Ltd | Maharashtra | KCX72 | 3474K774 | 5058589210 | 2025-05-24 | 505858 | 2025-05-24 | high oil consumption | 2024-05-09 | 2025-03-07 | 19 | 900 | food processing | 9 | High oil consumption complaint.. During visit they had taken open air trail and found oil throw from cylinder no. 1,2,4,6,7,8. Also., Piston ring close gap was found near 1mm. | null | closed | Replaced PISTON KC/KCX6nos, PISTON RING SET KC/KCX9nos, CYLINDER LINER KC/KCX6nos, SPRING CURTAIN, LINER ASSEMBLY KC/KCX6nos & LOCK PLATE CON ROD & INTER. HSG BOLT KC/KCX18nos.
2025-05-31 | Kalp Marketing | Gujrat | D | Nestle India Limited | Gujrat | KCX12 | 3415K083 | 5085089207 | 2025-05-23 | 508508 | 2025-05-23 | high oil consumption | 2023-11-30 | 2024-10-14 | 1076 | null | food processing | 8 | Float valve assembly is not working in 3 compressors | null | closed | Replaced FLOAT VALVE ASSEMBLY FOR OIL SEP 3nos
2025-05-31 | Multivista Global Pvt Ltd | Tamil Nadu | D | Shakayam Ice Factory | Tamil Nadu | KCX6 | 3394K2469 | 5074989185 | 2025-05-17 | 507498 | 2025-05-17 | high oil consumption | 2024-06-20 | 2025-04-20 | PC | 771 | ice plant | 9 | Heavy wear and tear observed in the liner and piston ring | null | closed | Replaced CYLINDER LINER KC/KCX 6nos, PISTON RING SET KC/KCX6nos, PISTON KC/KCX6nos, ORING VLD PISTON KCX6nos, ORING VLD KCX6nos.
2025-05-31 | Trade Links | Goa | D | Natasha Ice Plant & Cold Storage | null | KCX2 | 3364K2705 | 5071009171 | 2025-05-15 | 507100 | 2025-05-14 | shaft seal leakage | 2024-06-24 | 2024-08-20 | 1684 | 800 | ice plant | 1 | Shaft seal leakage complaint and replaced defective shaft seal O rings and resolved complaint | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX
2025-06-23 | M/S. Robin Refrigeration Works | Odisa | D | United Breweries Ltd | Khurdah, Odisha | KCX6 | 3394K2468 | 5090869257 | 2025-06-03 | 509086 | 2025-06-10 | high oil consumption | 2024-03-30 | 2024-09-18 | 2226 | 850 | beverage / breweries | 5 | Asan open air test and found that there was oil lift in cylinder number 5,2 and discharge valve 1 no leakage. As observation that it is a premature failure. | 5, 2 | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX, PISTON RING SET KC/KCX5nos, ORING VLD PISTON KCX 6nos, ORING VLD KCX6nos, KIT DELIVERY VALVE KC/KCX, GASKET HEAD COVER KC/KCX 6nos.
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Nambardar Sheetgrah | Uttar Pradesh | KC4 | 338K5888 | 5096749248 | 2025-06-02 | 509674 | 2025-06-05 | abnormal noise | 2023-12-29 | 2024-03-12 | 3146 | 750 | cold storage | 2 | Liner and piston ring worn out | null | closed | Replaced CYLINDER LINER KC/KCX 4nos, PISTON KC/KCX 2nos PISTON RING SET KC/KCX 4nos.
2025-06-23 | Kalp Marketing | Gujrat | D | Shreenath Cold Storage | Madhya Pradesh | KCX4 | 3384K3463 | 5087069221 | 2025-05-27 | 508706 | 2025-05-27 | cylinder overheating | 2023-10-26 | 2024-01-31 | 3952 | 767 | cold storage | 14 | The DV rings found broken resulting to overhaet the respective cylinder and caused to damage the Piston,Piston rings,Cylinder Liner and gudgeon pin | null | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX,GUDGEON PIN KC/KCX, CYLINDER LINER KC/KCX, DISCHARGE VALVE ASSEMBLY KCX.
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Sumanglam Cold Storage | Uttar Pradesh | KCX6 | 3394K2333 | 5099409264 | 2025-06-05 | 509940 | 2025-06-18 | high oil consumption | 2023-11-20 | 2024-02-15 | 1703 | 750 | cold storage | 2 | Oil Throw from cylinder no-2 | 2 | closed | Replaced PISTON RING SET KC/KCX
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | H Saqlaini Cold Store | Uttar Pradesh | KC3 | 337K4963 | 5074549235 | 2025-05-29 | 507454 | 2025-06-01 | high oil consumption | 2025-02-22 | 2025-03-19 | 501.3 | 750 | cold storage | 1 | Liner and Piston Ring worn Out. | null | closed | Replaced PISTON RING SET KC/KCX 3nos, CYLINDER LINER KC/KCX, PISTON KC/KCX
2025-06-23 | Kalp Marketing | Gujrat | D | Adani Wilmar Limited | Gujrat | KCX3 | 3374K3604 | 5088209227 | 2025-05-28 | 508820 | 2025-05-27 | high oil consumption | 2024-11-22 | 2025-03-13 | 1115 | 768 | cold storage | 3 | The liner has cut in 360 degree ring pattern from one point. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON RING SET KC/KCX, BEARING BUSH BIG END CON ROD KC/KCX
2025-06-23 | Model Pneumatic Co | Punjab | D | Guru Hargobind Cold Store | Punjab | KC3 | 337K4889 | 5090409226 | 2025-05-27 | 509040 | 2025-05-27 | kc pump low oil pressure issue | 2024-04-30 | 2025-03-18 | 910 | 750 | cold storage | 10 | Oil pressure not built up desire pressure only build up 1.4Kg/cm2 maximum | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Parwana Cold Storage | Uttar Pradesh | KC4 | 338K5942 | 5101689270 | 2025-06-06 | 510168 | 2025-06-12 | kc pump low oil pressure issue | 2024-05-30 | 2025-02-12 | 388.9 | 750 | cold storage | 8 | Found deep Cut Mark on cover plate of Oil pump. | null | closed | Replaced OIL PUMP ASSEMBLY KC
2025-06-23 | Kalp Marketing | Gujrat | D | Om Cold Storage | Gujrat | KCX3 | 3374K3646 | 5088589219 | 2025-05-27 | 508858 | 2025-06-06 | kcx pump air purging | 2024-12-28 | 2025-02-25 | 55.8 | 770 | cold storage | 2 | It was discovered that there was an air punching issue within the compressor, and the oil pressure would drop within half an hour. | null | closed | Replaced THRUST RING PUMP END BEARING COVER KCX, OIL PUMP ASSEMBLY KCX.
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Chaudhary Cold Storage | Uttar Pradesh | KC4 | 338K6027 | 5043709040 | 2025-04-16 | 504370 | 2025-04-16 | knocking / abnormal sound | 2025-01-27 | 2025-03-23 | 24.4 | 750 | cold storage | 2 | Buffer Spring Found damage | null | closed | Replaced BUFFER SPRING KC/KCX
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Natural Foods | Uttar Pradesh | KC4 | 338K5960 | 5086149253 | 2025-06-02 | 508614 | 2025-06-13 | shaft seal leakage | 2024-11-15 | 2025-03-23 | 599 | 750 | cold storage | 3 | O ring changed and lapping done twice but still facing problem. | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Mldc Cold Solutions Llp | Uttar Pradesh | KCX4 | 3384K3940 | 5094349252 | 2025-06-02 | 509434 | 2025-06-13 | sv coil burnt | 2025-01-17 | 2025-03-18 | 961.1 | 750 | cold storage | 2 | SV Coil Burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Jai Ambey Ice & Cold Storage | Uttar Pradesh | KC4 | 338K6005 | 5099009259 | 2025-06-04 | 509900 | 2025-06-04 | sv coil burnt | 2025-01-09 | 2025-03-26 | 624 | 750 | cold storage | 2 | SV Coil burnt and TAL valve also found leakage. | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER, TEFLON SEAT BOTTOM TAL 80/100
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Jai Ambey Ice & Cold Storage | Uttar Pradesh | KC4 | 338K6005 | 5087389222 | 2025-05-27 | 508738 | 2025-05-30 | sv coil burnt | 2025-01-09 | 2025-03-26 | 533 | 750 | cold storage | 2 | SV Coil burnt | null | closed | Replaced COIL FOR NO SOLENOID VALVE, 230V, 50 Hz WITH GREEN COLOUR STICKER
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Rana Cold Storage And Ice Factory | Uttar Pradesh | KC4 | 338K6015 | 5091049229 | 2025-05-28 | 509104 | 2025-05-31 | sv coil burnt | 2025-01-17 | 2025-03-03 | 1015 | 750 | cold storage | 1 | SV Coil Burnt | null | closed | Replaced SOLENOID VALVE 3WAY
2025-06-23 | Hss Solution Pvt Ltd | Rajasthan | D | Shri Hanumant Agro Cold Storage Llp | Rajastan | KCX3 | 3374K3624 | 5034289030 | 2025-04-13 | 503428 | 2025-04-09 | toggle switch not working | 2024-12-09 | 2025-04-09 | 1 | 767 | cold storage | 1 | TOGGLE SWITCH NOT WORKING. DUE TO N EW ENGINEER DID'NT KNOW THE PROCESS . KINDLY APPROVE THIS TIME. Approval History : | null | closed | Replaced TOGGLE SWITCH
2025-06-23 | Hss Solution Pvt Ltd | Rajasthan | D | Agastya Industries | Rajastan | KCX2 | 3364K2719 | 5013989128 | 2025-05-04 | 501398 | 2025-05-03 | pressure gauge damaged. | 2024-07-13 | 2025-05-03 | 2 | 764 | dairy / ice cream | 9 | Gauge burst during commissioning. | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 25 KG/CM2 , 100MM DIAL, GLYSERINE FILLED
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Unimax Frozen Treat Pvt Ltd | Haryana | KCX72 | 3474K799 | 5103409278 | 2025-06-07 | 510340 | 2025-06-17 | kcx pump tang broken | 2024-07-01 | 2025-04-14 | 7 | 990 | food processing | 8 | Zero hour Defect- Drive Gear Tang broken | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-06-23 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Andhra Pradesh | KCX4 | 3384K3831 | 5090909228 | 2025-05-28 | 509090 | 2025-05-27 | cylinder overheating | 2024-11-07 | 2024-12-28 | 1708 | 850 | ice plant | 1 | Overheating of No 4 cylinder was reported by the customer. Upon inspection, it was determined that cylinder No 4 was discharge back leaking due to damage to all its components. Additionally, cylinders 1 and 3 were also found to have discharge back leaks. Damaged parts were replaced from TL stock, and the machine was restored. | 4 | closed | Replaced PISTON KC/KCX, PISTON RING SET KC/KCX, SHAFT SEAL ASSEMBLY KC/KCX, GUDGEON PIN KC/KCX, BUSH CONNECTING ROD KC/KCX, BEARING BUSH BIG END CON ROD KC/KCX, DISCHARGE VALVE ASSEMBLY KCX3nos, RING SUCTION VALVE KC/KCX, VALVE SPRING SUCTION KC2nos, CYLINDER LINER KC/KCX.
2025-06-23 | Multivista Global Pvt Ltd | Gurgaon | D | Kamal Milk Chilling Plant | Uttar Pradesh | KCX4 | 384K3978 | 5096689249 | 2025-06-02 | 509668 | 2025-06-18 | high oil consumption | 2025-02-12 | 2025-03-27 | 1269 | 450 | ice plant | 1 | Piston Ring Worn Out | null | closed | Replaced PISTON RING SET KC/KCX 4nos
2025-06-23 | Gargi Engineering Enterprices Pvt Ltd | MH | D | Colortex Industries Pvt Ltd | Surat, Gujarat | KCX72 | 3474K751 | 5091209237 | 2025-05-29 | 509120 | 2025-05-29 | krms smps & pt malfuction | 2024-02-19 | 2025-05-29 | 0 | 830 | ice plant | 16 | SMPS Malfunction & PT Malfunction | null | closed | Replaced SMPS 24VDC_ 2.5A SINGLE OUTPUT DIN RAIL MOUNTED, SUCTION / OIL / INTER. PRESSURE TRANSDUCER, 0 TO 5 Vdc, ()1 TO 12.8 bar(g), MAKECAREL, CODESPKT00E1S0 2nos
2025-06-23 | Multivista Global Pvt Ltd | Tamil Nadu | D | Nallayan Agro Products Foundation | Tamil Nadu | PCX2 | 3106K0263 | 5090069244 | 2025-05-31 | 509006 | 2025-06-17 | pcx2 unloading problem | 2023-11-28 | 2025-06-17 | 6 | 886 | ice plant | 1 | The oil pump malfunctioned while taking a trial run | null | closed | Replaced OIL PUMP ASSEMBLY PC2
2025-06-23 | Hss Solution Pvt Ltd | Rajasthan | D | Abhinandan Traders | Rajastan | KCX2 | 3364K2714 | 5054229114 | 2025-05-01 | 505422 | 2025-05-01 | pressure gauge not working | 2024-07-09 | 2025-05-01 | 7 | 762 | ice plant | 1 | Zero Hour Complaint, pressure switch not working | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-06-23 | Kirloskar Pneumatic Co Ltd | New Delhi | D | Fair Exports (India) Pvt Ltd | Punjab | KCX4 | 3384K3541 | 5060429138 | 2025-05-06 | 506042 | 2025-05-06 | cylinder overheating | 2023-12-26 | 2024-03-03 | 2514 | 934 | meat/fish process | 2 | DV leakage due to that other parts get damaged. | null | closed | Replaced PISTON KC/KCX, CYLINDER LINER KC/KCX, DISCHARGE VALVE ASSEMBLY KCX, PISTON RING SET KC/KCX.
2025-06-24 | Multivista Global Pvt Ltd | Gurgaon | D | Dubey Cold Storage | Uttar Pradesh | KC4 | 338K5958 | 5099169261 | 2025-06-04 | 509916 | 2025-06-14 | abnormal noise | 2024-11-13 | 2025-03-20 | 845 | 768 | cold storage | 3 | Liner Piston Worn Out. | null | closed | Replaced CYLINDER LINER KC/KCX2Nos, PISTON KC/KCX2nos, PISTON RING SET KC/KCX4nos.
2025-06-24 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2321 | 5103109283 | 2025-06-09 | 510310 | 2025-06-09 | cylinder overheating | 2023-10-26 | 2024-03-14 | 4960.5 | 800 | food processing | 4 | Overheating complaint of cylinder no 2. They noticed that due to DV leak and excessive heat cylinder liner and other parts are effected | null | closed | Replaced CYLINDER LINER KC/KCX, DISCHARGE VALVE ASSEMBLY KCX 2nos, BUFFER SPRING KC/KCX, PISTON KC/KCX, BUSH CONNECTING ROD KC/KCX, GUDGEON PIN KC/KCX, PISTON RING SET KC/KCX, RING SUCTION VALVE KC/KCX,VALVE SPRING SUCTION KC 2nos.
2025-06-24 | Multivista Global Pvt Ltd | Gurgaon | D | Bveg Foods Private Limited | Haryana | KCX51 | 3454K243 | 5108509296 | 2025-06-11 | 510850 | 2025-06-24 | cylinder overheating | 2024-02-12 | 2024-07-23 | 1363 | 990 | food processing | 5 | Discharge valve Leakage due to that other parts get damaged. | null | closed | Replaced CYLINDER LINER KC/KCX, PISTON KC/KCX, PISTON RING SET KC/KCX,BUFFER SPRING KC/KCX, DISCHARGE VALVE ASSEMBLY KCX, TEFLON RING SAFETY VALVE KC/KCX.
2025-06-24 | Model Pneumatic Co | Punjab | D | Rudra Food Products | Punjab | KCX3 | 3374K3539 | 5092889312 | 2025-06-13 | 509288 | 2025-06-13 | kcx pump tang broken | 2024-09-27 | 2025-06-13 | 2 | 950 | food processing | 8 | Zero hour complaint, Drive Gear tang broken. | null | closed | Replaced OIL PUMP ASSEMBLY KCX
2025-06-24 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Andhra Pradesh | KCX4 | 3384K3831 | 5100189262 | 2025-06-04 | 510018 | 2025-06-05 | abnormal noise | 2024-11-07 | 2024-12-28 | 1815 | 850 | ice plant | 1 | NO 1 ,2 & 3 cylinder liners worn out and piston also found worn out | 1,2,3 | closed | Replaced CYLINDER LINER KC/KCX 3nos, PISTON KC/KCX2nos, BUSH CONNECTING ROD KC/KCX2nos, GUDGEON PIN KC/KCX 2nos, PISTON RING SET KC/KCX 3nos.
2025-06-24 | Kalp Marketing | Gujrat | D | Raunak Ice & Cold Storage | Gujrat | KCX72 | 3474K795 | 5106569292 | 2025-06-12 | 510656 | 2025-06-10 | high oil consumption | 2024-06-27 | 2024-08-23 | 5058 | 990 | meat/fish process | 1 | The dv rings of both hp cylinders found broken. This caused overheating and subsequent damage to the compressor. | null | closed | Replaced CYLINDER LINER KC/KCX 2nos, PISTON RING SET KC/KCX7nos, BEARING BUSH BIG END CON ROD KC/KCX, NEEDLE ROLLER BEARING KC/KCX4nos, SPACER FOR NEEDLE ROLLER BEARING KC/KCX2nos, OIL RETURN VALVE KC/KCX/PC2, PISTON KC/KCX, GASKET LINER 1.5 mm KC/KCX2nos, GASKET HEAD COVER KC/KCX9nos, KIT DELIVERY VALVE KC/KCX2nos.
2025-06-27 | Pragya Industrial Supply | Karnataka | D | John Lawrence Ice And Cold Storage | Karnataka | KCX6 | 3394K2388 | 5087329238 | 2025-05-30 | 508732 | 2025-05-30 | abnormal noise and oilleakage | 2023-12-30 | 2024-06-18 | null | 850 | ice plant | 5 | All rings are worn out, piston haveing marking on working surface | null | closed | Replaced PISTON RING SET KC/KCX6nos, PISTON KC/KCX2nos, BEARING BUSH BIG END CON ROD KC/KCX 6nos, GUDGEON PIN KC/KCX6nos, BUSH CONNECTING ROD KC/KCX6nos, CYLINDER LINER KC/KCX6nos, SHAFT SEAL ASSEMBLY KC/KCX1nos.
2025-06-30 | Parag Marketing Services | null | D | United Breweries Limited (Ellora) | Waluj | KCX3 | 3374K3366 | 5109289304 | 2025-06-12 | 510928 | 2025-06-12 | kcx pump air purging | 2024-01-17 | 2024-02-10 | 2975 | 750 | beverage / breweries | 1 | Air purging problem to pump | null | closed | Replaced KCX Pump assembly
2025-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Ghazi Brothers Cold Storage | Up | KCX6 | 3394K2661 | 5113229322 | 2025-06-23 | 511322 | 2025-06-23 | abnormal noise | 2025-02-04 | 2025-03-19 | 1093 | 750 | cold storage | 1 | Liner , Piston & Piston rings wornout | Not mentioned | closed | Replaced Liner4 , Piston 2 & Piston ring set4
2025-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | R.K.V.K Cold Storage P. Ltd | Up | KCX4 | 3384K3757 | 5113209320 | 2025-06-16 | 511320 | 2025-06-22 | abnormal noise | 2024-08-10 | 2024-08-29 | 2624 | 750 | cold storage | 1 | Liner , Piston & Piston rings wornout | Not mentioned | closed | Replaced Liner1 , Piston 1 & Piston ring set3
2025-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Sheetla Cold Storage & Ice Factory | Up | KCX4 | 3384K3615 | 5114169326 | 2025-06-23 | 511416 | 2025-06-23 | abnormal noise | 2024-01-31 | 2024-03-22 | 2622 | 768 | cold storage | 2 | Delivery valve leak , Liner , Piston Piston rings wornout | Not mentioned | closed | Replaced Liner1 , Piston 1 & Piston ring set1, DV1
2025-06-30 | Kalp Marketing | Gujrat | D | Patidar Agricare | Gj | KCX4 | 3384K3657 | 5105509291 | 2025-06-17 | 510550 | 2025-06-17 | cylinder overheating | 2024-03-04 | 2024-03-22 | 4830 | 800 | cold storage | 1 | Delivery valve ring spring broken & Consequential failures. | null | closed | Replaced DV4 , Piston1 , Liners2, Piston rings 4
2025-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Sanjay Kumar | Up | KC2 | 336K3440 | 5122229364 | 2025-06-24 | 512222 | 2025-06-24 | KC Pump Low oil pressure | 2024-12-17 | 2025-04-04 | 762 | 764 | dairy / ice cream | 4 | KC Pump scoring & damaged | null | closed | Replaced KC Pump assembly.
2025-06-30 | Multivista Global Pvt Ltd | Gurgaon | D | Bveg Foods Private Limited | Haryana | KCX51 | 3454K243 | 5122089362 | 2025-06-29 | 512208 | 2025-06-29 | Safety valve spring damaged | 2024-02-12 | 2024-07-23 | 1366 | 990 | food processing | 5 | Safety valve spring damaged due to overheating , Intermediate pressure high. | null | closed | Replaced safety valve spring
2025-06-30 | Kalp Marketing | Gujrat | D | Kiri Industries Limited | Gujrat | KCX6 | 3394K2574 | 5108189295 | 2025-06-11 | 510818 | 2025-06-11 | cylinder overheating | 2024-10-24 | 2025-01-16 | 644 | 750 | ice plant | 3 | Delivery valve ring spring broken | null | closed | Replaced delivery valve 1
2025-06-30 | Hss Solutions Pvt Ltd | Rajastan | D | Hr Indra Industries Pvt Ltd | Rajasthan | KCX2 | 3364K2851 | 5108209299 | 2025-06-11 | 510820 | 2025-06-11 | knocking / abnormal sound | 2025-02-18 | 2025-05-17 | 469 | 763 | ice plant | 3 | Knocking sound due to delivery valve leakage | null | closed | Replaced delivery valve assembly 1 No.
2025-06-30 | Multivista Global Pvt Ltd | Tamil Nadu | D | Sangam Ice Factory & Cold Storage | Tn | KC4 | 338K6058 | 5114929335 | 2025-06-18 | 511492 | 2025-06-18 | Pressure gauge error | 2025-02-24 | 2025-06-18 | 2 | 770 | ice plant | 4 | Pressure gauge error - 16kg/cm2 | null | closed | Replaced Pressure gauge
2025-06-30 | Hss Solutions Pvt Ltd | Rajastan | D | Rajgir Crrogenic Gases Llp | Rajasthan | KCX84 | 3305K039 | 5120649365 | 2025-06-24 | 512064 | 2025-06-24 | high oil consumption | 2024-05-27 | 2025-04-26 | 380 | 930 | others | 11 | Liner , Piston & Piston rings wornout | null | closed | Replaced Liner1 , Piston 1 & Piston ring set12, DV1
2025-06-30 | Kalp Marketing | Gujrat | D | Shiv Kripa Gases Metals Pvt Ltd | Mp | KCX63 | 3464K237 | 5114189327 | 2025-06-17 | 511418 | 2025-06-17 | high oil consumption | 2024-09-24 | 2025-02-08 | 1213 | 936 | chemical / pharma | 5 | Liner , Piston & Piston rings wornout | null | closed | Replaced Liner2 , Piston 2 & Piston ring set9, ORV1
2025-07-22 | Model Pneumatic Co | Punjab | D | Shri Guru Ram Das Cold Store | Pb | KC4 | 338K5977 | 5143629436 | 2025-07-09 | 514362 | 2025-07-09 | abnormal noise | 2024-12-14 | 2025-03-18 | 485 | 750 | cold storage | 2 | Liner and Piston ring worn out. | null | closed | Replaced Piston2nos ,Liner2nos & piston ring set4nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Tanya Ice And Cold Storage | Up | KC4 | 338K6040 | 5068629211 | 2025-06-02 | 506862 | 2025-06-02 | abnormal noise | 2025-02-05 | 2025-03-24 | 484 | 750 | cold storage | 1 | Liner and piston ring set worn out. | null | closed | Replaced Liner2nos, piston2nos & piston ring set 2nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | S.S.R.T. Cold Storage | Up | KC6 | 339K3799 | 5063669160 | 2025-05-13 | 506366 | 2025-05-17 | abnormal noise | 2024-10-29 | 2025-03-01 | 675 | 768 | cold storage | 4 | Cylinder 1 and 4 have cut mark. Both 1 and 4 piston worn out. Due to this all 6 ring worn out | null | closed | Replced Liner2nos, Piston 2Nos and Piston ring set 6nos.
2025-07-22 | Parag Marketing Services | Chhatisgarh | D | Shreenath Sheetgrih | Chhattisgarh | KCX4 | 3384K3539 | 5023589113 | 2025-05-01 | 502358 | 2025-05-01 | abnormal noise | 2023-12-26 | 2024-08-03 | 839 | 750 | cold storage | 7 | Knocking sound complaint, during visit they noticed that step cut on cylinder liner #1 and oil throw from other cylinders. | null | closed | Replaced PISTON RING SET4nos, BEARING BUSH BIG END CON ROD4 nos, PISTON 2nos, SPRING CURTAIN 1nos, CYLINDER LINER 2nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | S.S.R.T. Cold Storage | Up | KC6 | 339K3799 | 5110269315 | 2025-06-14 | 511026 | 2025-06-18 | abnormal noise | 2024-10-29 | 2025-03-01 | 872 | 768 | cold storage | 5 | Discharge valve found leakage | null | closed | Replaced Piston 1nos, Piston ring set1nos, Liner1nos, Valve spring suction2nos,ring suction valve1nos,Discharge valve1nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Khi Cold Storage Pvt. Ltd | Hr | KCX3 | 3374K3564 | 5126949390 | 2025-06-30 | 512694 | 2025-07-07 | abnormal noise | 2024-10-19 | 2024-12-03 | 921 | 750 | cold storage | 1 | Liner & Piston Ring worn out. The D.V.'s wavy spring was found broken, though no leakage was found. | null | closed | Replaced Liner1nos Piston1nos DV1nos & Piston ring 3nos
2025-07-22 | Cool Comfort Private Limited | West Bengal | D | Rameshwaram Cold Storage Pvt Ltd | Wb | KCX4 | 3384K3601 | 5114269347 | 2025-06-20 | 511426 | 2025-07-11 | abnormal noise | 2024-01-27 | 2024-03-07 | 1773 | 850 | cold storage | 1 | Delivery valve ring spring broken | null | closed | Replaced KIT DELIVERY VALVE KC/KCX 2Nos
2025-07-22 | Kalp Marketing | Gujrat | D | Ram Bulk-1 | Gj | KCX4 | 3384K3818 | 5143249433 | 2025-07-09 | 514324 | 2025-07-11 | cylinder overheating | 2024-10-23 | 2025-02-08 | 1635 | 770 | cold storage | 3 | Compressor Overheating | 1 | closed | Replaced DV4nos, piston1nos, piston ring set1nos, liner1nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Pallavi Cold Storage & Ice Factory Pvt. Ltd | Up | KCX6 | 3394K2656 | 5127709396 | 2025-07-01 | 512770 | 2025-07-01 | High oil consumption ORV Leak | 2025-01-31 | 2025-03-12 | 674 | 750 | cold storage | 1 | ORV leakage found. | null | closed | Replaced OIL RETURN VALVE KC/KCX/PC2 2nos
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Dhanraj Cold & Warehouse | Up | KC6 | 339K3808 | 5127689395 | 2025-07-01 | 512768 | 2025-07-01 | High oil consumption ORV Leak | 2024-11-25 | 2025-03-12 | 405 | 750 | cold storage | 3 | ORV leakage found. | null | closed | Replaced OIL RETURN VALVE KC/KCX/PC2 2nos
2025-07-22 | Parag Marketing Services | Maharashtra | D | Bhoomi Agro Bio Foods | Mh | KCX31 | 3434K0226 | 5145789447 | 2025-07-11 | 514578 | 2025-07-11 | KRMA Discharge sensor not working | 2023-12-15 | 2025-02-17 | 1828 | 850 | cold storage | 13 | FOUND DISCHARGE TRMPERTURE SENSOR N OT WORKING. | null | closed | Replaced Discharge temp sensor, PT1000.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Narayan Hari Cold Storage | Up | KCX6 | 3394K2627 | 5124069403 | 2025-07-03 | 512406 | 2025-07-04 | Oil pressure switch malfunctioning | 2025-01-01 | 2025-05-29 | 198 | 750 | cold storage | 5 | Oil pressure switch mall functioning , it is tripping while oi pressure developed. | null | closed | Replaced PRESSURE SWITCH OP MP55A.
2025-07-22 | Kalp Marketing | Gujrat | D | Anand Cold Storage | Deesa Gujrat | KCX4 | 3384K3854 | 5117589345 | 2025-06-20 | 511758 | 2025-06-23 | shaft seal leakage | 2024-11-25 | 2025-02-25 | 1420 | 770 | cold storage | 2 | Both the rotary shaft seal and the stationary shaft seal inside were cut. | null | closed | Replaced shaft seal aseembly.
2025-07-22 | Parag Marketing Services | Maharashtra | D | Vrs Foods Limited | Mh | KCX2 | 3364K2726 | 5109689307 | 2025-06-12 | 510968 | 2025-06-12 | Gauge board Fitting leakage | 2024-07-30 | 2025-06-12 | 10 | 850 | dairy / ice cream | 11 | Leakage issue from the gauge fitting connector and observed that the connector thread was found damaged. | null | closed | Replaced FEMALE RUN TEE 3/8 BSP(F) X 6MM (TBG 2 SIDE)
2025-07-22 | Parag Marketing Services | Maharashtra | D | Heritage Foods Ltd | Mh | KCX4 | 3384K4000 | 5084209256 | 2025-06-03 | 508420 | 2025-06-03 | k5 valve thread damaged | 2025-02-28 | 2025-06-03 | 113 | 850 | dairy / ice cream | 3 | Identified that the K5 valve thread was damaged. | null | closed | Replaced K5 VALVE, LIGHT, SS.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Banke Bihari Cold Storage | Up | KC3 | 337K4974 | 5134449419 | 2025-07-07 | 513444 | 2025-07-12 | KC Pump Tang broken | 2025-03-11 | 2025-07-12 | 2 | 750 | dairy / ice cream | 2 | Drive Gear Tang broken | LC KPC 02 2025 297 | closed | Replaced OIL PUMP ASSEMBLY KC1nos.
2025-07-22 | Hss Solutions Pvt Ltd | Rajastan | D | Laxmi Food Product & Ice Factory | Rj | KCX2 | 3364K2663 | 5082189196 | 2025-05-20 | 508218 | 2025-05-22 | kcx pump tang broken | 2024-03-26 | 2025-05-09 | 615 | 1034 | dairy / ice cream | 13 | Drive Gear Tang broken. | LC 03 24 1329 | closed | Replaced oil pump assembly kcx.
2025-07-22 | Parag Marketing Services | Maharashtra | D | Seema'S Mohak Foods Llp | Mh | PCX2 | 3106K0307 | 5071349266 | 2025-06-05 | 507134 | 2025-05-30 | PCX Pump Drive shaft tang broken | 2024-08-13 | 2025-05-30 | 18 | 800 | dairy / ice cream | 9 | Oil pressure not developing. On inspection, it was found that the gear tag element was broken | PC2 LC 07 24 92 | closed | Replaced DRIVEN GEAR ASSEMBLY PC2, DRIVING GEAR OIL PUMP PC2, BEARING BUSH FOR OIL PUMP KC/PC2.
2025-07-22 | Parag Marketing Services | Maharashtra | D | Vrs Foods Limited | Mh | KCX2 | 3364K2728 | 5109669306 | 2025-06-12 | 510966 | 2025-06-12 | pressure gauge leak | 2024-07-30 | 2025-06-12 | 10 | 850 | dairy / ice cream | 11 | Leakage identified internally from the gauge. | null | closed | Replaced AMMONIA PRESSURE GAUGE 16Kg/cm2
2025-07-22 | Parag Marketing Services | Maharashtra | D | Sai Shradha Dudh Sankalan Kendra | Mh | PCX2 | 3106K0317 | 4925048726 | 2025-02-17 | 492504 | 2025-02-07 | pressure switch malfunctioning | 2024-10-22 | 2025-02-07 | 4 | 1000 | dairy / ice cream | 3 | FOUNT OP SWITCH NOT WORKING PROPER | null | closed | Replaced Pressure switch MP55
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Vashisht Enterprises | Uk | KCX63 | 3464K235 | 5130969410 | 2025-07-04 | 513096 | 2025-07-05 | abnormal noise | 2024-09-30 | 2025-02-11 | 600 | 750 | food processing | 4 | Liner & Piston Ring worn Out. | null | closed | Replaced Liner3nos, piston3nos & piston ring set 3nos.
2025-07-22 | Model Pneumatic Co | Punjab | D | Guru Nanak Agro Foods Pvt Ltd | Punjab | KCX63 | 3464K241 | 5085029225 | 2025-05-27 | 508502 | 2025-06-19 | abnormal noise | 2024-10-18 | 2025-01-11 | 1297 | 950 | food processing | 2 | Discharge valve Found Leakage due to that other parts also get damaged. | null | closed | Replaced Liner 2nos, Piston ring set2nos, Piston1nos & DV1nos.
2025-07-22 | Kalp Marketing | Gujrat | D | Deepvijay Ice Factory | Gujrat | KCX4 | 3384K3682 | 5126789399 | 2025-07-02 | 512678 | 2025-07-01 | high oil consumption | 2024-03-27 | 2024-08-11 | 4850 | 880 | ice plant | 4 | The liners have cut in 360 degree pattern resulting to damaged the piston rings set as well. | null | closed | Replaced Liner2nos, piston ring set4nos,BEARING BUSH BIG END CON ROD1nos,OIL RETURN VALVE1nos.
2025-07-22 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Ap | KCX4 | 3384K3830 | 5120249357 | 2025-06-23 | 512024 | 2025-06-23 | high oil consumption | 2024-11-07 | 2024-12-27 | 2049 | 850 | ice plant | 1 | Abnormal wearing of Cylinder liners | 2&4 | closed | Replaced liner 2nos & piston ring sets 2nos.
2025-07-22 | Multivista Global Pvt Ltd | Gurgaon | D | Shourya Banana Raping Plant | Uk | KCX3 | 3374K3634 | 5118089371 | 2025-06-25 | 511808 | 2025-07-04 | KCX Oil pump low oil pressure issue | 2024-12-20 | 2025-02-06 | 622 | 750 | ice plant | 1 | Oil pressure found low, oil pump opened found oil pump element damaged. | LC 12 24 882 | closed | Replaced OIL PUMP ASSEMBLY KCX 1nos.
2025-07-22 | Cool Comfort Private Limited | West Bengal | D | Hindustan Cables | Wb | KCX2 | 3364K2903 | 5132789414 | 2025-07-05 | 513278 | 2025-07-06 | kcx pump tang broken | 2025-04-26 | 2025-07-06 | 4 | 850 | ice plant | 2 | Oil pump element driving gear trunk broken. | LC 02 25 1155 | closed | Replaced pump element KCX
2025-07-22 | Trade Links | Secunderabad | D | Sri Ramanjaneya Ice Industry | Ap | KCX4 | 3384K4036 | 5108489309 | 2025-06-13 | 510848 | 2025-06-13 | kcx pump tang broken | 2025-04-21 | 2025-06-10 | 48 | 750 | ice plant | 1 | The oil pump tang was damaged as a result of a stuck ball bearing | NE 240 03 25 | closed | Replaced OIL PUMP ASSEMBLY KCX 1nos.
2025-07-22 | Parag Marketing Services | Maharashtra | D | Gadre Marine Export Pvt Ltd | Mh | KCX72 | 3474K824 | 5122429367 | 2025-06-24 | 512242 | 2025-06-24 | kcx pump air purging | 2024-09-03 | 2025-06-24 | 24 | 850 | meat/fish process | 8 | Oil pump air purging issue. After oil pump replacement, the air purging issue was resolved and no further abnormalities were observed. | null | closed | Replaced oil pump aseemblykcx1nos
2025-07-22 | Parag Marketing Services | Maharashtra | D | Ari Foods | Mh | KCX31 | 3434K0236 | 5044389051 | 2025-04-18 | 504438 | 2025-04-18 | Solenoid valve leakage | 2024-02-27 | 2024-08-13 | 3772 | 900 | others | 5 | Solenoid FOUND LEAKAGE FROM BOTTOM O RING | null | closed | Replaced solenoid valve1nos
2025-07-22 | Model Pneumatic Co | Punjab | D | Pancarbo Greenfuels Private Limited | Pb | KCX72 | 3474K747 | 5108229422 | 2025-07-08 | 510822 | 2025-07-08 | abnormal noise | 2024-02-29 | 2024-08-11 | 4872 | 992 | chemical / pharma | 6 | Found DV assembly leakage , Due to that other parts get damaged. | null | closed | Replaced Piston ring set1nos, DV1nos,Piston1nos,Liner1nos,SUCTION / OIL / INTER. PRESSURE TRANSDUCER, 0 TO 5 Vdc, ()1 TO 12.8 bar(g), MAKECAREL, CODESPKT00E1S01nos
2025-07-22 | Gargi Engineering Enterprises Pvt Ltd | Gujrat | D | Jay Jalaram Lifesciences Pvt Ltd | Gj | KCX3 | 3374K3528 | 5115569336 | 2025-06-18 | 511556 | 2025-06-21 | kcx pump air purging | 2024-08-29 | 2025-01-17 | 45 | 767 | chemical / pharma | 4 | Due to air purging issue compressor dry run. parts need to replace. | H24 015 LDK | closed | Replaced KIT CRANKSHAFT BEARING KCX 1nos , SET OF O RINGS FOR KCX3 1nos & BEARING BUSH BIG END CON ROD KC/KCX 3nos
2025-07-22 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX72 | 3474K726 | 5110469384 | 2025-06-28 | 511046 | 2025-06-13 | shaft seal leakage | 2023-12-25 | 2024-02-13 | 2050 | 750 | chemical / pharma | 1 | Oil leakage from drain pipe of the shaft seal. A new shaft seal has now been installed with neoprene "O" rings | null | closed | Replaced SHAFT SEAL ASSEMBLY KC/KCX 1nos.
2025-07-26 | Multivista Global Pvt Ltd | Tamil Nadu | D | Sicgil Industrial Gases Ltd | Tn | KCX93 | 3485K 0188 | 5114329460 | 2025-07-14 | 511432 | 2025-07-14 | abnormal noise | 2024-01-31 | 2025-07-15 | 3 | 1000 | beverage / breweries | 18 | Abnormal noise from HP cylinders due to valve leakage and 2 linrs & piston rings wornout. | null | closed | Replaced liner , piston ring & Piston 2 nos
2025-07-26 | S. B. Refrigeration Services | Bihar | D | Bokaro Distillery Pvt Ltd | Jharkhand | KCX6 | 3394K2608 | MAIL | 2025-07-17 | null | 2025-07-17 | High vibration at suction strainer | 2024-12-14 | 2025-07-10 | 24 | 850 | beverage / breweries | 7 | At suction strainer flange 45-50 mm/sec & Discharge flange 22-26 mm/sec in horizontal direction | null | open | Decided to replace the compressor.
2025-07-26 | Cool Comfort Private Limited | West Bengal | D | Kishan Bandhu Himghar Pvt Ltd | Wb | KCX4 | 3384K3618 | 5145969483 | 2025-07-19 | 514596 | 2025-07-19 | abnormal noise | 2024-02-02 | 2025-03-25 | 520 | 850 | cold storage | 1 | Abnormal sound due to the delivery valve leak , ring spring broken and one liner piston rings seized. | 1 | closed | Replaced liner & piston ring 1 , DV Kit 3 nos
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | H. Saqlani Cold Storage | Up | KC4 | 338K6044 | 5153049470 | 2025-07-16 | 515304 | 2025-07-24 | high oil consumption | 2025-02-11 | 2025-03-19 | 1015 | 750 | cold storage | 1 | Abrasive wear of pump cover might be due to contaminated oil due to liner & piston rings wornout and low oil pressure issue. | null | closed | Replaced KC Oil pump
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Ji Coldstorage | Up | KC4 | 338K6045 | 5122269393 | 2025-06-30 | 512226 | 2025-06-30 | high oil consumption | 2025-02-10 | 2025-03-22 | 904.7 | 750 | cold storage | 1 | All 4 cylinders liners and piston rings wornout & Pump abrasive scoring | null | closed | Replaced liners , piston rings 4 nos & KC Pump
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | Sunder Cold Storage | Up | KC6 | 339K3847 | 5142429431 | 2025-07-09 | 514242 | 2025-07-09 | high oil consumption | 2025-01-10 | 2025-03-18 | 566 | 750 | cold storage | 3 | All 6 cylinders liners and piston rings wornout | null | closed | Replaced liners , piston rings 6 nos & Piston 4 nos
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | H. Saqlani Cold Storage | Up | KC4 | 338K6044 | 5129329445 | 2025-07-11 | 512932 | 2025-07-11 | high oil consumption | 2025-02-11 | 2025-03-19 | 1009 | 750 | cold storage | 1 | All 4 cylinders liners and piston rings wornout | null | closed | Replaced liners , piston rings 4 nos & Thrust ring
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | Bikanerwala Foods Pvt Ltd | Haryana | KCX72 | 3474K800 | 5128169461 | 2025-07-14 | 512816 | 2025-07-16 | cylinder overheating | 2024-07-06 | 2025-06-06 | 142 | 935 | food processing | 11 | HP Cylinder 4 Delivery valve leakage due to spring broken. | 4 | closed | Replaced delivery valve.
2025-07-26 | Parag Marketing Services | null | D | Al Quresh Exports | Mh | KCX4 | 3384K3653 | 5084989346 | 2025-06-20 | 508498 | 2025-06-20 | high oil consumption | 2024-02-29 | 2024-04-17 | 2255 | 950 | food processing | 14 | Cylinder liners , piston and piston rings worn out | null | closed | Replaced ALL 4 liners , piston rings.
2025-07-26 | Trade Links | Secunderabad | D | Lakshmi Srinivasa Ice Industries | Ap | KCX6 | 3394K2751 | 5130289407 | 2025-07-03 | 513028 | 2025-07-03 | high oil consumption | 2025-05-22 | 2025-06-02 | 525 | 850 | ice plant | 1 | Cyl no. 4 & 6 Liners & Piston rings wornout & Cyl 1 & 3 Delivery valve leakages | 4 &6 | closed | Replaced liner 2nos, Piston ring set2nos, & DV2nos.
2025-07-26 | Trade Links | Secunderabad | D | Sai Balaji Ice Factory | Ap | KCX4 | 3384K3997 | 5097149342 | 2025-06-20 | 509714 | 2025-06-20 | high oil consumption | 2025-02-20 | 2025-04-14 | 940 | 850 | ice plant | 2 | Piston rings & Cylinder liner wornout | null | closed | Replaced ALL 4 liners , piston rings.
2025-07-26 | Trade Links | Secunderabad | D | Kmc Ice Factory | Ap | KCX4 | 3384K3862 | 5126749392 | 2025-06-30 | 512674 | 2025-06-30 | high oil consumption | 2024-11-28 | 2025-03-24 | 2183 | 750 | ice plant | 17 | Piston rings & Cylinder liner wornout | NA | closed | Replaced liners 1 no , piston rings 4 nos.
2025-07-26 | Multivista Global Pvt Ltd | Gurgaon | D | Almarziya Agro Foods | Up | KCX72 | 3474K836 | 5117989385 | 2025-06-28 | 511798 | 2025-06-28 | abnormal noise | 2024-09-25 | 2024-12-25 | 1898 | 850 | meat/fish process | 3 | Cylinder liners , piston and piston rings worn out | null | closed | Replaced liners , piston rings 9 nos & Piston 4 nos and Delivery valve 1 no.
2025-07-26 | Trade Links | Secunderabad | D | Aparna Marine Exports | Ap | KCX93 | 3485K243 | 5152589488 | 2025-07-22 | 515258 | 2025-07-22 | kcx pump tang broken | 2025-04-30 | 2025-07-22 | 15 | 950 | meat/fish process | 3 | KCX Pump tang broken within 15 hours | LC 12 24 953 | closed | Replaced pump assly
2025-07-26 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Rizwan Taloja | null | KCX72 | 3474K932 | MAIL | 2025-07-21 | null | 2025-07-21 | Painting issue | 2025-06-06 | 2025-07-21 | 0 | null | Na | 1 | Paint damaged and peeloff on lifted area like on discharge pipes , cylinder block bottom area due to wet paint. | null | closed | Rectified by paint touchup at site by KPCL Team on 28th July 25
2025-07-26 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Uttan Machhimar & Vahtuk Sahakari Society | Mh | KCX3 | 3374K3761 | 5155969489 | 2025-07-22 | 515596 | 2025-07-22 | pressure switch malfunctioning | 2025-06-19 | 2025-07-22 | 0 | null | Na | 1 | OP Pressure switch MP55 found defective & not working. | null | closed | Replaced OP Pressure switch
2025-07-26 | Multivista Global Pvt Ltd | Tamil Nadu | D | Sicgil Industrial Gases Ltd | Tn | KCX93 | 3485K 0187 | 5114309459 | 2025-07-14 | 511430 | 2025-07-14 | cylinder overheating | 2024-01-31 | 2025-07-14 | 5 | 1000 | chemical / pharma | 6 | Cylinder overheating 2 nos due to delivery valve leakage | NA | closed | Replaced delivery valves , Liners , Piston & piston rings 2 nos and discharge temp sensor due to wire cut.
2025-07-26 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2695 | 5159369491 | 2025-07-23 | 515936 | 2025-07-23 | knocking / abnormal sound | 2025-02-27 | 2025-05-08 | 1429 | 850 | chemical / pharma | 4 | Abnormal sound due to the cylinder no. 5 Buffer spring shrinkage. | 5 | closed | Replaced BUFFER SPRING KC/KCX
2025-07-31 | Trade Links | Secunderabad | D | Dodla Dairy Limited | Sec | KCX2 | 3364K2873 | 5162449508 | 2025-07-28 | 516244 | 2025-07-28 | KRMSPressure sensor cable issue. | 2025-03-13 | 2025-07-28 | 0 | null | dairy / ice cream | 4 | Refer mail communication with HO Service | null | closed | Replaced PRESSURE SENSOR CABLE WITH CONNECTOR
2025-07-31 | Pragyaa Industrial Supply | Karnataka | D | Maggemane Milk Dairy | Ka | KCX2 | 3364K2789 | 5149649486 | 2025-07-19 | 514964 | 2025-07-18 | pressure gauge malfunctioning | 2024-11-26 | 2025-07-02 | 19 | 750 | dairy / ice cream | 7 | Oil pressure gauge malfunctioning, Replaced new gauge then found ok | null | closed | Replaced Pressure gauge 16kg/cm2
2025-07-31 | Pragyaa Industrial Supply | Karnataka | D | Nestle India Limited | Karnataka | KCX12 | 3415K086 | 5161429496 | 2025-07-24 | 516142 | 2025-07-24 | Oil separator float valve not working | 2023-12-12 | 2024-11-26 | 2000 | 700 | food processing | 12 | Opend float , float not working properly, cleaning return line strainer and flushed line with air. | null | closed | Replaced FLOAT VALVE ASSEMBLY FOR OIL SEP
2025-08-02 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Pushpai Marine Exports Pvt Ltd | Mh | KCX72 | 3474K882 | 5153709510 | 2025-07-29 | 515370 | 2025-07-17 | KRMS Discharge Pressure Alarm | 2025-01-31 | 2025-07-17 | 0 | null | null | 6 | Gargi Engineer attended the site for checking the discharge pressure readings, which were showing errors. During the visit, they verified the issue by cross-checking with another pressure transducer and concluded that the problem is isolated to a single pressure transducer | null | closed | Replaced DISCHARGE PRESSURE TRANSDUCER, 0 TO 5 Vdc, 0 TO 45 bar
2025-08-02 | Dicksons Engineering Company Pvt Ltd | Nagpur | D | S.R Agro Pvt Ltd | Mh | KCX4 | 3384K3488 | 5149929467 | 2025-07-16 | 514992 | 2025-07-16 | abnormal noise | 2023-11-20 | 2024-02-23 | 2054 | 750 | cold storage | 2 | Abnormal sound complaint. During site visits, they noticed that step cut found on cylinder liner no 3 and Piston rings were worn out. Also. clearance play noticed in connecting bush (3nos) and gudgeon pins Relevant images and FSR are attached for FRR approval process | 3 | closed | Replaced liner1, bush con rod3nos, piston ring set1nos.
2025-08-02 | Kalp Marketing | Gujrat | D | Ram Bulk-1 | Gj | KCX3 | 3374K3571 | 5143649434 | 2025-07-09 | 514364 | 2025-07-11 | Cylinder Overheating DV Leak | 2024-10-23 | 2025-02-08 | 408 | 767 | cold storage | 3 | Observed all 3 delivery valves rings springs broken | null | closed | Replaced DV3nos
2025-08-02 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Mathura Parsad Cold Storage | Up | KC3 | 337K4940 | 5161229498 | 2025-07-24 | 516122 | 2025-07-24 | Fitting LeakPipe bend, disch. filter to shaft seal cover found leak | 2025-01-16 | 2025-03-13 | 81.599999999999994 | 750 | cold storage | 1 | Pipe leakage was found and it became bigger during the opening. | null | closed | Replaced PIPE BEND, DISCH. FILTER TO SHAFT SEAL COVER. FOR KC3/KC21 MODEL
2025-08-02 | Multivista Global Pvt Ltd | Gurgaon | D | R D Cold Store | Up | KC4 | 338K6021 | 5167969521 | 2025-07-30 | 516796 | 2025-07-30 | Knocking Sound DV Leak | 2025-01-21 | 2025-03-17 | 94 | 750 | cold storage | 1 | DV valve found leakage. | null | closed | Replaced DV kit
2025-08-02 | Multivista Global Pvt Ltd | Tamil Nadu | D | Asal Food Products Ltd | Tn | KCX3 | 3374K3714 | 5132749449 | 2025-07-11 | 513274 | 2025-07-09 | shaft seal leakage | 2025-03-21 | 2025-07-09 | 6 | 993 | food processing | 3 | The shaft seal leaked within a few minutes of starting the compressor. I opened the shaft seal and checked it and found that the shaft seal was damaged. | null | closed | Replaced shaft seal assembly.
2025-08-21 | Pragyaa Industrial Supply | Karnataka | D | Vinp Distilleries And Sugars P. Ltd | Ka | KCX93 | 3485K227 | 5149849570 | 2025-08-11 | 514984 | 2025-08-11 | abnormal noise | 2024-10-28 | 2025-07-01 | 471 | 950 | beverage / breweries | 8 | Knocking sound in HP Cylinder | null | closed | Replaced Liner2nos, piston ring set12nos, big end bush1nos, piston1nos, gudeon pin1nos, Needle roller bearing1nos, Spacer for needle roller bearing1nos & DV1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Om Agro Cold Storage Llp | Up | KCX4 | 3384K3571 | 5162289503 | 2025-07-26 | 516228 | 2025-08-04 | abnormal noise | 2024-01-10 | 2024-06-13 | 1171 | 750 | cold storage | 4 | Liner & Ring Worn Out | null | closed | Replaced Liner2nos , Piston 2nos, Piston ring sets4nos and DV1Nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | A.K. Agro Food | Up | KCX4 | 3384K3941 | 5165329509 | 2025-07-28 | 516532 | 2025-08-11 | abnormal noise | 2025-01-16 | 2025-03-28 | 1561 | 750 | cold storage | 2 | Liner and Ring Worn out. | 1 | closed | Replaced liner1nos piston ring set4nos.
2025-08-21 | Parag Marketing Services | Maharashtra | D | Bhalerao Cold Chain | Mh | KCX51 | 3454K239 | 5155769566 | 2025-08-09 | 515576 | 2025-08-09 | abnormal noisedelivery valve leak | 2024-01-30 | 2024-06-07 | 5658 | 750 | cold storage | 4 | Abnormal sound complaint from Cylinder No. 1. Upon inspection, piston rings were found to be worn out &DV valve leak was identified in the cylinder liner of Cylinder No. 2 | 1 & DV-2 | closed | Replaced DV1nos , Piston ring set1nos & Liner1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Sunder Cold Storage | Up | KC6 | 339K3847 | 5155129482 | 2025-07-18 | 515512 | 2025-08-01 | high oil consumption | 2025-01-10 | 2025-03-18 | 575 | 750 | cold storage | 1 | Liner and piston ring worn out | null | closed | Replaced Liner1nos , Piston1nos & piston ring set1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | H. Saqlani Cold Storage | Up | KC4 | 338K6044 | 5161209497 | 2025-07-24 | 516120 | 2025-08-06 | high oil consumption | 2025-02-11 | 2025-03-19 | 1019.5 | 750 | cold storage | 1 | Cylinder Liner & Piston Ring Set worn out. | null | closed | Replaced piston ring set1nos & liner1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Tilokpur Cold Storage & Allied Industries | Up | KC6 | 339K3827 | 5158849487 | 2025-07-21 | 515884 | 2025-08-01 | solenoid coil issue | 2024-12-21 | 2025-03-24 | 512 | 773 | cold storage | 2 | SV Coil Burnt | null | closed | Replaced SV coil
2025-08-21 | Parag Marketing Services | Maharashtra | D | Washishti Milk And Milk Product Pvt Ltd | Chiplun Mh | KCX2 | 3364K2587 | 5155789532 | 2025-08-02 | 515578 | 2025-08-02 | cylinder overheatingdelivery valve leakage | 2023-11-30 | 2024-04-28 | 3200 | 750 | dairy / ice cream | 4 | Knocking sound and over heating complaint for cylinder liner no 2. During visit they noticed that DV valve leak and cylinder no 2 step cut marks. Replaced DV valve | 2 | closed | Replaced Piston1nos , Liner1nos , Piston ring set1nos & DV 1Nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Continental Milkose (India) Ltd | Up | KCX6 | 3394K2510 | 5164689505 | 2025-07-26 | 516468 | 2025-07-30 | high oil consumption | 2024-07-09 | 2024-10-10 | 1241.3 | 771 | dairy / ice cream | 2 | Piston Ring Worn Out | null | closed | Replaced Piston ring set 6nos
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Cm Food & Allied Product | Uk | KCX93 | 3485K220 | 5180709572 | 2025-08-11 | 518070 | 2025-08-11 | abnormal noise | 2024-09-23 | 2025-07-26 | 25 | 900 | food processing | 9 | Liner & Piston Ring worn out. | null | closed | Replaced Liner 2nos , Piston 2nos ring sets3nos, & oil pump assembly 1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Gera Fresh Foods | Hr | KCX63 | 3464K243 | 5180749573 | 2025-08-11 | 518074 | 2025-08-11 | abnormal noisedelivery valve leak | 2024-10-25 | 2025-02-17 | 2042 | 850 | food processing | 3 | Wavy ring of DV assembly found broken due to that other parts also gets damaged | null | closed | Replaced LINER 1nos, Poston1nos, piston ring set1nos, Buffer spring1nos, Gudgeon pin 1nos, DV assly 1nos and Valve spring suction 2nos.
2025-08-21 | Kalp Marketing | Gujrat | D | Veravali Krupa Ice & Cold Storage | Gj | KCX3 | 3374K3440 | 5166809560 | 2025-08-08 | 516680 | 2025-07-31 | high oil consumption | 2024-03-27 | 2024-08-11 | 5038 | 766 | ice plant | 4 | The liner has cut in 360 degree pattern resulting to damage the piston rings in adjacent cylinders as well | 1 | closed | Replaced Liner1nos Piston ring set3nos.
2025-08-21 | Kalp Marketing | Gujrat | D | Minaz Export | Gj | KCX4 | 3384K3772 | 5164309507 | 2025-07-28 | 516430 | 2025-08-18 | high oil consumption | 2024-08-24 | 2024-11-24 | 187 | 880 | ice plant | 2 | Premature failure were noticed in all the liners(Step cut) caused to damaged the Piston rings set alongwith the Thrust ring. | All | closed | Replaced Liner4nos, Piston ring set4nos & Thrust ring pump end 1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Tyagi Dairy | Up | KCX2 | 3364K2790 | 5181649578 | 2025-08-13 | 518164 | 2025-08-13 | high oil consumption | 2024-11-28 | 2025-08-05 | 65 | 750 | ice plant | 8 | Piston Ring worn Out | null | closed | Replaced piston ring2nos
2025-08-21 | Parag Marketing Services | Maharashtra | D | Shifa Food Product | Mh | KCX3 | 3374K3327 | 5179309564 | 2025-08-09 | 517930 | 2025-08-09 | high oil consumption | 2023-12-19 | 2024-04-03 | 3270 | 900 | ice plant | 3 | Observed knocking sound in compressor ,After checking found step cut on all cylinder liner | 3 | closed | Replaced Piston3nos ,Liner3nos & piston ring set3nos. Oring1nos gasket 1nos.
2025-08-21 | Parag Marketing Services | Maharashtra | D | Cooltrust Ice Plant | Mh | KCX4 | 3384K4011 | 5178309562 | 2025-08-08 | 517830 | 2025-08-08 | high oil consumption | 2025-03-08 | 2025-04-29 | 2008 | 800 | ice plant | 1 | Oil throw in open air trail. checked the cylinder liner. Found step cut mark on all cylinder ,Then checked all piston ring close gaps found 2.05mm to 3.4mm and found the pistons were rubbing. | All | closed | Replaced Liner4nos Piston4nos Piston Ring4nos, Lock plate con rod & bolt 8nos.
2025-08-21 | Kalp Marketing | Gujrat | D | Shri Himalay Ice & Cold Storage | Gujrat | KCX3 | 3374K3459 | 5165709561 | 2025-08-08 | 516570 | 2025-07-28 | Knocking Sound DV Leak | 2024-05-17 | 2024-07-19 | 5041 | 880 | ice plant | 1 | The dv rings of delivery valve found damaged in 2 cylinders resulting to damage liners,piston rings and piston. | null | closed | Replaced Liner2nos, piston1nos , Piston ring set3nos & DV 2Nos.
2025-08-21 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Larsen & Toubro Ltd | Gujrat | KCX21 | 3424K188 | 5152249475 | 2025-07-17 | 515224 | 2025-07-23 | Safety valve leak Suction Pressure High | 2025-05-21 | 2025-07-14 | 11.5 | 770 | ice plant | 1 | Safety valve leakage observed and the recirculation | null | closed | Replaced spring safety valve & tafelon ring safety valve 1Nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Alm Group | Up | KCX72 | 3474K873 | 5181689576 | 2025-08-12 | 518168 | 2025-08-14 | abnormal noise | 2024-11-30 | 2025-08-08 | 54 | 850 | meat/fish process | 8 | Liner & Piston Ring worn Out. | 4 | closed | Replaced Liner1nos, Piston1nos & Piston Ring1nos.
2025-08-21 | Trade Links | Secunderabad | D | Kader Exports Private Limited | Ap | KCX72 | 3474K729 | 5143449448 | 2025-07-11 | 514344 | 2025-07-11 | Cylinder Overheating DV Leak | 2023-12-28 | 2024-04-06 | null | 950 | meat/fish process | 3 | Cyl. No. 3 Delivery valve back leaking | 3 | closed | Replaced DV1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Alm Group | Up | KCX72 | 3474K873 | 5165649545 | 2025-08-05 | 516564 | 2025-08-08 | KCX Pump Element damaged. | 2024-11-30 | 2025-08-08 | 5 | 850 | meat/fish process | 8 | Oil Pump Element Found damaged | LC 11 24 836 | closed | Replaced Oil pump assly1nos & Pressure switch OP 1nos
2025-08-21 | Trade Links | Secunderabad | D | Aparna Marine Exports | Ap | KCX93 | 3485K256 | 5174029543 | 2025-08-04 | 517402 | 2025-08-04 | KCX Pump Low oil pressure | 2025-04-30 | 2025-07-21 | 50 | 950 | meat/fish process | 2 | Oil pump element was worn out. | LC 02 25 1152 | closed | Replaced oil pump assly
2025-08-21 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2695 | 5174889558 | 2025-08-07 | 517488 | 2025-08-05 | abnormal noise | 2025-02-27 | 2025-05-08 | 1743 | 850 | chemical / pharma | 2 | No 5 cylinder liner and piston worn out. | 5 | closed | Replaced liner1nos piston ring set1nos.
2025-08-21 | Multivista Global Pvt Ltd | Gurgaon | D | Agson Global Pvt Ltd | Haryana | KCX63 | 3464K263 | 5177029554 | 2025-08-06 | 517702 | 2025-08-12 | abnormal noise | 2025-03-27 | 2025-07-02 | 628 | 750 | chemical / pharma | 3 | Liner & Piston Ring Worn out. | HP | closed | Replaced liner 4nos, piston3nos and piston ring sets9nos
2025-08-21 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Chemino Pharma Ltd-Unit1 | Gj | KC6 | 339K3794 | 5162729534 | 2025-08-02 | 516272 | 2025-07-26 | high oil consumption | 2024-07-10 | 2024-09-26 | 1007 | 770 | chemical / pharma | 2 | Replaced all VLD O rings and 3 nos of ORV s | null | closed | Replaced valve return valve 6nos.
2025-08-21 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Chemino Pharma Ltd-Unit1 | Gj | KC6 | 339K3794 | 5168669533 | 2025-08-02 | 516866 | 2025-08-02 | high oil consumption | 2024-07-10 | 2024-09-26 | 1317.87 | 770 | chemical / pharma | 2 | Liner have cut mark, piston rings misalign. | null | closed | Replaced Liner 1nos & Piston ring sets 6nos
2025-08-21 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Gokul Industries | Gj | KCX6 | 3394K2492 | 5142149446 | 2025-07-11 | 514214 | 2025-07-20 | shaft seal leakage | 2024-06-01 | 2024-08-14 | 4474 | 750 | chemical / pharma | 2 | OIL LEAKAGE FROM THE SHAFT SEAL ASS Y | null | closed | Replaced shaft seal assly
2025-08-23 | Viet An Refrigeration Industry Co. - Ltd | Viet Nam | E | Viet An Refrigeration Industry Co., Ltd | Viet Nam | KCX6 | 3394K2772 | Mail | 2025-08-18 | null | 2025-08-18 | Rusty & Paint issue | 2025-06-20 | 2025-08-19 | 0 | null | null | 2 | Crankshaft rusty from external side on taper portion near dust sealing ring & Wet paint/Wrinkles on discharge pipe. | null | open | null
2025-08-23 | Viet An Refrigeration Industry Co. - Ltd | Viet Nam | E | Viet An Refrigeration Industry Co., Ltd | Viet Nam | KCX6 | 3394K2771 | Mail | 2025-08-18 | null | 2025-08-18 | Rusty & Paint issue | 2025-06-20 | 2025-08-19 | 0 | null | null | 2 | Crankshaft rusty from external side on taper portion near dust sealing ring & Wet paint/Wrinkles on discharge pipe. | null | open | null
2025-08-23 | Gargi Engineering Enterprises Pvt Ltd | Vadodara | D | Global Gourmet Pvt Ltd (Unit Iii) | Gj | KCX72 | 3474K779 | 5188709617 | 2025-08-20 | 518870 | 2025-08-20 | Oil filter manifold M10 bolts broken | 2024-05-14 | 2025-02-04 | 2365 | 990 | food processing | 9 | Oil filter manifold M10 bolts broken | NA | closed | Replaced M10 Allun bolts 2 pairs.
2025-08-23 | Gargi Engineering Enterprises Pvt Ltd | Vadodara | D | Global Gourmet Pvt Ltd (Unit Iii) | Gj | KCX72 | 3474K773 | 5188709617 | 2025-08-20 | 518870 | 2025-08-20 | Oil filter manifold M10 bolts broken | 2024-05-14 | 2025-02-04 | 2365 | 990 | food processing | 9 | Oil filter manifold M10 bolts broken | NA | closed | Replaced M10 Allun bolts 2 pairs.
2025-08-23 | Gargi Engineering Enterprises Pvt Ltd | Vadodara | D | Global Gourmet Pvt Ltd (Unit Iii) | Gj | KCX72 | 3474K771 | 5187149602 | 2025-08-18 | 518714 | 2025-08-18 | Oil filter manifold M10 bolts broken | 2024-05-14 | 2025-02-04 | 619 | 990 | food processing | 9 | Oil filter manifold M10 bolts broken | NA | closed | Replaced M10 Allun bolts 2 pairs.
2025-08-23 | Gargi Engineering Enterprises Pvt Ltd | Vadodara | D | Global Gourmet Pvt Ltd (Unit Iii) | Gj | KCX4 | 3384K3700 | 5188769620 | 2025-08-20 | 518876 | 2025-08-20 | Oil filter manifold M10 bolts broken | 2024-05-14 | 2025-02-04 | 1463 | 990 | food processing | 9 | Oil filter manifold M10 bolts broken | NA | closed | Replaced M10 Allun bolts 2 pairs.
2025-08-23 | Gargi Engineering Enterprises Pvt Ltd | Vadodara | D | Global Gourmet Pvt Ltd (Unit Iii) | Gj | KCX72 | 3474K780 | 5188749619 | 2025-08-20 | 518874 | 2025-08-20 | Oil filter manifold M10 bolts broken | 2024-05-14 | 2025-02-10 | 1368 | 990 | food processing | 9 | Oil filter manifold M10 bolts broken | NA | closed | Replaced M10 Allun bolts 2 pairs.
2025-08-26 | Parag Marketing Services | null | D | Shifa Food Product | Mh | KCX3 | 3374K3326 | 5179289563 | 2025-08-09 | 517928 | 2025-08-09 | high oil consumption | 2023-12-19 | 2024-04-01 | 3237 | 900 | ice plant | 4 | Step cut on all cylinder liners & abnormal noise | all 3 | closed | Replaced liner , piston ring & Piston 3 nos
2025-08-28 | Viet An Refrigeration Industry Co. - Ltd | Viet Nam | E | Viet An Refrigeration Industry Co., Ltd | Viet Nam | KCX6 | 3394K2772 | Mail | 2025-08-27 | null | 2025-08-27 | Oil Black within 3 Hrs | 2025-06-20 | 2025-08-19 | 3 | null | null | 2 | Oil came to black after around 03 hrs running while KCX6 Sr. 3394K2271 running 05 days oil is still transperent. They are running in the same system as parallel compressors, using same oil. | null | open | null
2025-08-30 | Multivista Global Pvt Ltd | Gurgaon | D | Jai Ambey Ice & Cold Storage | Up | KC4 | 338K6005 | 5173289546 | 2025-08-05 | 517328 | 2025-08-05 | abnormal noise | 2025-01-09 | 2025-01-09 | 1173 | 750 | cold storage | 1 | Cylinder Liner, Piston & Piston Rin g Worn Out. | All | open | Replaced Liners & piston rings 4
2025-08-30 | Multivista Global Pvt Ltd | Gurgaon | D | Rama Cold Storage | Up | KC2 | 336K3439 | 5184389599 | 2025-08-24 | 518438 | 2025-08-24 | abnormal noise | 2024-12-17 | 2025-03-29 | 209 | 750 | cold storage | 3 | Cylinder Liner, Piston & Piston Rin g Worn Out. | All | open | Replaced Liners & piston rings
2025-08-30 | Cool Comfort Private Limited | West Bengal | D | Kishan Bandhu Himghar Pvt Ltd | Wb | KCX6 | 3394K2430 | 5188869626 | 2025-08-20 | 518886 | 2025-08-20 | cylinder overheating | 2024-02-02 | 2025-03-25 | 145 | 850 | cold storage | 13 | one valve seat damaged and one kit broken | 3.4 | open | Replaced DV1 & Kit1
2025-08-30 | Model Pneumatic Co | Punjab | D | Armaan Cold Store Pvt Ltd | Pb | KCX4 | 3384K3948 | 5193709646 | 2025-08-23 | 519370 | 2025-08-23 | kcx pump tang broken | 2025-01-22 | 2025-03-17 | 1261 | 750 | cold storage | 2 | Pump seized and tang broken | N 174 12 24 | open | Replaced Pump assembly
2025-08-30 | Parag Marketing Services | Maharashtra | D | Srushti Milk And Milk Products | Solapur | KCX4 | 3384K4021 | 5123669468 | 2025-07-16 | 512366 | 2025-07-16 | high oil consumption | 2025-03-17 | 2025-04-10 | 1991 | 750 | dairy / ice cream | 1 | 1) Step cut marks found on 3 nos. of cylinder liners 2) 4 nos. of 397 code piston rings worn out 3) 4 nos. of pistons found to be worn out | All 4 | open | Replaced 3 liners , 4 piston and piston rings .
2025-08-30 | Kalp Marketing | Gujrat | D | Shreedhi Milk & Milk Products | Mp | KCX4 | 3384K3675 | 5188349629 | 2025-08-21 | 518834 | 2025-08-21 | shaft seal leakage | 2024-03-19 | 2025-02-03 | 456 | 770 | dairy / ice cream | 11 | Shaft seal assembly leak , wornout and Oring flatened. | NA | open | Replaced shaft seal assembly
2025-08-30 | Trade Links | Secunderabad | D | K V Reddy & Co Ice Factory | Ap | KCX4 | 3384K3652 | 5168769565 | 2025-07-31 | 516876 | 2025-07-31 | high oil consumption | 2024-02-27 | 2024-06-03 | 7542 | 878 | ice plant | 4 | Cylinder Liner, Piston & Piston Rin g Worn Out. | All | open | Replaced all 4 liners and piston rings.
2025-08-30 | Trade Links | Secunderabad | D | Maa Kali Ice Plant | Ap | KCX6 | 3394K2454 | 5160349504 | 2025-07-26 | 516034 | 2025-07-26 | high oil consumption | 2024-03-04 | 2025-07-03 | 442 | 850 | ice plant | 16 | Within 442 hrs. , since commissioning of compressor , piston ring and liners worn out abnormally. Spare parts replaced from Tl stock with 107 piston ring | All 6 | open | Replaced all 6 liners and piston rings.
2025-08-30 | Trade Links | Secunderabad | D | Sri Vishnu Smitha Ice Factory | Ap | KCX4 | 3384K3577 | 5149729490 | 2025-07-22 | 514972 | 2025-07-22 | high oil consumption | 2024-01-15 | 2024-04-05 | 7684 | 850 | ice plant | 3 | Each day, 4 liters of oil were being lifted, and some unusual sounds were also noted in the compressor.All 4 liners and piston rings worn out. | All 4 | open | Replaced 4 liners & piston ring sets
2025-08-30 | Trade Links | Secunderabad | D | Ananda Fisheries | Ap | KCX6 | 3394K2601 | 5160209502 | 2025-07-26 | 516020 | 2025-07-25 | high oil consumption | 2024-11-26 | 2024-12-07 | 2096 | 850 | ice plant | 1 | All liners and pistons were determined to be excessively worn. | all 6 | open | Replaced all 6 liners and piston rings & 3 pistons
2025-08-30 | Kalp Marketing | Gujrat | D | Madina Ice Factory | Gj | KCX3 | 3374K3531 | 5182089613 | 2025-08-19 | 518208 | 2025-08-19 | kcx pump air purging | 2024-08-29 | 2024-11-08 | 2855 | 880 | ice plant | 3 | Pump element wornout leads purging issue | LC 07 24 432 | open | Replaced pump element due to wornout.
2025-08-30 | Multivista Global Pvt Ltd | Gurgaon | D | Alm Group | Up | KCX72 | 3474K874 | 5189209624 | 2025-08-20 | 518920 | 2025-08-20 | abnormal noise | 2024-11-30 | 2025-08-05 | 248 | 850 | meat/fish process | 9 | cylinder liner 02, piston 02, and piston ring set 02 of HP side were found damaged. | HP 1 & 4 | open | Replaced Liners & piston rings
2025-08-30 | Geekay Pneumatics Pvt Ltd | Kerala | D | Milma Dairy Plant | Kerala | KCX2 | 3364K2694 | 5179269585 | 2025-08-29 | 517926 | 2025-08-29 | high oil consumption | 2024-05-31 | 2025-01-14 | 763 | 980 | meat/fish process | 8 | Cylinder Liner, Piston & Piston Rin g Worn Out. | All | open | Replaced liners and pistonr rings 2 nos.
2025-08-30 | Multivista Global Pvt Ltd | Gurgaon | D | Alm Group | Up | KCX72 | 3474K873 | 5188809622 | 2025-08-20 | 518880 | 2025-08-20 | KCX Pump low oil pressure issue | 2024-11-30 | 2025-08-08 | 151 | 850 | meat/fish process | 9 | Once suction pressure goes down on that that time pump unable to maintain DP and gradually drop below 1 KG | LC 11-24-836 | open | Replaced pump assly
2025-08-30 | Kalp Marketing | Gujrat | D | Al Karam Exports | Gj | KCX72 | 3474K789 | 5176889574 | 2025-08-19 | 517688 | 2025-08-19 | shaft seal leakage | 2024-05-30 | 2025-08-19 | 29 | 993 | meat/fish process | 3 | Shaft seal leak …Site analysis ? | NA | open | Replaced shaft seal
2025-08-30 | Trade Links | Secunderabad | D | Assago Industries Pvt. Ltd | Ap | KCX93 | 3485K213 | 5173109544 | 2025-08-05 | 517310 | 2025-08-05 | cylinder overheating HP | 2024-06-27 | 2025-04-12 | 652 | 950 | others | 9 | The back leakage from the discharge valve of HP Cylinder No. 1 and 4 has caused damage to other components. | 1 & 4 | open | Replaced cylinder assembly 2 nos.
2025-08-30 | Multivista Global Pvt Ltd | Gurgaon | D | Agson Global Pvt Ltd | Haryana | KCX63 | 3464K262 | 5160269499 | 2025-08-02 | 516026 | 2025-08-02 | abnormal noise | 2025-03-27 | 2025-07-02 | 304 | 750 | chemical / pharma | 4 | Cylinder Liner, Piston & Piston Rin g Worn Out. | All | open | Replaced Liners 5 , Piston 3 & piston rings 9
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shri Mathura Parsad Cold Storage | Up | KC4 | 338K6013 | 5183189650 | 2025-08-25 | 518318 | 2025-09-01 | abnormal noise | 2025-01-16 | 2025-03-13 | 1171.8 | 750 | cold storage | 1 | Liner Piston Worn out. | All | closed | Replaced Liner 4nos, Piston 3nos & Piston ring set 4nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | H Saqlaini Cold Store | Up | KC3 | 337K4963 | 5192849643 | 2025-08-22 | 519284 | 2025-09-01 | abnormal noise | 2025-02-22 | 2025-03-19 | 922.4 | 750 | cold storage | 1 | Liner and Piston worn out. | 1&2 | closed | Replaced Liner2nos ,Piston ring sets3nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Mldc Cold Solutions Llp | Up | KCX3 | 3374K3672 | 5200209671 | 2025-08-29 | 520020 | 2025-08-29 | abnormal noise | 2025-01-30 | 2025-04-06 | 360.9 | 750 | cold storage | 3 | Liner And Piston Ring worn out. | 3 | closed | Replaced Liner 1nos, Piston1nos & Piston ring sets 3nos
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Parwana Cold Storage | Up | KC4 | 338K5942 | 5189309625 | 2025-08-20 | 518930 | 2025-08-28 | abnormal noise | 2024-05-30 | 2025-02-12 | 701.4 | 750 | cold storage | 7 | Liner & Piston ring worn-out | null | closed | Replaced liner1nos & piston ring sets4nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Ghazi Brothers Cold Storage | Up | KCX6 | 3394K2661 | 5188669623 | 2025-08-20 | 518866 | 2025-09-10 | abnormal noise | 2025-02-04 | 2025-03-19 | 1596 | 750 | cold storage | 1 | Liner and Piston worn out. | null | closed | Replaced Liner 3nos, Piston1nos & piston ring set6nos.
2025-09-17 | Kalp Marketing | Gujrat | D | Patidar Agricare | Gj | KCX4 | 3384K3657 | 5201369681 | 2025-08-30 | 520136 | 2025-08-30 | cylinder overheating | 2024-03-04 | 2024-03-22 | 5561 | 800 | cold storage | null | DV rings/springs of middle one found broken | 3 | closed | Replaced DV 1 nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Navyug Cold Storage | Up | KCX6 | 3394K2612 | 5199789683 | 2025-08-31 | 519978 | 2025-09-10 | high oil consumption | 2024-12-13 | 2025-03-06 | 764 | 750 | cold storage | 2 | Liner and Piston ring set worn out. | null | closed | Replaced Liner 4nos, Piston ring set 6nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Shree Ji Coldstorage | Up | KC3 | 337K4960 | 5146889457 | 2025-07-14 | 514688 | 2025-08-24 | high oil consumption | 2025-02-11 | 2025-03-22 | 655 | 750 | cold storage | 1 | Liner And Piston ring worn out. | null | closed | Replaced Liner 3nos, Piston 1nos & Piston ring set 3nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | R.K.V.K Cold Storage Pvt Ltd | Up | KCX4 | 3384K3757 | 5193129640 | 2025-08-22 | 519312 | 2025-08-29 | high oil consumption | 2024-08-10 | 2024-08-29 | 3805 | 750 | cold storage | null | Liner And Piston ring worn out. | 1&2 | closed | Replaced Liner 2Nos, Piston 2Nos & Piston ring set 4Nos
2025-09-17 | Model Pneumatic Co | Punjab | D | Rab Cold Store | Pb | KCX4 | 3384K3894 | 5199929684 | 2025-08-28 | 519992 | 2025-08-28 | high oil consumption | 2024-12-18 | 2025-03-08 | 1519 | 750 | cold storage | 2 | Found the DV assembly leakage , and other parts also get worn. | 3 | closed | Replaced Piston1nos, DV1nos, Piston ring 1nos & Liner 1nos.
2025-09-17 | Parag Marketing Services | Maharashtra | D | Ifc Overseas | Mh | KCX2 | 3364K2797 | 5148809605 | 2025-08-18 | 514880 | 2025-08-18 | shaft seal leakage | 2024-11-30 | 2025-03-20 | 280 | 700 | cold storage | 3 | Found shaft seal seat damaged | null | closed | Replaced shaft seal assly
2025-09-17 | Parag Marketing Services | Maharashtra | D | Milky More Industries | Mh | KCX2 | 3364K2717 | 5189149670 | 2025-08-29 | 518914 | 2025-08-29 | abnormal noise | 2024-07-11 | 2024-12-28 | 830 | 800 | dairy / ice cream | 4 | Step cuts on 2 cylinder liners, worn-out piston rings, and pistons showing rubbing marks. | All | closed | Replaced Liner 2nos, Piston 2nos , Piston ring set 2nos. & Lock plate conrod & inter hsg bolt 2nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Ali Ice Plant | Hr | KCX3 | 3374K3683 | 5198009657 | 2025-08-26 | 519800 | 2025-09-04 | high oil consumption | 2025-02-15 | 2025-04-30 | 1491 | 767 | dairy / ice cream | 1 | Liner and Ring set worn out. | 1&3 | closed | Replaced Liner 2nos & piston ring sets 3nos.
2025-09-17 | Parag Marketing Services | Maharashtra | D | Parag Milk Foods Ltd | Mh | KCX42 | 3444K0460 | 5194369645 | 2025-08-23 | 519436 | 2025-08-23 | KRMS Suction temperature sensor malfunction. | 2024-03-29 | 2024-09-25 | 6770 | 700 | dairy / ice cream | 5 | KRMS suction temperature sensor reading error. | null | closed | Replaced suction temp sensor ()50105⁰
2025-09-17 | Kalp Marketing | Gujrat | D | Jain Dairy Product Pvt. Ltd | Gj | KCX63 | 3464K210 | 5201229674 | 2025-08-30 | 520122 | 2025-08-30 | shaft seal leakage | 2024-03-09 | 2024-06-13 | 1048 | 850 | dairy / ice cream | 2 | Leakage of Shaft seal from Orings | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX
2025-09-17 | Trade Links | Secunderabad | D | Heritage Foods Ltd | Ap | KZX6 | 3216K 004 | 5170849568 | 2025-08-11 | 517084 | 2025-08-15 | shaft seal leakage | 2025-06-14 | 2025-07-13 | 414 | 1300 | dairy / ice cream | 1 | The shaft seal has deteriorated due to the abnormal wear of the piston ring, which allowed particles to enter the shaft seal area. | null | closed | Replaced shaft seal assly
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Vashisht Enterprises | Uk | KCX63 | 3464K235 | 5197989655 | 2025-08-26 | 519798 | 2025-08-31 | abnormal noise | 2024-09-30 | 2025-02-11 | 805 | 750 | food processing | 4 | Liner & Piston ring worn out. | 3 | closed | Replaced Liner 3nos, Piston3nos & piston ring set3nos.
2025-09-17 | Trade Links | Secunderabad | D | Pramadha Aquatic Exports | Ap | KCX12 | 3415K0065 | 5179669596 | 2025-08-17 | 517966 | 2025-08-10 | high oil consumption | 2023-08-30 | 2025-03-29 | 389 | 950 | food processing | 18 | Oil lifting due to abnormal wearing | 10 | closed | Replaced liner 1nos & Piston ring sets 4nos
2025-09-17 | Kalp Marketing | Gujrat | D | Mc Patel Foods Pvt Ltd | Gj | KCX9 | 3404K400 | 5205209702 | 2025-09-03 | 520520 | 2025-09-03 | pressure gauge leak | 2025-02-28 | 2025-08-20 | 107 | 938 | food processing | 5 | Leakage of Pressure Gauge | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-09-17 | Trade Links | Secunderabad | D | Godavari Ice & Cold Storage | Ap | KCX4 | 3384K3659 | 5198169695 | 2025-09-01 | 519816 | 2025-09-01 | cylinder overheating | 2024-03-12 | 2024-05-31 | 5979 | 800 | ice plant | 2 | NO 4 cylinder discharge valve back leakage and resulting other damaged | 4 | closed | Replaced DV1Nos, Bush con rod 1nos, Bearing bush big end con rod 1nos, Liner 1nos, Piston ring set 1nos, Piston 1nos & Gudeon pin 1nos.
2025-09-17 | Trade Links | Secunderabad | D | Kmc Ice Factory | Ap | KCX4 | 3384K3863 | 5182149589 | 2025-08-14 | 518214 | 2025-08-14 | high oil consumption | 2024-11-28 | 2025-03-24 | 2955 | 750 | ice plant | 3 | Wearing of Cylinder liner within 500 hrs of running | All | closed | Replaced Liner4nos Piston Ring sets4nos, DV1nos.
2025-09-17 | Trade Links | Secunderabad | D | Devi Ice Factory | Ap | KCX6 | 3394K2705 | 5145949595 | 2025-08-17 | 514594 | 2025-07-13 | high oil consumption | 2025-04-08 | 2025-04-11 | 2020 | 900 | ice plant | null | Oil lifting due to abnormal wearing | All | closed | Replaced liner 6nos & Piston ring sets 6nos
2025-09-17 | Parag Marketing Services | Maharashtra | D | Sitara Ice And Cold Storage | Mh | KCX6 | 3394K2540 | 5192209659 | 2025-08-28 | 519220 | 2025-08-28 | high oil consumption | 2024-09-25 | 2025-03-24 | 633 | 900 | ice plant | 6 | Found step ciut mark on cylinder liner | All | closed | Replaced Liner 6nos, Piston 4nos , Piston ring set 6nos. & Lock plate conrod & inter hsg bolt 6nos.
2025-09-17 | Cool Comfort Private Limited | West Bengal | D | Shankha Deep Exports Pvt Ltd | Wb | KCX2 | 3364K2884 | 5207889711 | 2025-09-05 | 520788 | 2025-09-05 | high oil consumption | 2025-03-26 | 2025-05-13 | 750 | 850 | ice plant | 1 | Oil lifting issue and he observed during his visit that liner step mark on top side and oil troughing from both cylinder. | All | closed | Replaced Liner 2nos & Piston ring set 2nos.
2025-09-17 | Trade Links | Secunderabad | D | Sri Mutyalamma Ice Factory | Ap | KCX4 | 3384K4009 | 5166349642 | 2025-08-22 | 516634 | 2025-08-02 | high oil consumption | 2025-03-03 | 2025-04-29 | 1399 | 750 | ice plant | 1 | Found plenty of oil in discharge chamber which is abnormal. Also observed all delivery valves are not free over cylinder and immovable. opened slowly and took open trial n found no oil throw over pistons | All | closed | Replaced Liner4nos, Piston ring set4nos, Oil return valve4Nos, Oring1Nos, Gasket1Nos, KOil 2nos.
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | S Ali Azam Ice Plant | Up | KCX3 | 3374K3702 | 5197129656 | 2025-08-26 | 519712 | 2025-09-05 | Solenoid spindle damaged | 2025-02-27 | 2025-04-17 | 2520.8000000000002 | 750 | ice plant | 1 | Pressure Gauge arranged by customer and SV coil Burnt due to that solenoid spindle get damaged. | null | closed | Replaced solenoid valve1nos
2025-09-17 | Multivista Global Pvt Ltd | Gurgaon | D | Aov Agro Foods Private Limited | Hr | KCX3 | 3374K3797 | 5202809701 | 2025-09-03 | 520280 | 2025-09-06 | kcx pump tang broken | 2025-08-04 | 2025-08-29 | 3 | 900 | meat/fish process | null | Drive Gear Tang broken | NE 423 07 25 | closed | Replaced oil pump assly
2025-09-17 | Parag Marketing Services | Maharashtra | D | Gadre Marine Export Pvt Ltd | Mh | KCX72 | 3474K801 | 5192809631 | 2025-08-21 | 519280 | 2025-08-21 | Knocking sound HP Piston Crack | 2024-07-18 | 2025-01-01 | 24 | 1000 | meat/fish process | 5 | Knocking sound issue. During the inspection, it was found that Cylinder No. 1 piston is cracked on the top side. The DV assembly was checked and found to be in good condition, with no visible defects. | 1 | closed | Replaced piston1nos
2025-09-17 | Kalp Marketing | Gujrat | D | Taiba Exports | Gj | KCX31 | 3434K0272 | 5201509679 | 2025-08-30 | 520150 | 2025-08-30 | pressure gauge leak | 2025-02-14 | 2025-08-11 | 10 | 875 | meat/fish process | 5 | Glycerin Leakage | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 25 KG/CM2 , 100MM DIAL, GLYSERINE FILLED
2025-09-17 | Kalp Marketing | Gujrat | D | Sea Star Marine Impex | Gj | KCX51 | 3454K269 | 5201489676 | 2025-08-30 | 520148 | 2025-08-30 | pressure gauge leak | 2025-03-08 | 2025-08-28 | 6 | 990 | meat/fish process | 4 | Glycerin Leakage | null | closed | Replaced AMMONIA PRESSURE GAUGE WITH BOTTOM ENTRY, RANGE ()760MM OF HG TO 16 KG/CM2, 100MM DIAL, GLYSERINE FILLED
2025-09-17 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2738 | 5198289666 | 2025-08-29 | 519828 | 2025-08-28 | stop valve leakage | 2025-04-29 | 2025-08-28 | 4 | 800 | chemical / pharma | 3 | Discharge Tal valve 80/100 leaking while pressure testing ,inspected the valve internal parts Teflon ring found damaged | null | closed | Replaced TEFLON SEAT BOTTOM TAL 80/100.
2025-09-23 | Multivista Global Pvt Ltd | Gurgaon | D | Sunder Cold Storage | Up | KC6 | 339K3847 | 5216749749 | 2025-09-15 | 521674 | 2025-09-20 | abnormal noise | 2025-01-10 | 2025-03-18 | 725 | 750 | cold storage | 1 | Liner and Piston Ring Worn Out. | 1,2&6 | closed | Replaced Liner3nos, piston3nos & piston ring set 6nos.
2025-09-23 | Multivista Global Pvt Ltd | Gurgaon | D | Healthy Ways Milk Product Pvt. Ltd | Up | KCX1 | 3354K332 | 5206249707 | 2025-09-04 | 520624 | 2025-09-04 | high oil consumption | 2024-05-22 | 2024-07-27 | 1637 | 750 | dairy / ice cream | 1 | ORV plate came out from assembly. | null | closed | Replaced ORV 1nos.
2025-09-23 | Hss Solutions Pvt Ltd | Rajastan | D | Agastya Industries | Rj | KCX2 | 3364K2719 | 5199629686 | 2025-09-01 | 519962 | 2025-08-30 | shaft seal leakage | 2024-07-13 | 2025-05-03 | 1114 | 764 | dairy / ice cream | 13 | Leakage did not stop even after lapping, after replacement of new seal | null | closed | Replaced Shaft seal assly 1nos.
2025-09-23 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2441 | 5208289715 | 2025-09-06 | 520828 | 2025-09-06 | cylinder overheating | 2024-02-12 | 2024-06-03 | 16102 | 800 | food processing | 3 | Cylinder no 3 liner DV valve leak and due to that all spares were damaged. | 3 | closed | Replaced Liner 1nos, Piston 1Nos, Piston ring sets 1nos, DV1nos, Bush conrod1nos, Gudeon Pin 1nos,
2025-09-23 | Kalp Marketing | Gujrat | D | Zenith International | Gj | KCX72 | 3474K891 | 5216989751 | 2025-09-16 | 521698 | 2025-09-18 | abnormal noise | 2025-03-10 | 2025-08-26 | 22 | 991 | meat/fish process | 4 | Both HP liners have cut in 360 degree(Ring) Patter | 1&2 | closed | Replaced Liner 2Nos Piston ring set 2nos.
2025-09-29 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX6 | 3394K2321 | 5210589725 | 2025-09-08 | 521058 | 2025-09-08 | abnormal noise | 2023-10-26 | 2024-03-14 | 5855 | 800 | food processing | 4 | 1) Step cut marks and oil throw on cylinder liners 1 and 3 2) DV leakage in cylinder liner 4 3) All piston rings were worn out (397 Codes) | 1,2,3,4 | closed | Replaced Liner2 Nos, DV 1 Nos & Piston ring set 4 Nos.
2025-10-09 | Model Pneumatic Co | Punjab | D | Goyal Cold Storage | Pb | KCX6 | 3394K2597 | 5224709780 | 2025-09-25 | 522470 | 2025-09-27 | high oil consumption | 2024-11-22 | 2025-03-04 | 1855 | 750 | cold storage | 3 | Liner and piston ring worn Out. | 1 & 4 | closed | Replaced Piston2nos ,Liner2nos & piston ring set2nos.
2025-10-09 | Multivista Global Pvt Ltd | Gurgaon | D | Pallavi Cold Storage & Ice Factory Pvt. Ltd | Up | KCX6 | 3394K2656 | 5223809774 | 2025-09-23 | 522380 | 2025-10-02 | high oil consumption | 2025-01-31 | 2025-03-12 | 1456 | 1456 | cold storage | 1 | Liner and Piston Worn Out. | null | closed | Replaced Liner4nos, Piston2nos & Pidton ring sets 6nos.
2025-10-09 | Kalp Marketing | Gujrat | D | Adani Wilmar Limited | Gj | KCX3 | 3374K3604 | 5120169378 | 2025-06-27 | 512016 | 2025-06-26 | high oil consumption | 2024-11-22 | 2025-03-13 | 1417 | 768 | cold storage | 3 | The liner has cut in 360 degree pattern(Ring Cut) thus resulting to damaged the piston rings in adjacent cylinders as well. | 1 | closed | Replaced Liner1nos, Piston ring set3nos, Thrust ring pump end bearing cover1nos & Buffer Spring1Nos
2025-10-09 | Parag Marketing Services | Chhatisgarh | D | Ratnapriya Cold Storage | Cg | KCX4 | 3384K3824 | 5176769763 | 2025-09-20 | 517676 | 2025-09-19 | pressure switch malfunctioning | 2024-10-29 | 2025-09-19 | 2 | 750 | cold storage | 11 | Tripping op cutout even if ODP is m ore than 1 ka/cm2 | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-10-09 | Parag Marketing Services | Maharashtra | D | Sonai Chilling Center | null | PCX2 | 3106K0358 | 5224569793 | 2025-09-28 | 522456 | 2025-09-27 | oil pump tang broken | 2025-08-14 | 2025-09-27 | 7 | 1000 | dairy / ice cream | 1 | Oil pump jam and non-rotation of the flywheel. During inspection, scoring marks were observed on the gear plate | PC2 LC 07 2025 27 | closed | Replaced Oil pump assly 1nos, Driving gear1nos, Driven gear 2nos, Bearing bush oil pump 1nos, Bush small bush oil pump & Oring shaft seal cover 3nos.
2025-10-09 | Model Pneumatic Co | Punjab | D | Sahib Farm Nainewal | Punjab | KCX2 | 3364K2778 | 5218189755 | 2025-09-17 | 521818 | 2025-09-17 | pressure switch malfunctioning | 2024-10-29 | 2025-07-23 | 5 | 750 | dairy / ice cream | 7 | Oil pressure switch issue | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-10-09 | Kalp Marketing | Gujrat | D | Deepkiran Foods Pvt Ltd | Gj | KCX42 | 3444K530 | 5219269764 | 2025-09-20 | 521926 | 2025-09-20 | oil pump tang broken | 2025-08-08 | 2025-09-20 | 3 | 880 | food processing | 1 | Tang Broken | NE 241 03 25 | closed | Replaced KIT OIL PUMP GEAR KCX
2025-10-09 | Trade Links | Secunderabad | D | Ananda Fisheries | Ap | KCX6 | 3394K2601 | 5225589783 | 2025-09-26 | 522558 | 2025-09-26 | high oil consumption | 2024-11-26 | 2024-12-07 | 5281 | 850 | ice plant | null | No 5 cylinder piston found crack and piston ring worn out. | 5 | closed | Replaced Piston1nos & Piston ring set1nos.
2025-10-09 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Ap | KCX4 | 3384K3830 | 5212069743 | 2025-09-12 | 521206 | 2025-09-12 | high oil consumption | 2024-11-07 | 2024-12-27 | 3078 | 850 | ice plant | 1 | Delivery valve spring had broken into pieces, and all piston rings were significantly worn out. Additionally, the liners for cylinders 1 and 3 were noted that worn out. | 1&3 | closed | Replaced Liner2nos, DV4nos & Piston ring set4nos
2025-10-09 | Geekay Pneumatics Pvt Ltd | Kerala | D | Eminent Sea Foods Pvt Ltd | Kerala | KCX2 | 3364K2953 | 5177989569 | 2025-08-11 | 517798 | 2025-08-08 | pressure switch malfunctioning | 2025-07-22 | 2025-08-08 | 20 | 755 | ice plant | 1 | OP CUT OUT MALFU NCTIONING | null | closed | Replaced PRESSURE SWITCH OP MP55A
2025-10-09 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Vkm Foods Pvt Ltd Taloja | Mh | KCX3 | 3374K3573 | 5218069768 | 2025-09-22 | 521806 | 2025-09-19 | cylinder overheating | 2024-10-25 | 2024-11-01 | 4728 | 800 | meat/fish process | null | DV leak had caused severe wear on the cylinder liner, resulting the piston, piston rings, buffer spring, and other related sectional components were affected due to this leak | 1 | closed | Replaced DV1nos, Buffer spring1nos, Ring Suction Valve1nos, Valve spring suction2nos, Piston1nos, Liner1nos, Piston ring set1nos, & Kit cylinder maintenace 1nos.
2025-10-09 | Multivista Global Pvt Ltd | Tamil Nadu | D | St. Peter & Paul Seafood Exports Pvt Ltd | Tn | KCX93 | 3485K185 | 5193769734 | 2025-09-11 | 519376 | 2025-09-22 | cylinder overheating | 2024-02-15 | 2025-09-22 | 9 | 900 | meat/fish process | 18 | Discharge Valve leak | HP-4 | closed | Replaced Piston1nos, Gudgeon pin1nos, Piston Ring1nos, DV1nos, Buffer Spring1nos, Liner1nos.
2025-10-18 | Model Pneumatic Co | Punjab | D | G.S. Farm & Cold Store | Pb | KCX4 | 3384K3794 | 5239289833 | 2025-10-08 | 523928 | 2025-10-08 | abnormal noise | 2024-09-30 | 2025-02-21 | 1653 | 800 | cold storage | 4 | Liner and Piston Worn Out. | 1 | closed | Replaced Piston1Nos, Liner1Nos, Piston ring set1Nos.
2025-10-18 | Multivista Global Pvt Ltd | Gurgaon | D | Ganpati Dairy Products Pvt Ltd | Hr | KCX4 | 3384K4083 | 5236409829 | 2025-10-07 | 523640 | 2025-10-07 | hour meter not working | 2025-07-29 | 2025-10-07 | 5 | 880 | dairy / ice cream | null | Hour Meter not working | null | closed | Replaced hour meter
2025-10-18 | Multivista Global Pvt Ltd | Gurgaon | D | Gera Fresh Foods | Hr | KCX72 | 3474K850 | 5237209831 | 2025-10-08 | 523720 | 2025-10-07 | abnormal noisedelivery valve leak | 2024-10-25 | 2025-02-17 | 755 | 850 | food processing | 3 | HP cyl Wavy Ring Of Discharge Valve found Broken. | HP | closed | Replaced DV1Nos
2025-10-18 | Model Pneumatic Co | Punjab | D | Pancarbo Greenfuels Private Limited | Pb | KCX72 | 3474K747 | 5228849816 | 2025-10-03 | 522884 | 2025-10-03 | high oil consumption | 2024-02-29 | 2024-08-11 | 6711 | 992 | chemical / pharma | 5 | DV assembly get leak and wavy spring found broken due | 4 | closed | Replaced Piston1Nos, Liner1Nos, Piston ring set1Nos & DV1nos.
2025-10-20 | Multivista Global Pvt Ltd | Gurgaon | D | Gendanlal Maurya Enterprises | Up | KC4 | 338K6006 | 5224849808 | 2025-10-01 | 522484 | 2025-10-09 | abnormal noise | 2025-01-09 | 2025-03-22 | 1704.8 | 750 | cold storage | 3 | Cylinders liners , Piston & piston rings wornout. | All 4 | closed | Replacde Linres 3, Piston rings 4 & Piston 2
2025-10-20 | Multivista Global Pvt Ltd | Gurgaon | D | Eng Organic Agro Foods | Up | KCX4 | 3384K3996 | 5222329772 | 2025-09-23 | 522232 | 2025-10-08 | abnormal noise | 2025-02-19 | 2025-03-27 | 1148.5 | 750 | cold storage | 1 | Cylinders liners , Piston & piston rings wornout. | All 4 | closed | Replacde Linres 4, Piston rings 4 & Piston 2
2025-10-20 | Cool Comfort Private Limited | West Bengal | D | Maa Agrocorp Cold Storage Private Limited | Wb | KCX3 | 3374K3540 | 5241549844 | 2025-10-10 | 524154 | 2025-10-10 | cylinder overheating | 2024-09-28 | 2025-02-28 | 598 | 990 | cold storage | 5 | Cylinder No. 3 , Delivery valve ring spring broken | 3 | closed | Replaced KIT DELIVERY VALVE KC/KCX1
2025-10-20 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Pushpai Marine Exports Pvt Ltd | Mh | KCX42 | 3444K511 | 5242549864 | 2025-10-16 | 524254 | 2025-10-12 | delivery valve leakage | 2025-01-31 | 2025-07-29 | 332 | null | cold storage | 6 | One delivvery valve leakage | Not mentioned | closed | Replaced delivery valve assly 1
2025-10-20 | Cool Comfort Private Limited | West Bengal | D | Bandhu Multipurpose Cold Storage Private Ltd | Wb | KCX4 | 3384K3964 | 5225649782 | 2025-09-26 | 522564 | 2025-09-29 | high oil consumption | 2025-02-01 | 2025-03-06 | 1218 | 850 | cold storage | 1 | Cylinders liners , Piston & piston rings wornout. | All | closed | Replacde Linres 1, Piston rings 4 & Piston 1
2025-10-20 | Multivista Global Pvt Ltd | Gurgaon | D | Banke Bihari Cold Storage | Up | KC4 | 338K5948 | 5210949732 | 2025-09-10 | 521094 | 2025-10-07 | high oil consumption | 2024-09-30 | 2025-03-15 | 1465 | 750 | cold storage | 6 | Cylinders liners , Piston & piston rings wornout. | All 4 | closed | Replaced Cylinder liner4, Piston 2 & Piston ring set4
2025-10-20 | Multivista Global Pvt Ltd | Gurgaon | D | Jsb Dairy Products Pvt. Ltd | Up | KCX3 | 3374K3428 | 5226689836 | 2025-10-14 | 522668 | 2025-10-14 | abnormal noise | 2024-03-05 | 2024-04-30 | 5849 | 764 | dairy / ice cream | 1 | Liner & Piston rings worn-out | 3 | closed | Replaced Liner 1 , Piston 1 & Piston rings 3
2025-10-20 | Parag Marketing Services | null | D | Milky More Industries | Mh | KCX2 | 3364K2729 | 5216549807 | 2025-09-30 | 521654 | 2025-09-30 | abnormal noise | 2024-08-06 | 2024-12-28 | 905 | 800 | dairy / ice cream | 4 | Both cylinders liner , Piston & piston rings wornout | All 2 | closed | Replaced liners , Piston , Piston Rings
2025-10-20 | Trade Links | Secunderabad | D | Manasa Dairy Products | Telangana | KCX2 | 3364K2933 | 5225729799 | 2025-09-29 | 522572 | 2025-09-25 | high oil consumption | 2025-06-11 | 2025-07-05 | 1237 | 850 | dairy / ice cream | 1 | No 1 cylinder liner have step marks was observed and piston ring gap f also found 1.2 mm for No 1 & 2 cylinder & piston ring | 1.2 | closed | Replacde Linres 1, Piston rings 2
2025-10-20 | Geekay Pneumatics Pvt Ltd | Kerala | D | Kozhikode Dairy | Kerala | KCX2 | 3364K2693 | 5182329597 | 2025-08-18 | 518232 | 2025-08-17 | high oil consumption | 2024-05-31 | 2024-09-22 | 2535 | 980 | dairy / ice cream | 4 | Liner & Piston rings worn-out | 2 | closed | Replaced Liner & piston ring 1
2025-10-20 | Model Pneumatic Co | Punjab | D | Sahib Farm Nainewal | Punjab | KCX2 | 3364K2765 | 5218169754 | 2025-09-17 | 521816 | 2025-10-13 | pressure switch malfunctioning | 2024-09-30 | 2025-07-23 | 2 | 750 | dairy / ice cream | 10 | Oil pressure switch is triping is not working properly because oil pressure on 4 bar and suction is on 2 bar but compressor is triping. | NA | closed | Replaced PRESSURE SWITCH OP MP55A
2025-10-20 | S. B. Refrigeration Services | Bihar | D | Vaishali Patliputra Dugdh Utpadak Sahakari Sanghltd | Bihar | KCX4 | 3384K4079 | 5230189803 | 2025-09-30 | 523018 | 2025-09-30 | shaft seal leakage | 2025-07-11 | 2025-09-06 | 245 | 864 | dairy / ice cream | 2 | Shaft seal leakage within 250 hrs | null | closed | Replaced shaft seal assembly
2025-10-20 | Multivista Global Pvt Ltd | Gurgaon | D | Agrich Foods | Uk | KCX63 | 3464K255 | 5222349773 | 2025-09-23 | 522234 | 2025-10-05 | abnormal noise | 2025-01-15 | 2024-04-15 | 830 | 900 | food processing | 3 | Cylinders liners , Piston & piston rings wornout. | 2,3,4,9 | closed | Replacde Linres 4, Piston rings 9 & Piston 2
2025-10-20 | Kalp Marketing | Gujrat | D | Mcpatel Foods Pvt Ltd | Gujrat | KCX9 | 3404K401 | 5227589788 | 2025-09-27 | 522758 | 2025-09-27 | oil pressure problem | 2025-02-28 | 2025-08-19 | 115 | 930 | food processing | 7 | Oil pressure not developed. Replaced pump element | LC 02 25 1055 | closed | Replaced pump element.
2025-10-20 | Parag Marketing Services | Maharashtra | D | Sitara Ice And Cold Storage | Mh | KCX6 | 3394K2539 | 5225289826 | 2025-10-07 | 522528 | 2025-10-07 | high oil consumption | 2024-09-25 | 2025-03-24 | 24 | 900 | ice plant | 6 | Observed 12liter oil charge in 24 hrs.After starting the compressor i observed normally knocking sound in all cylinders | All 6 | closed | Replacde Linres 6, Piston rings 6 & Piston 3
2025-10-20 | Kalp Marketing | Gujrat | D | S K Foods | Gujrat | KCX93 | 3485K210 | 5235109825 | 2025-10-06 | 523510 | 2025-10-07 | oil pressure not buildup | 2024-06-27 | 2024-09-18 | 585 | 882 | meat/fish process | 3 | Oil pressure not developed. Replaced pump element | null | closed | Replaced pump element.
2025-10-20 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Arati Drugs Ltd | Mh | KCX6 | 3394K2700 | 5216969769 | 2025-09-22 | 521696 | 2025-09-24 | high oil consumption | 2025-03-10 | 2025-04-24 | 2843 | 800 | chemical / pharma | 1 | All 6 piston rings & 4 Linres wornout. | All 6 | closed | Replacde Linres 4 & Piston rings 6
2025-10-31 | Multivista Global Pvt Ltd | Gurgaon | D | Krishna Kumar Ice And Cold Storage Pvt. Ltd | Gj | KC4 | 338K5945 | 5246149872 | 2025-10-17 | 524614 | 2025-10-17 | abnormal noise | 2024-09-24 | 2025-02-26 | 1053 | 750 | cold storage | 5 | Abnormal Noise due to increased gap between the piston and liner and Liner and Piston ring worn out. Oil Used- Kirloskar Advantage Ring-397/08/24 Required Piston ring will be provided by KPC Delhi . | All 4 | closed | Replaced liners 3 & Piston 1
2025-10-31 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Sonia Fishries Pvt Ltd | Raigad | KCX72 | 3474K762 | 5248529869 | 2025-10-17 | 524852 | 2025-10-17 | solenoid valve leakage | 2024-03-18 | 2024-05-21 | 2650 | 950 | meat/fish process | 2 | TDV Solenoid valve leak from bottom knob Oring. | NA | closed | Replaced TDV Solenoid valve.
2025-11-07 | Parag Marketing Services | Maharashtra | D | Royal Foodstuffs Pvt Ltd | Mh | KCX72 | 3474K776 | 5248209870 | 2025-10-17 | 524820 | 2025-10-17 | abnormal noise | 2024-05-09 | 2025-03-07 | 2355 | 900 | food processing | 9 | During inspection, step cut marks were observed on cylinder liners # 2 and # 5. All 9 nos of piston rings were found worn out, and piston -1 was found rubbed | 2&5 | closed | Replaced Piston 1nos Liner 2nos & piston ring set9nos.
2025-11-07 | Geekay Pneumatics Pvt Ltd | Kerala | D | Aswathi Ice Plant | Kerala | KCX2 | 3364K2942 | 5181449577 | 2025-08-13 | 518144 | 2025-08-13 | high oil consumption | 2025-06-25 | 2025-08-01 | 145 | 770 | ice plant | 1 | Piston & Liner worn out & oil throw, SHAFT SEAL LEAKING | 1 | closed | Replaced Piston ring set1nos, Liner1nos, Shaft seal assembly1nos & teflon ring safety valve1nos.
2025-11-07 | Parag Marketing Services | Maharashtra | D | Gadre Marine Export Pvt Ltd | Mh | KCX72 | 3474K827 | 5239749889 | 2025-10-31 | 523974 | 2025-10-29 | oil pump tang broken | 2024-09-03 | 2025-09-25 | 46 | 1000 | meat/fish process | 11 | Found oil pump element tang Brocken and housing damage. | LC 08 24 460 | closed | Replaced oil pump assly
2025-11-07 | Gargi Engineering Enterprises Pvt Ltd | Gujrat | D | Jay Jalaram Lifesciences Pvt Ltd | Gj | KCX1 | 3354K0334 | 5227469791 | 2025-09-27 | 522746 | 2025-09-27 | Oil Pressure Issue | 2024-08-29 | 2025-01-17 | 506 | 548 | chemical / pharma | 4 | Air purging issue noticed. It found damage | H 24 015 LDK | closed | Replaced THRUST RING PUMP END BEARING COVER KCX
2025-11-07 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2695 | 5236589830 | 2025-10-07 | 523658 | 2025-10-07 | abnormal noise | 2025-02-27 | 2025-05-08 | 3072 | 850 | chemical / pharma | 2 | Abnormal sound observed in cylinder no 5 and replaced worn out parts | 5 | closed | Replaced Piston1nos, Gudgeon pin1nos, Bush con rod1nos.
2025-11-07 | Trade Links | Secunderabad | D | Covalent Laboratories Pvt Ltd | Telangana | KCX42 | 3444K439 | 5245689859 | 2025-10-15 | 524568 | 2025-10-16 | cylinder overheating | 2023-12-28 | 2024-12-30 | 3000 | 900 | chemical / pharma | 12 | The leakage issue of the NO 1HP cylinder discharge valve and has resulted in damaged to other components as well | HP-1 | closed | Replaced Liner1nos, Piston1nos & Piston Ring1nos, DV1nos, Gudgeon pin1nos, Needle roller bearing2nos & Spacer for NB1nos.
2025-11-10 | Multivista Global Pvt Ltd | Gurgaon | D | Vashisht Enterprises | Up | KCX42 | 3444K500 | 5262569888 | 2025-10-30 | 526256 | 2025-11-15 | abnormal noise | 2024-11-28 | 2025-02-11 | 1765 | 750 | food processing | 2 | Piston ring and liner worn worn out of HP Cylinder. Oil Use- Servo Friz 68 NH | HP-1 | closed | Replaced Liner2nos, Piston1nos ,Piston ring set2nos.
2025-11-10 | Model Pneumatic Co | Punjab | D | Pancarbo Greenfuels Private Limited | Pb | KCX72 | 3474K747 | 5254449883 | 2025-10-28 | 525444 | 2025-10-28 | KRMSDischarge temp sensor faulty. | 2024-02-29 | 2024-08-11 | 7208 | 992 | chemical / pharma | 5 | Discharge temp sensor get faulty. | null | closed | Replaced Discharge temp sensor, PT1000.
2025-11-13 | Trade Links | Secunderabad | D | Assago Industries Pvt. Ltd | Ap | KCX93 | 3485K212 | 5272569929 | 2025-11-07 | 527256 | 2025-11-07 | KRMS Controller issue. | 2024-06-27 | 2025-04-12 | 998 | 950 | others | 10 | The inspected wiring of the controller panel was found to be in accordance with the wiring diagram. The software has also been updated; however, it was observed that CCSV3 is receiving direct power when the MCB is switched on. Refer email dated 07/11/2025. | NA | closed | Replaced CONTROLLER BOARD pCOOEM+
2025-11-18 | Robin Refrigeration Works | Odisha | D | United Breweries Ltd (Khurdah) | Odisha | KCX6 | 3394K 2468 | 5272909932 | 2025-11-08 | 527290 | 2025-11-13 | knocking / abnormal sound | 2024-03-30 | 2024-09-11 | 3264 | 850 | beverage / breweries | 6 | found that the piston was stuck due to discharge valve leakage. There are no foreign particles inside the cylinder. In my opinion this is a premature failure. | null | closed | Replaced Delivery valve , Liner , Piston , Piston rings & Bearings 1 no each.
2025-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Maa Rasila Cold Storage Llp | Up | KC4 | 338K6007 | 5206689706 | 2025-09-04 | 520668 | 2025-09-04 | high oil consumption | 2025-01-10 | 2025-03-21 | 1634.6 | 750 | cold storage | 2 | Cylinder Liner & Piston Ring Set worn out. | All 4 | closed | Replaced Liners & Piston ring sets 4 nos each.& Piston 3 Nos.
2025-11-18 | Parag Marketing Services | null | D | Govind Milk & Milk Product Pvt Ltd | Phaltan Mh | KCX6 | 3394K2452 | 5209389821 | 2025-10-04 | 520938 | 2025-10-01 | high oil consumption | 2024-02-29 | 2025-01-31 | 1026 | 850 | cold storage | 10 | Issues of oil consumption and step cut marks on the cylinder liners. The following findings were noted: 1) Piston ring sets found worn out - 6 nos 2) Cylinder liners with visible step cut marks - 6 nos. 3) Pistons found with rubbing marks - 4 nos. 4) Connecting bush found worn out -1no | All 6 | closed | Replaced LINERS6 , Piston rings 6 & Piston 4 nos.
2025-11-18 | Multivista Global Pvt Ltd | Gurgaon | D | Paradise Cold Storage | Up | KCX2 | 3364K2793 | 5274489943 | 2025-11-19 | 527448 | 2025-11-19 | high oil consumption | 2024-11-28 | 2025-02-22 | 2222 | 750 | cold storage | 3 | Liner and Piston Ring worn our, A wavy pattern has formed in middle of Liner. Oil Used- Seetul N-68 Piston Ring will be provided by Delhi office. | Both cyl. | closed | Replaced
2025-11-18 | Cool Comfort Private Limited | West Bengal | D | Maa Renubala Himghar Pvt. Ltd | Wb | KCX4 | 3384K3982 | 5273789934 | 2025-11-09 | 527378 | 2025-11-09 | knocking / abnormal sound | 2025-02-12 | 2025-03-28 | 2304 | 850 | cold storage | 1 | open the head cover and check discharge valve leakage and piston cylinder and ring damage | null | closed | Replaced liner , piston , piston rings & Delivery valve 1 each , Valve kit 3 nos.
2025-11-18 | Geekay Pneumatics Pvt Ltd | Kerala | D | Wayanad Dairy | Kerala | KCX2 | 3364K2692 | 5267789930 | 2025-11-07 | 526778 | 2025-11-05 | high oil consumption | 2024-05-31 | 2024-09-25 | 2743 | 990 | dairy / ice cream | 4 | Cylinder Liner & Piston Ring Set worn out. | null | closed | Replaced Liners & Piston ring sets 2 nos each.
2025-11-18 | Multivista Global Pvt Ltd | null | D | Shakayam Ice Factory | Tn | KCX6 | 3394K2469 | 5272489953 | 2025-11-13 | 527248 | 2025-11-13 | high oil consumption | 2024-06-20 | 2025-04-20 | 2915 | 771 | ice plant | 10 | Hairline crack in the second piston | Cyl.2 | closed | Replaced Piston 1 no.
2025-11-18 | Trade Links | Secunderabad | D | Sai Balaji Ice Factory | Ap | KCX4 | 3384K3997 | 5248329875 | 2025-10-18 | 524832 | 2025-10-18 | high oil consumption | 2025-02-20 | 2025-04-14 | 3814 | 850 | ice plant | 2 | The issue of repeated oil carry was inspected, revealing that the liners, piston rings, and two pistons were worn out. They were replaced with B type liners and 107 piston rings. The compressor is now under observation for its operation. | All 4 | closed | Replaced Cylinder liners4 , Piston2 & Piston rings 4
2025-11-18 | Trade Links | Secunderabad | D | Shri Ice Links | Ap | KCX4 | 3384K3843 | 5209109891 | 2025-10-31 | 520910 | 2025-09-10 | cylinder overheating | 2024-11-15 | 2025-01-07 | 1070 | 750 | meat/fish process | 14 | No 3 & 4 cylinder Discharge valve back leaking and resulting piston seized and piston rings , liners are worn out. | Cyl. 3 & 4 | closed | Replaced Delivery valve 2 , Liner , Piston , Piston rings , Gudgeon pin & Buffer spring 1 no. each
2025-11-22 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Sonia Fishries Pvt Ltd | Raigad | KCX72 | 3474K763 | 5277589969 | 2025-11-14 | 527758 | 2025-11-14 | solenoid valve leakage | 2024-03-18 | 2024-05-21 | 3801 | 950 | meat/fish process | 2 | Solenoid valve leak from bottom knob from Oring. | null | closed | Replaced solenoid valve assembly.
2025-11-29 | Trade Links | Secunderabad | D | Crux Bioethanol India Private Limited | Ap | KCX93 | 3485K0222 | 5266589991 | 2025-11-22 | 526658 | 2025-11-06 | oil pump tang broken | 2024-09-27 | 2025-11-06 | 6 | 800 | beverage / breweries | 13 | Driving gear tang had brocken within3 hrs of running. | null | closed | Replaced oil pump assly
2025-11-29 | Multivista Global Pvt Ltd | Gurgaon | D | Unimax Frozen Treat Pvt Ltd | Haryana | KCX72 | 3474K799 | 5282049983 | 2025-11-19 | 528204 | 2025-11-29 | shaft seal leakage | 2024-07-01 | 2025-04-14 | 919 | 990 | food processing | 9 | Shaft Seal Leakage | null | closed | Replaced Shaft seal assly.
2025-11-29 | Multivista Global Pvt Ltd | Tamil Nadu | D | Mm Ice Plant | Tn | KCX4 | 3384K3807 | 5244709848 | 2025-10-13 | 524470 | 2025-10-22 | abnormal noise | 2024-10-16 | 2025-05-23 | 3167 | 825 | ice plant | 6 | 1 dv assembly all are damaged | 1 | closed | Replaced Liner1Nos, Piston1Nos,Valve spring suction1Nos, DV1Nos.
2025-11-29 | Trade Links | Secunderabad | D | Varma Marineprivate Limited | Ap | KCX6 | 3394K2605 | 5275409961 | 2025-11-14 | 527540 | 2025-11-14 | abnormal noise | 2024-12-07 | 2025-06-14 | 1565 | 950 | ice plant | 5 | The problem of back leakage in the discharge valves No. 3 and No. 4 is also linked to damage in other components. Additionally, the piston rings for cylinders 1, 3, 5, and 6 have worn out, with cylinder 1 exhibiting step marks in its middle. | 1,3,4 | closed | Replaced Valve spring suction2Nos, Ring suction valve1Nos, Gudeon Pin1Nos, Bearing bush big end con rod 1Nos,Bush con rod1Nos, DV2Nos, Liner3Nos, Liner3Nos,Piston ring set6Nos & Piston2Nos.
2025-11-29 | Kalp Marketing | Gujrat | D | Lunai Enterprises | Gj | KCX6 | 3394K2672 | 5281909987 | 2025-11-21 | 528190 | 2025-11-21 | cylinder overheating | 2025-02-13 | 2025-08-01 | 2271 | 770 | ice plant | 1 | Head cover no 1 and found cylinder liner number 1 Seized and Delivery valve Leaked . | 1 | closed | Replaced DV1nos,Liner1nos,Piston1nos & Piston ring set1Nos.
2025-11-29 | Trade Links | Secunderabad | D | Asvini Fishries | Bhimavaran Ap | KCX51 | 3454K 280 | 5275429950 | 2025-11-11 | 527542 | 2025-11-11 | cylinder overheating | 2025-08-22 | 2025-10-24 | 467 | 986 | meat/fish process | 1 | Cylinder no. 3 delivery valve leakage resulted to Overheating. | 300 | closed | Replaced delivery valve assembly 1 No.
2025-11-29 | Trade Links | Secunderabad | D | Asvini Fishries | Bhimavaran Ap | KCX51 | 3454K0280 | 5245029881 | 2025-10-26 | 524502 | 2025-10-24 | KRMSDischarge temp sensor faulty. | 2025-08-22 | 2025-10-24 | 55 | 986 | meat/fish process | 2 | KRMS-Discharge temp sensor faulty. | null | closed | Replaced DISCHARGE TEMPERATURE SENSOR, PT1000 WITH 12 MTR CABLE LENGTH. RANGE
2025-11-29 | Trade Links | Secunderabad | D | Shri Ice Links | Ap | KCX4 | 3384K3843 | 5242109866 | 2025-10-16 | 524210 | 2025-10-16 | oil pump tang broken | 2024-11-15 | 2025-01-07 | 1018 | 750 | meat/fish process | 1 | Oil pump element tang broken | PTOK10 24 755 | closed | Replaced oil pump assly
2025-12-01 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Singhal Commodities Pvt. Ltd | Daman | KCX3 | 3374K3774 | 52822610004 | 2025-11-26 | 528226 | 2025-11-22 | LP switch malfunctioning | 2025-07-07 | 2025-11-22 | 0 | 622 | construction | 5 | LP Switch not woking properly malfuction | null | closed | Replaced PRESSURE SWITCH LP KP1A
2025-12-09 | Parag Marketing Services | Chhatisgarh | D | Shreenath Sheetgrih | Chhattisgarh | KCX3 | 3374K3336 | 5256869999 | 2025-11-26 | 525686 | 2025-11-23 | abnormal noise | 2023-12-26 | 2024-05-03 | 2543 | 770 | cold storage | 4 | Opened Head cover 3 no cylinder liner step cut. | 3 | closed | Replaced Liner1 nos, Piston1 nos, Piston ring set1 Nos & curtain spring 1Nos.
2025-12-09 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Pushpai Marine Exports Pvt Ltd | Mh | KCX93 | 3485K245 | 5280669989 | 2025-11-22 | 528066 | 2025-11-18 | cylinder overheating | 2025-01-31 | 2025-07-29 | 728 | 930 | cold storage | 5 | 2 delivery valve leak found. 2 time attempt to leak proof this valve. Cylinder No 10 success. but Cylinder No 3 strokelimiter holding cup spring slot step cut | 3 | closed | Replaced DV 1nos.
2025-12-09 | Cool Comfort Private Limited | West Bengal | D | Shiv Dairy | Wb | KCX4 | 3384K3672 | 52903010017 | 2025-12-01 | 529030 | 2025-12-03 | abnormal noise | 2024-03-14 | 2025-02-27 | 573 | 850 | dairy / ice cream | 12 | Crack in piston head and have to change the piston ring of cylinder no 3 .so we need 1nos piston and 1 nos piston ring set | 3 | closed | Replaced Piston 1nos Piston ring set 1nos
2025-12-09 | Trade Links | Secunderabad | D | Mulpuri Aqua Processors | Ap | KCX6 | 3394K2683 | 5274369949 | 2025-11-11 | 527436 | 2025-11-11 | high oil consumption | 2025-02-19 | 2025-07-06 | 1618 | 950 | ice plant | 3 | An abnormal sound and oil lifting problem was identified; upon inspection, it was discovered that 2nos liners and 3nos piston rings were worn out. | 1,4&5 | closed | Replaced Liner 2 Nos & Piston ring set 3 Nos.
2025-12-09 | Trade Links | Secunderabad | D | Sri Raghu Rama Ice Factory | Ap | KCX4 | 3384K3830 | 5245669858 | 2025-10-15 | 524566 | 2025-10-15 | high oil consumption | 2024-11-07 | 2024-12-27 | 3482 | 850 | ice plant | 1 | Cylinder NO. 2nd 3rd 4th light condition oil throwing lost time changed cylinder no.1st 3rd liners and also all piston rings present cylinder no.3rd liner stepping condition and also ORV is a back leakage | 23&4 | closed | Replaced Liner 1nos & Piston ring set 3Nos.
2025-12-09 | Multivista Global Pvt Ltd | Tamil Nadu | D | Maruthi Trading And Seafoods | Tn | KCX4 | 3384K4027 | 5216649797 | 2025-09-29 | 521664 | 2025-10-18 | high oil consumption | 2025-03-27 | 2025-08-24 | 902 | 887 | ice plant | 4 | Piston worn out. cylinder temperature is so high | null | closed | Replaced Liner 2nos, Piston ring set4nos.
2025-12-09 | Geekay Pneumatics Pvt Ltd | Kerala | D | Ai Marine Products India Private Limited | Kerala | KCX93 | 3485K206 | 5225909786 | 2025-09-26 | 522590 | 2025-09-26 | abnormal noise | 2024-04-30 | 2024-10-02 | 1654 | 980 | meat/fish process | 3 | Dismantled the head and found that 4 nos delivery valves were leaked. 2 nos in LP side (head No. 5 & 11) and 2 nos in HP side (head No. 2 & 4). Dismantled the delivery valve checked found that the delivery valve stroke limitor pin worn out. In head No. 4 piston and liner damaged because of the over heat. | 4 | closed | Replaced Piston 1nos, Piston ring set1nos, Liner1nos, Discharge valve2nos, DELIVERY STROKE LIMITOR KC 2Nos, Gudeon Pin1nos, Bolf Safety 1Nos, & Lok Plate Con rod 2Nos.
2025-12-09 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Sonia Fishries Pvt Ltd | Raigad | KCX72 | 3474K762 | 5278289968 | 2025-11-15 | 527828 | 2025-11-14 | abnormal noise | 2024-03-18 | 2024-05-21 | 2775 | 950 | meat/fish process | 1 | 4th cylinder head cover and observed that the DV valve springs were broken. Consequently, the buffer spring was also affected and had reduced in length. This condition was identified as the primary cause of the knocking sound. | 4 | closed | Replaced DV1 Nos, Buffer Spring1 Nos.
2025-12-09 | Geekay Pneumatics Pvt Ltd | Kerala | D | Cap Seafoods Pvt Ltd | Kerala | KCX72 | 3474K930 | 5262549896 | 2025-11-01 | 526254 | 2025-11-01 | GAUGE LEAK INSIDE | 2025-06-28 | 2025-11-01 | 4 | 950 | meat/fish process | 4 | Pressure gauge leakage | null | closed | Replaced AMMONIA PRESSURE GAUGE 016 Kg/cm2
2025-12-09 | Geekay Pneumatics Pvt Ltd | Kerala | D | Bell Exim Pvt Ltd | Kerala | KCX31 | 3434K0257 | 5232389823 | 2025-10-06 | 523238 | 2025-10-06 | high oil consumption | 2024-08-30 | 2024-10-07 | 7257 | 800 | meat/fish process | 1 | Dismantled all heads take open trial found oil splash from all pistons checked all cylinders found high side liner had small step mark then dismantled all pistons all rings had worn out | HP | closed | Replaced Liner 1 Nos, Piston ring set 4Nos & Lock plate con rod 8 Nos.
2025-12-09 | Multivista Global Pvt Ltd | Gurgaon | D | Tropical Agrosystem India Pvt. Ltd | Up | PCX2 | 3106K0300 | 5283489996 | 2025-11-24 | 528348 | 2025-11-26 | high oil consumption | 2024-07-16 | 2024-12-25 | 338 | 1050 | chemical / pharma | 4 | Piston Ring Worn Out | null | closed | Replaced piston ring set2 Nos
2025-12-20 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Pushpai Marine Exports Pvt Ltd | Mh | KCX93 | 3485K246 | 5280649990 | 2025-11-22 | 528064 | 2025-11-18 | cylinder overheating | 2025-01-31 | 2025-07-29 | 728 | 930 | cold storage | 5 | After inspection and dismantling of head cover No. 7, it was observed that the DV valve had a minor leak caused by step-cut marks on the stroke limiter plate and the DV valve holding disc. The team conducted 2?3 leak tests to confirm the issue. A new DV valve was installed, after which the problem was resolved. | DV-7 | closed | Replaced DV1 Nos
2025-12-20 | Parag Marketing Services | Maharashtra | D | Govind Milk & Milk Product Pvt Ltd | Phaltan Mh | KCX72 | 3474K758 | 5256689967 | 2025-11-15 | 525668 | 2025-11-15 | high oil consumption | 2024-02-29 | 2024-07-31 | 5357 | 900 | dairy / ice cream | 5 | Oil throwing was observed from all cylinders. Step-cut marks were found on cylinders 1, 2, 3, 4, 5, 6, 7, and 9. Additionally, all 9 Nos. of 397-code piston rings were found to be worn out. | 1,2,3,4,5,6,7 & 9 | closed | Replaced Liner8Nos, Piston1Nos, Piston Ring set9Nos, Curtain Spring 4Nos, Lock plate conrod 9Nos.
2025-12-20 | Parag Marketing Services | Maharashtra | D | Gadre Marine Export Pvt Ltd | Mh | KCX72 | 3474K824 | 5280049976 | 2025-11-18 | 528004 | 2025-11-18 | high oil consumption | 2024-09-03 | 2025-06-24 | 1876 | 850 | meat/fish process | 10 | 1) Step cut marks were found on all liner cylinders (B type) 2) All 397 code piston rings were worn out, with clearance gaps ranging from 1.0 mm to 7.25 mm. 3) Crankshaft crank pins and intermediate bearing diameters does not meet standard specifications. | 1,4,6,7,9 | closed | Replaced Piston1nos, Piston ring set9nos, Liner9nos, Bearing int half2nos, Lock plate con rod 18 nos, Bearing bush big end 6Nos, Crankshaft KCX91nos.
2025-12-21 | Cool Comfort Private Limited | West Bengal | D | Shiv Dairy | Wb | KCX4 | 3384K3671 | 52902810022 | 2025-12-03 | 529028 | 2025-12-05 | abnormal noise | 2024-03-14 | 2025-02-27 | 556 | 850 | dairy / ice cream | 10 | Cylinder no3 piston Crack and piston ring damage. | null | closed | Replaced Piston1nos & Piston ring set 1Nos
2025-12-21 | Multivista Global Pvt Ltd | Gurgaon | D | Agson Global Pvt Ltd | Haryana | KCX63 | 3464K263 | 52886210011 | 2025-11-29 | 528862 | 2025-12-04 | high oil consumption | 2025-03-27 | 2025-07-02 | 1958 | 750 | chemical / pharma | 3 | Piston ring close Gap found 1mm to 5mm in all cylinder. Found emery particles found | HP | closed | Replaced Liner 3 Nos, & Piston 2 Nos
2025-12-31 | Cool Comfort Private Limited | West Bengal | D | Sicgil Industrial Gases Ltd | As | KCX93 | 3485K 0254 | 53086610059 | 2025-12-16 | 530866 | 2025-12-31 | high oil consumption | 2025-03-29 | 2025-06-12 | 260 | 1000 | beverage / breweries | 2 | All the cylinders and found that the piston rings were worn out . Shaft seal leakage | All | closed | Replaced shaft seal assly1nos & Piston ring sets12nos.
2025-12-31 | Kalp Marketing | Gujrat | D | Mansadevi Cold Storage | Gj | KCX3 | 3374K3553 | 5198449658 | 2025-08-27 | 519844 | 2025-08-27 | abnormal noise | 2024-10-21 | 2025-02-20 | 1145 | 770 | cold storage | 3 | The liners have cut in 360 Degree Pattern(Ring Cut). | 1 | closed | Replaced Liner 1 Nos & Piston ring set 1nos.
2025-12-31 | Kalp Marketing | Gujrat | D | Jagdamba Cold Storage | Mp | KCX4 | 3384K3782 | 5279749979 | 2025-11-18 | 527974 | 2025-11-18 | abnormal noise | 2024-09-24 | 2025-03-24 | 2166 | 770 | cold storage | 6 | The Liners have cut in 360 Degree Pattern(Ring Cut). this is result in to damage the Piston rings,Piston and one DV assembly. | 2 | closed | Replaced Liner2nos, Piston 2Nos, Piston ring set 2nos & DV1Nos.
2025-12-31 | Kalp Marketing | Gujrat | D | Patidar Agricare | Gj | KCX4 | 3384K3657 | 5166509517 | 2025-07-29 | 516650 | 2025-07-29 | cylinder overheating | 2024-03-04 | 2024-03-22 | 5339 | 800 | cold storage | null | cylinder numbers 1 and 3 in the compressor were overheating.The DV rings /Springs found broken | 1 & 3 | closed | Replaced Kit DV2nos
2025-12-31 | Kalp Marketing | Gujrat | D | Sahkar Services Pvt Ltd | Gj | KCX3 | 3374K3751 | 52981410072 | 2025-12-18 | 529814 | 2025-12-19 | kcx pump tang broken | 2025-06-09 | 2025-09-29 | 74 | 767 | cold storage | 2 | Tang Broken | LC 05 25 45 | closed | Replaced KIT OIL PUMP GEAR KCX1nos & THRUST RING PUMP END BEARING COVER KCX 1nos
2025-12-31 | Kalp Marketing | Gujrat | D | Balaji Fresh Potato Private Limited | Gj | KCX4 | 3384K3857 | 5213669735 | 2025-09-11 | 521366 | 2025-09-11 | shaft seal leakage | 2024-12-14 | 2025-02-08 | 781 | 770 | cold storage | 1 | Shaft seal leakage inside the compressor. | null | closed | Replaced KIT SHAFT SEAL ORING KC/KCX 1nos
2025-12-31 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K4040 | 52990810032 | 2025-12-06 | 529908 | 2025-12-06 | shaft seal leakage | 2025-04-23 | 2025-09-20 | 509 | 800 | food processing | 4 | Shaft seal leak complaint. During inspection, scoring marks were observed on the stationary ring and bronze ring. | null | closed | Replaced shaft seal assly 1 nos
2025-12-31 | Trade Links | Goa | D | Mb Ice Plant & Cold Storage | Goa | KCX4 | 3384K3779 | 52981210028 | 2025-12-05 | 529812 | 2025-12-05 | high oil consumption | 2024-09-24 | 2025-05-13 | 2091 | 700 | ice plant | 7 | ORVs were defective. The defective ORVs were replaced, | null | closed | Replaced Oil return valve 4nos & gasket suction strainer & side cover
2025-12-31 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Delta Refrigeration | Mh | KCX3 | 3374K3448 | 53022810058 | 2025-12-16 | 530228 | 2025-12-10 | high oil consumption | 2024-04-10 | 2024-07-10 | 11686 | 750 | ice plant | 3 | Liner cut found at the topside. Piston rings worn out | null | closed | Replaced Liner 3nos & Piston ring set3nos
2025-12-31 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Uttan Machhimar & Vahtuk Sahakari Society | Mh | KCX3 | 3374K3761 | 5277089957 | 2025-11-13 | 527708 | 2025-11-13 | high oil consumption | 2025-06-19 | 2025-07-28 | 1965.9 | 750 | ice plant | 1 | During inspection, it was observed that Cylinder Liner No. 1 had a step-cut mark and all three piston ring sets were found to be worn out. | 1 | closed | Replaced liner1nos & piston ring sets3nos
2025-12-31 | Parag Marketing Services | Maharashtra | D | Radhe Ice Factory | Mh | KCX4 | 3384K4053 | 5280149975 | 2025-11-17 | 528014 | 2025-11-17 | KRMS Temp sensor malfuction | 2025-05-16 | 2025-11-17 | 34 | 760 | ice plant | 5 | Discharge temperature readings were showing negative values, which was confirmed after cross-checking in KRMS | null | closed | Replaced discharge temp sensor PT1000(50⁰ 250⁰)
2025-12-31 | Geekay Pneumatics Pvt Ltd | Kerala | D | Ashirwad Marine Ice | Kerala | KCX3 | 3374K3713 | 53090210069 | 2025-12-17 | 530902 | 2025-12-17 | pressure gauge malfunctioning | 2025-03-15 | 2025-12-17 | 34 | 870 | ice plant | 8 | GAUGE OUT | null | closed | Replaced Pressure gauge 16kg/cm2
2025-12-31 | Kalp Marketing | Gujrat | D | Winsor World Exports | Gj | KCX72 | 3474K0802 | 53026610043 | 2025-12-10 | 530266 | 2025-12-10 | shaft seal leakage | 2024-07-20 | 2024-08-14 | 5803 | 990 | meat/fish process | null | The O-ring found flatten from OD | null | closed | Replaced Kit Shaft seal oring1 Nos
2025-12-31 | Kalp Marketing | Gujrat | D | Shiv Kripa Gases Metals Pvt Ltd | Mp | KCX63 | 3464K237 | 53119810073 | 2025-12-18 | 531198 | 2025-12-20 | abnormal noise | 2024-09-24 | 2025-02-08 | 1865 | 936 | chemical / pharma | 4 | The Cylinder Liners have cut uniformaly resulting to damage the piston rings and piston as well | 2 | closed | Replaced Liner 2Nos, Piston 2Nos, Piston ring set 2 Nos & Needle roller bearing 4Nos
2026-01-09 | Multivista Global Pvt Ltd | Gurgaon | D | Om Cold Storage | Up | KC3 | 337K4910 | 53239210105 | 2025-12-29 | 532392 | 2026-01-07 | high oil consumption | 2024-11-28 | 2025-02-19 | 1001.6 | 750 | cold storage | 2 | Liner And Piston Ring Worn out. | null | closed | Replaced Liner2 Nos & Piston ring set3 Nos.
2026-01-09 | Geekay Pneumatics Pvt Ltd | Kerala | D | Kozhikode Dairy | Kerala | KCX2 | 3364K2693 | 53160210128 | 2025-12-24 | 531602 | 2025-12-24 | high oil consumption | 2024-05-31 | 2024-09-22 | 2887 | 980 | dairy / ice cream | 3 | Changed the cylinder liner, piston ring set 2 nos each and piston 1 no. VLD O rings also changed | 2 | closed | Replaced CYLINDER LINER KC/KCX 2 PISTON KC/KCX 1 PISTON RING SET KC/KCX 2 BOLT SAFETY M12X1.75XDRG for Piston 1 SAFETY PLATE FOR GUDGEON PIN KC/KCX 1 GASKET LINER 1.5 mm KC/KCX2 GASKET HEAD COVER KC/KCX 2 GASKET SUCT STRAINER & SIDE COVER KC/KCX 2 DAMAGED ORING VLD PISTON KCX2 ORING VLD KCX 2 DAMAGED LOCK PLATE CON ROD & INTER. HSG BOLT KC/KCX4
2026-01-09 | Multivista Global Pvt Ltd | Tamil Nadu | D | Naveen Agro Food Corporation (P) Ltd | Tn | PCX2 | 3106K0352 | 53191410116 | 2025-12-30 | 531914 | 2025-12-27 | shaft seal leakage | 2025-06-25 | 2025-08-04 | 0 | 849 | dairy / ice cream | 1 | O-ring become flat | null | closed | Replaced KIT SHAFT SEAL ORING PC2/PCX21nos
2026-01-09 | Multivista Global Pvt Ltd | Gurgaon | D | Unimax Frozen Treat Pvt Ltd | null | KCX72 | 3474K799 | 52904010020 | 2025-12-01 | 529040 | 2025-12-06 | high oil consumption | 2024-07-01 | 2025-04-14 | 920.6 | 990 | food processing | 8 | Found emery particles | null | closed | Replaced Liner2 Nos & Piston2 nos
2026-01-09 | Trade Links | Secunderabad | D | Hyson Exports Private Limited | Ap | KCX72 | 3474K838 | 53155610089 | 2025-12-24 | 531556 | 2025-12-24 | KRMS controller problem | 2024-09-30 | 2024-12-13 | 3906 | 990 | food processing | 2 | Krms CCSV 4 loading not taking place. Toggle switch & SV4 working check by interchanging found ok. KRMS controller problem. It is suspected that the controller relay is malfunctioning. | null | closed | Replaced CONTROLLER BOARD pCOOEM1Nos
2026-01-09 | Multivista Global Pvt Ltd | Gurgaon | D | Pal Frozen Foods | Uk | KC72 | 347K1008 | 53194210117 | 2025-12-31 | 531942 | 2026-01-03 | sv coil burnt | 2025-06-19 | 2026-01-03 | 1.7 | 900 | food processing | 6 | SV Coil Burnt | null | closed | Replaced SOLENOID VALVE 3WAY2nos
2026-01-09 | Trade Links | Goa | D | Mb Ice Plant & Cold Storage | Goa | KCX4 | 3384K3778 | 52981010027 | 2025-12-05 | 529810 | 2025-12-05 | high oil consumption | 2024-09-24 | 2025-05-13 | 2047 | 700 | ice plant | 7 | It was observed that the ORVs were found defective. | null | closed | Replaced OIL RETURN VALVE 4 Nos, GASKET SUCT STRAINER & SIDE COVER4 Nos.
2026-01-09 | Trade Links | Secunderabad | D | Crystal Ice Depot | Ts | KZX6 | 3216K0001 | 53119410074 | 2025-12-18 | 531194 | 2025-12-19 | shaft seal leakage | 2025-02-17 | 2025-05-08 | 1050 | 1000 | ice plant | 2 | Freon gas application. Gas leakage from shaft seal assembly. Observed wearing of stationary seal ring and o ring damaged | null | closed | Replaced SHAFT SEAL ASSEMBLY 1 Nos
2026-01-09 | Multivista Global Pvt Ltd | Gurgaon | D | Carabo Foods Pvt. Ltd | Hr | KCX72 | 3474K796 | 53242810108 | 2025-12-29 | 532428 | 2026-01-06 | KCX Pump oil pressure issue | 2024-06-28 | 2025-11-12 | 5 | 850 | meat/fish process | 4 | Zero hour complaint, Driver gear tang broken | LC 05 24 182 | closed | Replaced Oil pump assly1 nos.
2026-01-09 | Gargi Engineering Enterprises Pvt Ltd | Mumbai | D | Premier Minerls And Chemical Industries | Gj | KCX1 | 3354K355 | 5276689962 | 2025-11-14 | 527668 | 2025-11-14 | abnormal noise | 2025-08-25 | 2025-09-15 | 216 | 690 | chemical / pharma | 1 | Compressor pump down remove head covers found dv assly leak replace dv assly | 1 | closed | Replaced DV1 nos
2026-01-09 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2695 | 5244489868 | 2025-12-17 | 524448 | 2025-10-15 | high oil consumption | 2025-02-27 | 2025-05-08 | 3142 | 850 | chemical / pharma | 2 | This compressor was producing an unusual sound, prompting the decision to conduct a thorough inspection. During the inspection, it was discovered that several parts were worn out, | null | closed | Replaced Piston ring set 6nos, Liner 2nos, Bearing bush big 2Nos, GASKET SUCT STRAINER & SIDE COVER 6nos, GASKET HEAD COVER 6nos, GASKET LINER 1.5 mm 6nos , ORING VLD 6nos & GASKET LINER 1.0 mm 4nos
2026-01-09 | Trade Links | Secunderabad | D | Arene Life Sciences Private Limited (Unit-3) | Telangana | KCX6 | 3394K2695 | 53089210061 | 2025-12-17 | 530892 | 2025-12-17 | high oil consumption | 2025-02-27 | 2025-05-08 | 4118 | 850 | chemical / pharma | 2 | Knocking sound from Cylinder No. 5 & 6 | 5 & 6 | closed | Replaced Piston2nos, Liner assly1nos, Gudeon pin2nos, Conrod assly2nos, DV2nos, Ring suction valve2nos, valve spring suction 4nos, Cup spring DV2nos, Buffer spring2nos, VLD piston 1nos,Actuating plunger1nos , Hsg VLD piston 1nos, Gasket liner & head cover1&2 respt, VLD piston & VLD 1nos, Safety plate gudeon pin 2nos,& Safety bolt for piston2nos.
2026-01-09 | Trade Links | Secunderabad | D | Biomed International P Ltd | Ap | KCX4 | 3384K3699 | 52924610056 | 2025-12-12 | 529246 | 2025-12-12 | shaft seal leakage | 2024-05-13 | 2025-12-12 | 5 | 850 | chemical / pharma | 7 | The shaft seal failed during the gas charging phase. An inspection was conducted, revealing that the seal face was worn out. | null | closed | Replaced Shaft seal assembly 1 Nos
2026-01-22 | Multivista Global Pvt Ltd | Gurgaon | D | Ramo Refrigerations | Up | KC3 | 337K4985 | 53343810160 | 2026-01-14 | 533438 | 2026-01-14 | sv coil burnt | 2025-10-29 | 2026-01-14 | 4 | 750 | dairy / ice cream | 2 | Zero Hour Defect, SV Coil burnt during the Commissioning. | null | closed | Replaced Solenid valve coil1 nos
2026-01-22 | Multivista Global Pvt Ltd | Gurgaon | D | Galaxy Agro Frozen Foods | Uk | KC72 | 347K1011 | 53425010151 | 2026-01-12 | 534250 | 2026-01-19 | KC Pump drive gear shaft broken | 2025-07-11 | 2026-01-10 | 4 | 850 | food processing | 5 | While commissioning and found a problem with the oil pump. The oil pump was replaced under warranty after 2 running hours, and then the compressor was started. The compressor is now running successfully. | F25C46 003 LDK | closed | Replaced Oil pump assly 1 nos
2026-01-22 | Multivista Global Pvt Ltd | Gurgaon | D | Saral Frozen Foods Pvt. Ltd | Up | KCX72 | 3474K965 | 53369810153 | 2026-01-13 | 533698 | 2026-01-08 | sv coil burnt | 2025-10-01 | 2026-01-11 | 2 | 950 | food processing | 3 | Zero Hour Defect, one Coil Mall Functioning. | null | closed | Replaced Solenid valve coil1 nos
2026-01-22 | Trade Links | Secunderabad | D | Glaze Ice Industries | Ap | KCX4 | 3384K4098 | 5264509901 | 2025-11-02 | 526450 | 2025-11-02 | abnormal noise | 2025-08-13 | 2025-10-25 | 99 | 750 | ice plant | 1 | Abnormal sounds stop compressor visit site run compressor abnormal noise for cy no1 piston area stop the compressor open both head covers cy no 1 piston rings and liner worn-out | 1 | closed | Replaced Liner 1nos & piston ring set 1nos
2026-01-27 | Kalp Marketing | Gujrat | D | Shraddha Ice & Cold Storage | Mp | KCX3 | 3374K3592 | 53405810148 | 2026-01-10 | 534058 | 2026-01-20 | abnormal noise | 2024-11-15 | 2025-03-28 | 1130 | 746 | cold storage | 5 | The DV rings found broken resulting to leaked DV and damage further to the cylinder assembly. hence instruct to replace the spares. | 2 | closed | Replaced liner , piston , piston rings & Delivery valve 1 no each.
2026-01-27 | Kalp Marketing | Gujrat | D | Seth Sanwariya Cold Storage Private Limited | Mp | KCX3 | 3374K3562 | 53406010149 | 2026-01-10 | 534060 | 2026-01-20 | high oil consumption | 2024-10-21 | 2025-03-01 | 1765 | 767 | cold storage | 6 | The Lineres have cut in 360 degree pattern(Ring Cut) though there is no evidence of liquid entry/Foreign Particles | All 3 | closed | Replaced liner & piston rings 3 nos
2026-01-27 | S. B. Refrigeration Services | Bihar | D | Shree Ramchandra Cold Storage | Bihar | KCX2 | 3364K2841 | 5281129981 | 2025-11-19 | 528112 | 2025-11-19 | shaft seal leakage | 2025-01-31 | 2025-03-19 | 2106 | 850 | cold storage | 2 | Shaft seal leakage , Oring cut replaced but problem not resolved. Hence replace the seal assly. | nil | closed | Replaced shaft seal assly
2026-01-27 | Parag Marketing Services | null | D | Vrs Foods Limited | Mh | KCX42 | 3444K474 | 52782410118 | 2025-12-31 | 527824 | 2025-12-31 | high oil consumption | 2024-07-30 | 2025-06-19 | 1442 | 1000 | dairy / ice cream | 11 | During the visit, oil was observed throwing from all piston heads. On dismantling, the following issues were found: Cylinder liner with step cut marks, Pistons showing rubbing, 397 code piston rings worn from 1.0 mm to 1.7 mm All damaged spares were replaced | All | closed | Replaced liner 6 , piston 3 & piston rings 6
2026-01-27 | Parag Marketing Services | null | D | Srushti Milk And Milk Products | Solapur | KCX4 | 3384K4021 | 53043210050 | 2025-12-12 | 530432 | 2025-12-11 | shaft seal leakage | 2025-03-17 | 2025-04-10 | 4448 | 750 | dairy / ice cream | 1 | Shaft seal wornout.During the visit, an attempt was made to resolve the leak by lapping the bronze ring and shaft seal faces; however, the leak persisted. A new shaft seal was installed, and the leak has been successfully resolved. | nil | closed | Replaced shaft seal assly
2026-01-27 | Trade Links | Goa | D | Tropical Mushrooms Pvt Ltd | Goa | KCX4 | 3384K4062 | 5253969879 | 2025-10-25 | 525396 | 2025-10-25 | oil pressure problem | 2025-06-03 | 2025-07-08 | 1551 | 700 | food processing | 1 | Oil pressure not develop. Element was broken | LC 05 25 67 | closed | Replaced pump element.