## Monitoring-Warranty
Sr. No. | Problem category | Due to Supplier/In-house | Probabale Causes
1 | High oil consumption (Piston rings & Liners wornout) | Inhouse | 1. Inadequate Lubrication. 2. Contamination in refrigerant and oil. 3. Overheating. 4.Operating Conditions-Excessive load/pressures. 5. Improper assembly and mechanical imbalance. 6. Age and Fatigue: Over time, materials can become fatigued and lose their structural integrity, leading to wear.
2 | Abnormal noise.(Piston rings & Liners wornout) | Inhouse | 1. Inadequate Lubrication. 2. Contamination in refrigerant and oil. 3. Overheating. 4.Operating Conditions-Excessive load/pressures. 5. Improper assembly and mechanical imbalance. 6. Age and Fatigue: Over time, materials can become fatigued and lose their structural integrity, leading to wear.
3 | Delivery valve leakage : Ring \ Spring broken , Stroke limitor damage & dents. | Inhouse | 1. Wear and Tear: Over time, the components of the valve can wear down due to continuous operation, leading to improper sealing. 2. Contamination: Dirt, debris, or refrigerant oil can contaminate the valve, preventing proper closure and leading to leakage. 3. Pressure Fluctuations: Sudden changes in pressure can stress the valve and contribute to leaks. 4. Corrosion: Exposure to corrosive substances or environments can degrade the valve material, leading to leaks 5. Overloading: Excessive pressure or load on the compressor can cause the springs to fail. 6.Fatigue Failure: Continuous cycling and stress can lead to material fatigue and eventual breakage of the springs. 7. Improper Tension: Incorrect spring tension during assembly can lead to premature failure. 8. Material Defects: Manufacturing defects in the spring material can result in weak points that are prone to breaking.
4 | Shaft seal leakage | In- house | 1. Wear and Tear due to lack of lubrication.. 2.Improper Installation: Incorrect installation of the seal can create gaps that allow refrigerant to escape. 4. Improper Installation of Orings : Incorrect installation of O-rings, such as twisting or pinching during assembly, can create gaps that allow leakage. 3. Incompatible Materials: Using seals & Orings made from materials that are not compatible with the refrigerant can lead to degradation and leakage. 4. Vibration: Continuous vibration from the compressor operation can loosen seals or cause misalignment. 5.Contamination: Ingress of foreign particles or liquid entry can damage the seal, leading to leakage. 6. High temperature. 7. Incorrect O-ring Size: Using O-rings that are too large or too small for the application can result in inadequate sealing and potential leaks. 8. Excessive Compression or Compression Set.
5 | Solenoid valve issue : Malfunctioning , Leakage & Coil burnt. | Supplier | 1. Overvoltage or Voltage Spikes: Applying a voltage higher than the coil’s rated voltage can cause excessive current flow, leading to overheating and coil failure. 2. Electrical Short Circuits: Short circuits within the coil winding or in the wiring can result in high current flow, generating heat and damaging the coil. 3. Continuous or Prolonged Activation: Keeping the solenoid energized for extended periods beyond its design limits can lead to overheating and coil burnout. 4. Poor Electrical Connections: Loose, corroded, or faulty wiring connections can cause arcing or increased resistance, generating heat and damaging the coil. 5. Moisture or Contamination: Exposure to moisture, dust, or corrosive elements can degrade coil insulation, leading to short circuits and burnout. 6. Frequent Switching or Rapid Cycling: Rapid on/off cycling causes thermal stress on the coil, potentially leading to insulation failure and burnout over time. 7. Mechanical or Valve Sticking Issues: If the valve sticks or operates improperly, it may cause electrical components to overheat due to improper operation or sustained energizati
6 | KCX Oil Pump purging , low oil pressure and OPR issue & tang broken. | Supplier | 1. Low Oil Level. 2. Clogged or Blocked Oil Filter: Debris or dirt may obstruct the oil flow, reducing oil pressure. 3. Worn or Damaged Oil Pump: Mechanical wear or damage to the oil pump rotors. 4. Oil Leakages from fittings can cause a drop in oil pressure. 5.Using oil with inappropriate viscosity can affect proper lubrication and oil pump operation. 6. Air or Vapor in Oil Lines: Entrapped air or vapor can cause purging issues. 7. Overheating of Compressor: Excessive heat can degrade oil quality and impair pump function. 8. Internal Wear or Damage: Worn piston rings, valves, or other internal parts can affect oil circulation and pressure. 9. Pump clearances. 10. Regulator mechanism malfuctioning.
7 | KRMS Problem :,Temp sensor, Power adaptor, SMPS & control board not working) Discharge temp sensor malfunctioning ,cable burnt,RMS Device not, working,Replaced controller board / HMI display | Supplier | 1. Improper fitment of temperature sensor & loose connection. 2. Sensor wire touches to hot thermowel.
8 | KC Oil pump Assly Low oil pressure/ oil Pr not develop/ tang broken | Supplier | 1. Low Oil Level. 2. Clogged or Blocked Oil Filter: Debris or dirt may obstruct the oil flow, reducing oil pressure. 3. Worn or Damaged Oil Pump: Mechanical wear or damage to the oil pump rotors. 4. Oil Leakages from fittings can cause a drop in oil pressure. 5.Using oil with inappropriate viscosity can affect proper lubrication and oil pump operation. 6. Air or Vapor in Oil Lines: Entrapped air or vapor can cause purging issues. 7. Overheating of Compressor: Excessive heat can degrade oil quality and impair pump function. 8. Internal Wear or Damage: Worn piston rings, valves, or other internal parts can affect oil circulation and pressure. 9. Pump clearances. 10. Regulator mechanism malfuctioning.
9 | KCX Manifold leakage due to damaged. M10 Bolt broken. | Inhouse | 1. Over-tightening or excessive torque 2. Fatigue due to repeated stress 3. Material defects or corrosion 4. Improper installation or use of incorrect tools
10 | Compressor foot crack | Supplier | 1. Overlap of shell and foot welding seams for both 4 and 6 Cylinder models. 2. Single weld run. 3. Welding run size not specified. 4. High vibrations. 5. Uneven foot gap & stress 6. Poor welding.